## Issues Log (hidden)
ISSUES LOG
# | Tab Name | Measure Name | Issues | Resolution Status | Status Last Updated | Other Notes | Part of PY26 Update
1 | C_Appliance_Refrigerator |  | kW calculation corrected. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
2 | C_Kitchen_Freezers |  | Values changed slightly with implementation of calculations in spreadsheet. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
3 | C_Kitchen_Refrigerators |  | Values changed slightly with implementation of calculations in spreadsheet. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
4 | C_HVAC_Chiller |  | ◦ Deemed savings method converted to semi-prescriptive method ◦ Added supplementary worksheet. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
5 | C_HVAC_AC |  | ◦ Deemed savings method converted to semi-prescriptive method ◦ Added supplementary worksheet. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
6 | C_HVAC_water pump |  | Measure updated per EM&V: efficiency, load factor, savings by building type, EFLH and CF values modified to be consistent with SCE13HC030.1 | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
7 | C_Light_General |  | ◦ EFLH verified. Calculations revised to use hours from PY16 TRM due to results of verification. ◦ Added new measure: 3' Linear LED ◦ Added new measure: 8' Linear LED ◦ Added new measure: 4' T5/T5 HO to Linear LED ◦ Updated wattages for remaining Linear LED measures in order to be consistent with new measures. ◦ Updated wattage ranges for LED Corn Cob in order to reflect current market and equipment trends. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
8 | C_Light_CFL |  | Removed this measure as CFLs are not included in the portfolio post-PY2017 | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
9 | C_Light_Dimmable |  | Values changed slightly with implementation of calculations in spreadsheet. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
10 | C_PlugProcess_Night Covers |  | This measure was added back from PY15 TRM | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
11 | C_PumpMotor_PE Motor |  | This measure was added back from PY15 TRM with updated efficiency values. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
12 | C_WH_HPWH |  | Removed this measure since Commercial HPWH went customized in PY2017 | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
13 | R_HVAC_ceiling fan |  | Values changed slightly with implementation of calculations in spreadsheet. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
14 | R_Light_CFL |  | Removed this measure as CFLs are not included in the portfolio post-PY2017 | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
15 | R_Light_Occupancy Sensor |  | New TRM measure in PY18 | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
16 | R_PlugProcess_Adv Power Strip |  | Values changed slightly with implementation of calculations in spreadsheet. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
17 | R_WH_faucet aerators |  | Major changes in calculation methodology and assumptions per EM&V | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
18 | R_WH_showerhead |  | Major changes in calculation methodology and assumptions per EM&V | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
19 | R_Peer group comparison |  | Energy saving value changed from 0.89% to 0.80% per EM&V | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
20 | R_Direct install kits |  | Removed this measure since kit components are addressed individually | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
21 | R_Home energy kits |  | Removed this measure since kit components are addressed individually | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
22 | R_HVAC_Smart thermostat |  | New prescriptive measure that debuted in PY17 but was inadvertently missing from PY17 TRM. A very low volume of projects were rebate in PY17. | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
23 | R_HVAC_VRF Split |  | Enhanced case requirement increased from 16 to 18 per Honeywell | Resolved | For PY18 TRM | Per PY18 TRM Changes Log
24 | R_Light_LED |  | Added EISA baseline analysis and citations | Resolved | 2017-09-08 | From "Revision Log (internal" tab hidden in PY18 TRM
25 | C_Appliance_Refrigerator R_Appliance_Refrigerator |  | Demand using 70% duty cycle rather than 100% | Resolved | 2017-09-14 | From "Revision Log (internal" tab hidden in PY18 TRM
26 | General |  | For all the following, double-checked calculations and added calculations where none were present: ◦ C_Kitchen_Freezer ◦ C_Kitchen_Refrigerator ◦ C_Spray_Nozzle -- calculations added to show how final numbers were derived ◦ C_IceMaker (calcs added) ◦ C_ElectricSteamCooker ◦ C_Electric Griddle (calcs added) ◦ C_Fryer (calcs added) ◦ C_Holding Cabinet ◦ C_Convection Oven ◦ C_Combination Oven | Resolved | 2017-09-14 | From "Revision Log (internal" tab hidden in PY18 TRM
27 | C_Kitchen_DCV |  | C_Kitchen_DCV final savings value changed from kWh/year to kWh/hp/year | Resolved | 2017-09-14 | From "Revision Log (internal" tab hidden in PY18 TRM
28 | Definitions |  | Added definitions page | Resolved | 2017-09-21 | From "Revision Log (internal" tab hidden in PY18 TRM
29 | Reference |  | Added Reference tables page | Resolved | 2017-09-21 | From "Revision Log (internal" tab hidden in PY18 TRM
30 | R_WH_LFShowerhead |  | Added Showerheads from v1.3. changed MFDI pf from 0.51 to 0.96 | Resolved | 2017-09-21 | From "Revision Log (internal" tab hidden in PY18 TRM
31 | R_WH_Faucet Aerator |  | Added FaucetAerators from v1.3. changed MFDI pf from 0.59 to 0.96 | Resolved | 2017-09-21 | From "Revision Log (internal" tab hidden in PY18 TRM
32 | General |  | Remove all incentive dollar values because these do not belong in TRM, they are subject to change at Program discretion. | Resolved | 2017-09-21 | From "Revision Log (internal" tab hidden in PY18 TRM
33 | C_Light_Refrigerated Case |  | Added interactive factors to calculation | Resolved | 2017-09-21 | From "Revision Log (internal" tab hidden in PY18 TRM
34 | General |  | Augmented definitions | Resolved | 2017-09-21 | From "Revision Log (internal" tab hidden in PY18 TRM
35 | R_HVAC_Window¦VRF |  | Split R_HVAC_Window¦VRF into 2 distinct tabs | Resolved | 2017-10-13 | From "Revision Log (internal" tab hidden in PY18 TRM
36 | R_PlugProcess_Adv Power Strip |  | Remove R_smart strip "average/unknown". If not explicitly Tier 2, then it is Tier 1. | Resolved | 2017-11-15 | From "Revision Log (internal" tab hidden in PY18 TRM
37 |  |  | General rounding corrections (2 decimal places for kWh, 3 for kW) | Resolved | 2018-03-15 | From "Revision Log (internal" tab hidden in PY18 TRM
38 | R_Appliance_Clothes Washer |  | Filled in formulas for Clothes Washers, Tier 1,2,3 | Resolved | 2018-03-15 | From "Revision Log (internal" tab hidden in PY18 TRM
39 | R_HVAC_Smart Thermostat |  | Added tab for R_Smart Thermostat | Resolved | 2018-03-18 | From "Revision Log (internal" tab hidden in PY18 TRM
40 | Introduction |  | Added Introduction tab | Resolved | 2018-05-10 | From "Revision Log (internal" tab hidden in PY18 TRM
41 | Key Metrics |  | Added Key Metrics tab | Resolved | 2018-05-10 | From "Revision Log (internal" tab hidden in PY18 TRM
42 | Savings Factors |  | Added Savings Factors tab | Resolved | 2018-05-10 | From "Revision Log (internal" tab hidden in PY18 TRM
43 | Definitions |  | Renamed 'Definitions' tab to 'Glossary' tab | Resolved | 2018-05-10 | From "Revision Log (internal" tab hidden in PY18 TRM
44 | Reference |  | Redistributed reference tables to Savings Factors and EFLH tabs, then removed Reference tab. | Resolved | 2018-05-10 | From "Revision Log (internal" tab hidden in PY18 TRM
45 | Custom |  | Added Custom section tab | Resolved | 2018-05-18 | From "Revision Log (internal" tab hidden in PY18 TRM
46 | R_FaucetAerator |  | Remove old R_faucetaerator tab with proposed methodology | Resolved | 2018-05-21 | From "Revision Log (internal" tab hidden in PY18 TRM
47 | R_FaucetAerator |  | Add new R_faucetaerator tab with new OD approved methodology | Resolved | 2018-05-21 | From "Revision Log (internal" tab hidden in PY18 TRM
48 | R_Showerhead |  | Remove old R_showerhead tab with proposed methodology | Resolved | 2018-05-21 | From "Revision Log (internal" tab hidden in PY18 TRM
49 | R_Showerhead |  | Add new R_showerhead tab with new OD approved methodology | Resolved | 2018-05-21 | From "Revision Log (internal" tab hidden in PY18 TRM
50 | Master EUL |  | Added Master EUL tab. Cut EUL table from Key Metrics tab. | Resolved | 2018-05-23 | From "Revision Log (internal" tab hidden in PY18 TRM
51 | Master EUL |  | Made individual entry tab measures lives link to the Master EUL tab | Resolved | 2018-05-23 | From "Revision Log (internal" tab hidden in PY18 TRM
52 | C_Transformers |  | C_Transformers tab as this measure is now custom | Resolved | 2018-05-23 | From "Revision Log (internal" tab hidden in PY18 TRM
53 | R_CFL |  | Removed R_CFL tab | Resolved | 2018-05-23 | From "Revision Log (internal" tab hidden in PY18 TRM
54 | Master EUL |  | Master EUL table. There was some inconsistency between individual entries and Table entries. | Resolved | 2018-05-23 | From "Revision Log (internal" tab hidden in PY18 TRM
55 | C_Light_All |  | Added new measures: 3' Linear LED, 8' Linear LED, 4' T5/T5HO Linear LED | Resolved | 2018-06-01 | From "Revision Log (internal" tab hidden in PY18 TRM
56 | C_Light_All |  | Updated Linear LED wattages | Resolved | 2018-06-01 | From "Revision Log (internal" tab hidden in PY18 TRM
57 | C_Light_All |  | Updated Corn Cob wattage ranges and values | Resolved | 2018-06-01 | From "Revision Log (internal" tab hidden in PY18 TRM
58 | C_Light_All |  | Calculations link to EFLH and Savings Factor tab, instead of in-tab table | Resolved | 2018-06-01 | From "Revision Log (internal" tab hidden in PY18 TRM
59 | Key Metrics |  | Updated TRB table | Resolved | 2018-06-01 | From "Revision Log (internal" tab hidden in PY18 TRM
60 | C_HVAC_Chiller_WKST |  | Added Chiller worksheet | Resolved | 2018-06-03 | From "Revision Log (internal" tab hidden in PY18 TRM
61 | C_HVAC_AC_WKST |  | Added AC worksheet | Resolved | 2018-06-03 | From "Revision Log (internal" tab hidden in PY18 TRM
62 | C_Light_Dimmable(Nonlinear LED) |  | Linked to EFLH tab and Savings Factors tab (interactive factors), then removed excess EFLH tables that are not in use. | Resolved | 2018-06-03 | From "Revision Log (internal" tab hidden in PY18 TRM
63 | Key Metrics |  | Updated Net-to-gross table values and reference for residential LED value change from 0.79 to 0.5 | Resolved | 2018-06-04 | From "Revision Log (internal" tab hidden in PY18 TRM
64 | General |  | General format standardizations. | Resolved | 2018-06-04 | From "Revision Log (internal" tab hidden in PY18 TRM
65 | C_PumpMotor_PE Motor |  | Added Premium Efficiency Motor entry from PY15 TRM. | Resolved | 2018-06-19 | From "Revision Log (internal" tab hidden in PY18 TRM
66 | C_PumpMotor_PE Motor |  | Changed efficiency values to reflect updated standards. | Resolved | 2018-06-21 | From "Revision Log (internal" tab hidden in PY18 TRM
67 | R_HVAC_VRF Split |  | Changed enhanced SEER from 16 to 18. | Resolved | 2018-06-22 | From "Revision Log (internal" tab hidden in PY18 TRM
68 | C_Kitchen_Combination Oven C_Kitchen_Convection Oven |  | CF… should be 1.0 like other commercial kitchen? | TBD | 2017-09-14 | From "Revision Log (internal" tab hidden in PY18 TRM
69 | C_Light_Energy Advantage | COMMERCIAL: Energy Advantage | Review/update | Resolved | 2018-11-15 | Per PY19 prioritization | No
70 | C_Light_Stairwell Bi-Level | COMMERCIAL: Stairwell Bi-level Dimming Controls | Review/update | Resolved | 2018-11-14 | Per PY19 prioritization | No
71 | C_HVAC_Chiller, C_HVAC_Chiller_WKST | COMMERCIAL: Chiller | Chillers - review approach in its entirety | Resolved | 2018-11-15 | Per EEM talking points for AEG team | No
72 | C_Light_Dimmable(Nonlinear LED) | COMMERCIAL: Dimmable Lighting (Non-Linear LED) | Review/update | Resolved | 2018-11-08 | Per PY19 prioritization | No
73 | C_HVAC_EMS | COMMERCIAL: Energy Management System | Energy Management Controls (2% of PY16 portfolio) - Deemed savings are unsourced. Revisit methodology and determine best approach for revisions to this measure | Resolved | 2019-01-05 | Per EEM talking points for AEG team | No
74 | C_Light_Occupancy Sensor | COMMERCIAL: Light Occupancy Sensor | Review/update | Resolved | 2018-10-17 | Per PY19 prioritization | No
75 | C_Lighting_Refrigerated Case | COMMERCIAL: Refrigerated Case Lighting | Review/update | Resolved | 2018-11-11 | Per PY19 prioritization | No
76 | C_WH_Solar | COMMERCIAL: Solar Water Heater | Review/update | Resolved | 2019-01-22 | Per PY19 prioritization | No
77 | C_PumpMotor_VFD Booster Pump | COMMERCIAL: VFD Booster Pump | VFDs (0.8% of PY16 portfolio) - review approach in its entirety | Resolved | 2019-01-02 | Per EEM talking points for AEG team | No
78 | C_PumpMotor_VFD Pool Pump | COMMERCIAL: VFD Pool Pump | VFDs (0.8% of PY16 portfolio) - review approach in its entirety | Resolved | 2019-01-02 | Per EEM talking points for AEG team | No
79 | C_HVAC_VFD Water Pump | COMMERCIAL: VFD Water Pump | VFDs (0.8% of PY16 portfolio) - review approach in its entirety | Resolved | 2018-12-20 | Per EEM talking points for AEG team | No
80 | C_HVAC_VRF | COMMERCIAL: VRF | Review/update | Resolved | 2019-01-04 | Per PY19 prioritization | No
81 | C_Light_General | COMMERCIAL_Lighting | All lighting (27% of PY16 portfolio) - Separate Exterior Lighting from Interior Lighting and create new spreadsheet Tab - Need general update of all parameters - Need to revisit/document source of cooling load interactive factors (tracked back to PY15 TRM and they are unsourced) | Resolved | 2018-11-04 | Per EEM talking points for AEG team | No
82 | C_Light_General | COMMERCIAL_Lighting | Non-linear LED (~23% of PY16 portfolio) - Revisit overall methodology - Revisit percent incandescent/CFL mix based on market research - Revisit baseline wattages (currently not accounting for EISA, although they do account for 80% CFL assumption for A-19, which could be overly conservative) | Resolved | 2018-11-04 | Per EEM talking points for AEG team | No
83 | Custom | Custom Measures - Transformers | Review/update | Resolved | 2018-10-17 | Per PY19 prioritization | No
84 | Overall | N/A | Address formal definition of demand savings (currently not consistent between measures) and calculation of such demand savings. | Resolved | 2018-12-17 | Per EEM talking points for AEG team | No
85 | Overall | N/A | Inclusion of guidance for non-deemed savings calculation methods for certain measures | Resolved | 2018-12-17 | Per EEM talking points for AEG team | No
86 | Overall | N/A | Net to gross ratios with consideration of spillover, market effects, market transformation. Update using secondary information for PY19 TRM. | Resolved | 2018-12-18 | Per EEM talking points for AEG team | No
87 | Overall | N/A | Net to gross ratios with consideration of spillover, market effects, market transformation. Update using primary data for Hawai‘i for future TRM. | Unresolved | 2018-10-17 | Consider leveraging 2019 Baseline Study to survey participants and non-participants. | No
88 | Overall | N/A | Consistency, formatting for priority measures throughout document: - Standardize demand language (coincident peak) - Clean up language that refers to incorrect tables, numbers, values, etc. - Include sources for all deemed savings assumptions - Fix cell sizes so no text is hidden (also apply this to entire workbook) - S/R Hawaii with Hawai‘i, Energy Star with ENERGY STAR - Add asterisks to tabs that have been updated - Check bullet format - Complete QC checklists | Resolved | 2019-01-05 | Per EEM talking points for AEG team | No
89 | Overall | N/A | Review/update HOU/EFLH values using Hawai‘i-specific load shape data where possible. | Resolved | 2018-12-18 |  | No
90 | Overall | N/A | Review/update CF values using Hawai‘i-specific load shape data where possible. | Resolved | 2018-12-18 |  | No
91 | Overall | N/A | Review, update, and add definitions to Glossary as needed | Resolved | 2018-10-17 |  | No
92 | Overall | N/A | Review/update EULs and, where applicable, RULs. | Resolved | 2018-11-08 |  | No
93 | Overall | N/A | Check consistency/links between Master EUL table and individual measure entries. | Resolved | 2018-11-12 |  | No
94 | Overall | N/A | Review/update lighting/cooling interactive effect factors using Hawai‘i-specific load shape data for residential and benchmarking with secondary data for commercial. | Resolved | 2018-11-11 |  | No
95 | Overall | N/A | Update TOC; add hyperlink in each sheet to return to TOC to ease navigation | Resolved | 2018-10-22 |  | No
96 | Overall | N/A | Add update status for each measure that has been revised for PY19. | Resolved | 2019-01-05 |  | No
97 | R_Light_LED | RESIDENTIAL: LED | Review/update | Resolved | 2018-10-28 | Per PY19 prioritization | No
98 | R_Light_Occupancy Sensor | RESIDENTIAL: Lighting Occupancy Sensor | Review/update | Resolved | 2018-10-17 | Per PY19 prioritization | No
99 | R_Appliance_Refrigerator | RESIDENTIAL: Refrigerator | Review/update | Resolved | 2018-12-17 | Per PY19 prioritization | No
100 | R_WH_SWH | RESIDENTIAL: Solar Water Heater | Solar hot water heater (1.6% of PY16 portfolio) - Revisit baseline and methodology and make consistent with other input assumptions in TRM (e.g., people per house, hot water temperature assumptions, hot water usage assumptions) | Resolved | 2019-01-22 | Per EEM talking points for AEG team | No
101 | R_WH_SWH Tune Up | RESIDENTIAL: Solar Water Heater Tune Up | Review/update | Resolved | 2018-10-17 | Per PY19 prioritization | No
102 | R_PumpMotor_VFD Pool Pump | RESIDENTIAL: VFD Pool Pump | Review/update | Resolved | 2019-01-02 | Per PY19 prioritization | No
103 | R_HVAC_VRF Split | RESIDENTIAL: VRF Split | Variable Refrigerant Flow (1.5% of PY16 portfolio) - Need to document sources for deemed savings assumptions and/or consider a revised approach | Resolved | 2019-01-04 | Per EEM talking points for AEG team | No
104 | R_Other_Peer Group Comparison | Peer Program | The Description says the reports are monthly. The Program Criteria is incorrect (has information for solar WH tune-ups). Update text, but not savings. | Resolved | 2018-11-12 |  | No
105 | Overall | N/A | Consider page numbers if published format will be PDF; remove proprietary language from header/footer | TBD | 2018-12-03 |  | No
106 | Overall | N/A | Update Issues Log | Resolved | 2019-01-05 |  | No
107 | Overall | N/A | Update and rename Changes sheet | Resolved | 2019-01-05 |  | No
108 | Overall | N/A | Update Introduction | Resolved | 2018-12-17 |  | No
109 | Overall | N/A | Update Signature sheet | Resolved | 2019-01-05 |  | No
110 | Overall | N/A | Review/update values/approach for avoided costs and total resource benefits | Resolved | 2019-07-02 |  | No
111 | Overall | N/A | Review/update system loss factors | Resolved | 2019-01-05 |  | No
112 | R_Appliance_Dishwasher | RESIDENTIAL: Dishwasher | Review/update | Resolved | 2019-04-02 | This is a new measure for PY19 | No
113 | R_PlugProcess_Switch Plug, R_PlugProcess_Switch_Plug_CALC | RESIDENTIAL: Switch Plug | Review/update | Resolved | 2019-04-02 | This measure was added mid-year during PY18 | No
114 | R_Appliance_Air Purifier | RESIDENTIAL: Air Purifier | Review/update | Resolved | 2019-04-02 | This measure was added mid-year during PY18 | No
115 | R_HVAC_Dehumidifier | RESIDENTIAL: Dehumidifier | Review/update | Resolved | 2019-04-02 | This measure was added mid-year during PY18 | No
116 | R_HVAC_Window AC, R_HVAC_Central AC Retrofit | RESIDENTIAL: Window AC, Central A/C Retrofit | Add measures to the RESIDENTIAL: HVAC Savings Calculator | Resolved | 2019-04-16 |  | No
117 | Overall | N/A | Consider adding tables of annual ISR and PF values for measures, as applicable, in future TRM update | TBD | 2019-04-02 | Currently we are using lifetime values and applying the same factors to first year and lifetime savings | No
118 | Overall | N/A | Consider including residential dishwasher, switch plug, air purifier, dehumidifier and window AC measure in PY20 TRM prioritization process since only a light review was conducted for PY19 | TBD | 2019-04-02 | Due to small program-level savings expected from these measures and the fact that they were reviewed (albeit lightly) for PY19 TRM, the priority may be low. | No
119 | R_Light_LED | RESIDENTIAL: LED | (See item #154) | TBD
120 | R_WH_SWH, R_WH_SWH Tune Up | RESIDENTIAL: Solar Water Heater, Solar Water Heater Tune Up | Consider pros and cons of billing analysis approach for solar water heater and tune-up measures | TBD | 2019-04-02 | Include a review of Evergreen’s 2012 billing analysis results to assess reasonableness of using findings for a new deemed savings value | No
121 | Overall | N/A | Apply findings from the AEG baseline study to update TRM measure savings assumptions, as appropriate | Resolved | 2021-01-18 | This is for measures where the baseline results from the Evergreen Economics study are referenced. All measures except those affected by EISA were updated for the PY20 TRM v1.0 (R_Light_LED and R_Light_Occupancy Sensor). Updates for the EISA-affected measures were addressed during mid-year update for PY20 TRM v2.0. | No
122 | R_PlugProcess_Switch Plug, R_PlugProcess_Adv Power Strip | RESIDENTIAL: Switch Plug, Advanced Power Strip | Consider researching and adding an in-service rate to the savings algorithms for these measures | TBD | 2019-04-04 | An ISR of less than 1 would likely be appropriate for these measures | No
123 | R_HVAC_Window AC, R_HVAC_AC_WKST | RESIDENTIAL: Window AC | Add additional capacity bins to measure and calculation worksheet; expansion should be applicable for dual inverter driven window AC | Resolved | 2020-02-11 | Revised from one bin (8,000-13,999 Btu/h) to multiple bins for PY19 TRM v2.0; updated for v2.1 to clarify min. efficiency requirement | No
124 | C_HVAC_AC & Heat Pump, C_HVAC_AC_HP_WKST | COMMERCIAL: AC & Heat Pump, AC & HP Worksheet | Complete review and update of measure description and calculation worksheet | Resolved | 2020-04-01 | Added packaged terminal AC/heat pump (PTAC/PTHP), vertical heat pump, and water source heat pump technologies to the measure and calculation worksheets; Revised baseline and efficient cases to reflect current efficiency standards | No
125 | R_WH_Faucet Aerator | RESIDENTIAL: Faucet Aerator | Add blended savings for online marketplace | Resolved | 2019-12-27 | Added table of deemed savings for online marketplace for PY19 TRM v2.0 | No
126 | R__WH_LFShowerhead | RESIDENTIAL: Low-Flow Showerhead | Add blended savings for online marketplace | Resolved | 2019-12-27 | Added table of deemed savings for online marketplace for PY19 TRM v2.0 | No
127 | C_HVAC_EMS | COMMERCIAL: Guest Room Energy Management System | Clarify definition for large and small hotel | Resolved | 2019-12-27 | Added definitions in PY19 TRM v2.0: Large = 100+ rooms, Small <100 rooms | No
128 | C_HVAC_Chiller_WKST | COMMERCIAL: Chiller | Fix errors in hidden Cells P6 and P7 | Resolved | 2019-12-27 | Made corrections in PY19 TRM v2.0 | No
129 | C_HVAC_Window AC, C_HVAC_WindowAC_WKST | COMMERCIAL: Window AC | Add new measure and calculation worksheet; have it be applicable for dual inverter driven window AC | Resolved | 2020-02-11 | Added to PY19 TRM v2.0; updated for v2.1 to clarify min. efficiency requirement | No
130 | R_HVAC_Central AC Retrofit, R_HVAC_AC_WKST | RESIDENTIAL: Central A/C Retrofit | Expand measure and calculation worksheet to allow for retrofit of pre-2006 vintage AC units | Resolved | 2019-12-27 | Made change in PY19 TRM v2.0 | No
131 | R_Light_Linear LED | RESIDENTIAL: Linear LED | Review and add new measure | Resolved | 2020-01-04 | Added to PY19 TRM v2.0 | No
132 | R_Light_Security Light | RESIDENTIAL: Security Light | Review and add new measure | Resolved | 2020-01-04 | Added to PY19 TRM v2.0 | No
133 | R_Light_Holiday String Light | RESIDENTIAL: Holiday String Light | Review and add new measure | Resolved | 2020-01-04 | Added to PY19 TRM v2.0 | No
134 | R_Light_LED | RESIDENTIAL: LED | Update NTG ratio for upstream LEDs to include market effects | Resolved | 2020-01-04 | Revised in PY19 TRM v2.0 | No
135 | R_HVAC_Ductless | RESIDENTIAL: Ductless Split Systems | Change the minimum SEER to 16 SEER | Resolved | 2020-02-11 | Revised in PY19 TRM v2.1 | No
136 | Cover Page | N/A | Update of cover page for PY20 TRM | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
137 | TOC | N/A | Update of TOC to include new and modified content for PY20 TRM | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
138 | Changes from PY19 | N/A | List of changes made for PY20 TRM | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
139 | Introduction | N/A | Review/update of text for PY20 TRM | Resolved | 2020-04-01 | Revised in PY20 TRM | No
140 | Signatures | N/A | Update of Signature sheet for PY20 TRM | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
141 | C&S Tracking | N/A | Addition of Codes & Standards tracking sheet | Resolved | 2021-01-18 | New addition to PY20 TRM v1.0 to summarize codes and standards (C&S) that affect TRM measures; Change between v1.0 and v2.0 of PY20 TRM: Added Jul. 1, 2022 effective date for 45 lm/W GSIL baseline. | No
142 | Key Metrics | N/A | Addition of detail to clarify how the TRB is calculated for single and dual baseline measures | Resolved | 2020-06-15 | Added equations and detailed explanations in the TRB section of the Key Metrics sheet to show how the TRB is to be calculated for single baseline measures and dual baseline measures; Added a table that lists measures with dual baselines | No
143 | Issues Log | N/A | Update of Issues Log for PY20 TRM | Resolved | 2021-01-18 | Revised in PY20 TRM | No
144 | C_HVAC_VRF, C_HVAC_VRF_WKST | Commercial: VRF; Commercial: HVAC Savings Calculator - Variable Refrigerant Flow Systems | Addition of water-source VRFs to measure description and calculation worksheet | Resolved | 2020-04-01 | Added an option for water-source VRFs to measure and calculation worksheet; Clarified the baseline conditions | No
145 | C_Light_General | COMMERCIAL: Interior Lighting | Update of dual baseline measures to clarify two baseline periods; update of measures affected by EISA legislation to address recent rulings | Resolved | 2021-01-18 | Updated during mid-year PY20 TRM update process. Updates reflect 1) EISA ruling / HPUC decision and 2) dual baseline clarity. | No
146 | C_Light_Dimmable(Nonlinear LED) | COMMERCIAL: Dimmable Lighting (Non-Linear LED) | Update to address recent rulings related to EISA | Resolved | 2021-01-18 | Updated during mid-year PY20 TRM update process. Updates reflect 1) EISA ruling / HPUC decision and 2) dual baseline clarity. | No
147 | C_Lighting_Refrigerated Case | COMMERCIAL: Refrigerated Case Lighting | Update to clarify two baseline periods | Resolved | 2020-04-01 | Updates add clarity to two baseline periods | No
148 | C_Light_Energy Advantage | COMMERCIAL: Energy Advantage | Addition of detail to clarify how savings are calculated for this measure | Resolved | 2020-04-01 | Added Measure Details and Algorithms to clarify the savings estimation approaches; Added section to map key variables from the Amplify tool to variables in the savings algorithms | No
149 | R_Appliance_Clothes Washer | RESIDENTIAL: Clothes Washer | Update of shares of homes with electric clothes dryers and electric water heating | Resolved | 2020-04-01 | Updated data from Evergreen's baseline study with data from AEG's 2019 baseline study | No
150 | R_Appliance_Dishwasher | RESIDENTIAL: Dishwasher | Update of shares of homes with electric water heating | Resolved | 2020-04-01 | Updated data from Evergreen's baseline study with data from AEG's 2019 baseline study | No
151 | R_Appliance_Refrigerator | RESIDENTIAL: Refrigerator and Freezer | Clarification of the dual baseline savings as well as adjustments to savings for units turned in through the program | Resolved | 2020-04-01 | Updates add clarity to two baseline periods and revise savings approach for tuned in units | No
152 | R_HVAC_Whole House Fan | RESIDENTIAL: Whole-House Fan | Complete review and update of measure | Resolved | 2020-04-02 | Updated savings approach using Hawaii-specific model | No
153 | R_HVAC_Solar Attic Fan | RESIDENTIAL: Solar Attic Fan | Complete review and update of measure | Resolved | 2020-04-02 | Updated savings approach using Hawaii-specific model | No
154 | R_Light_LED | RESIDENTIAL: LED | Update to address recent rulings related to EISA; update of shares of homes with air conditioning | Resolved | 2021-01-18 | Updated during mid-year PY20 TRM update process. Updates reflect 1) EISA ruling / HPUC decision; 2) dual baseline clarity; and 3) new data from AEG's 2019 baseline study | No
155 | R_Light_Linear LED | RESIDENTIAL: Linear LED | Update of shares of homes with air conditioning | Resolved | 2020-04-01 | Updated data from Evergreen's baseline study with data from AEG's 2019 baseline study | No
156 | R_Light_Occupancy Sensor | RESIDENTIAL: Lighting Occupancy Sensor | Update to address recent rulings related to EISA; update of shares of homes with air conditioning | Resolved | 2021-01-18 | Updated during mid-year PY20 TRM update process. Updates reflect 1) EISA ruling / HPUC decision; 2) dual baseline clarity; and 3) new data from AEG's 2019 baseline study | No
157 | R_Light_Security Light | RESIDENTIAL: Security Light | Update to address recent rulings related to EISA | Resolved | 2021-01-18 | Updated during mid-year PY20 TRM update process. Updates reflect EISA ruling / HPUC decision. | No
158 | R_PlugProcess_Adv Power Strip | RESIDENTIAL: Advanced Power Strips | Updated counts of audio / visual and computing equipment; unhid row | Resolved | 2020-04-01 | Updated data from Evergreen's baseline study with data from AEG's 2019 baseline study | No
159 | R_WH_Faucet Aerator | RESIDENTIAL: Faucet Aerator | Complete review and update of measure | Resolved | 2020-04-02 | This measure is affected by the new state standards for faucet aerators and low-flow showerheads; Revised the baseline definition to assume early retirement with a dual baseline for the direct install program and replace on burnout with a single baseline for the online marketplace | No
160 | R__WH_LFShowerhead | RESIDENTIAL: Low-Flow Showerhead | Complete review and update of measure | Resolved | 2020-04-02 | This measure is affected by the new state standards for faucet aerators and low-flow showerheads; Revised the baseline definition to assume early retirement with a dual baseline for the direct install program and replace on burnout with a single baseline for the online marketplace | No
161 | R_WH_Heat Pump | RESIDENTIAL: Heat Pump Water Heater | Complete review and update of measure | Resolved | 2020-04-02 | Revised the baseline assumptions to meet current federal standards; updated overall approach to be consistent with best practices and SWH measure | No
162 | R_WH_SWH | RESIDENTIAL: Solar Water Heater | Update of average number of occupants by home type and county | Resolved | 2020-04-01 | Updated data from Evergreen's baseline study with data from AEG's 2019 baseline study | No
163 | C_Refrig_Evap Motor Control | COMMERCIAL: Evaporator Motor Controls | Add new measure | Resolved | 2021-01-18 | Added to PY20 TRM v2.0 | No
164 | C_Refrig_Add Case Doors | COMMERCIAL: Adding Doors to Refrigerated Cases | Add new measure | Resolved | 2021-01-18 | Added to PY20 TRM v2.0 | No
165 | C_Refrig_FHP Control | COMMERCIAL: Floating Head Pressure Controls | Add new measure | Resolved | 2021-01-18 | Added to PY20 TRM v2.0 | No
166 | C_HVAC_Chiller, C_HVAC_Chiller_WKST | COMMERCIAL: Chiller; COMMERCIAL: Chiller Savings Calculator | Correct a cell reference error in cell H6 | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
167 | C_HVAC_AC & Heat Pump, C_HVAC_AC_HP_WKST | COMMERCIAL: A/C & Heat Pump; COMMERCIAL: AC and Heat Pump Savings Calculator | Remove EER qualification requirement for high efficiency equipment of < 65 kBtu/h capacity; revisit demand savings calculation | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
168 | C_HVAC_VRF, C_HVAC_VRF_WKST | COMMERCIAL: VRF; COMMERCIAL: HVAC Savings Calculator - Variable Refrigerant Flow Systems | Remove EER qualification requirement for high efficiency equipment of < 65 kBtu/h capacity; revisit demand savings calculation | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
169 | R_HVAC_Ductless, R_HVAC_AC_WKST | RESIDENTIAL: Ductless Split Systems; RESIDENTIAL: HVAC Savings Calculator | Remove EER qualification requirement for high efficiency equipment of < 65 kBtu/h capacity; revisit demand savings calculation | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
170 | R_HVAC_Central AC Retrofit, R_HVAC_AC_WKST | RESIDENTIAL: Central A/C Retrofit; RESIDENTIAL: HVAC Savings Calculator | Remove EER qualification requirement for high efficiency equipment of < 65 kBtu/h capacity; revisit demand savings calculation | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
171 | Master EUL | N/A | Add EULs for new commercial refrigeration measures | Resolved | 2021-01-18 | Revised in PY20 TRM v2.0 | No
172 | Cover Page | N/A | Update of cover page for PY21 TRM | Resolved | 2021-03-31 | Revised in PY21 TRM v1.0 | No
173 | TOC | N/A | Update of TOC to include new and modified content for PY21 TRM | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
174 | Changes from PY20 | N/A | List of changes made for PY21 TRM | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
175 | Introduction | N/A | Review/update of text for PY21 TRM | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
176 | Signatures | N/A | Update of Signature sheet for PY21 TRM | Resolved | 2021-03-31 | Revised in PY21 TRM v1.0 | No
177 | C&S Tracking | N/A | Update of Codes & Standards tracking sheet to include R407 of Hawaii State Energy Code for Cool Wall measure | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
178 | Key Metrics | N/A | Addition of GHG Calculator | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
179 | Issues Log | N/A | Update of Issues Log for PY21 TRM | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
180 | R_HVAC_Window AC, R_HVAC_Ductless, R_HVAC_Central AC Retrofit, R_HVAC_AC_WKST, C_HVAC_Chiller, C_HVAC_Chiller_WKST, C_HVAC_AC & Heat Pump, C_HVAC_AC_HP_WKST, C_HVAC_Window AC, C_HVAC_WindowAC_WKST, C_HVAC_VRF, C_HVAC_VRF_WKST | RESIDENTIAL: Window AC, Ductless Split Systems, and Central AC Retrofit COMMERCIAL: Chiller, AC & Heat Pump, Window AC, and VRF | • The capacity is now defined as “Rated cooling capacity” or “Rated capacity” in the measure entries to clarify that the intention is to calculate savings with the capacity determined at AHRI Standard Rating Conditions. • The HVAC worksheets now specify “Enter Rated AC or HP Capacity (Btu/h)” or “Enter rated chiller tonnage.” | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
181 | Custom | Commercial Kitchen Dishwasher | Clarification of description | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
182 | R_PlugProcess_Adv Power Strip | RESIDENTIAL: Advanced Power Strip | Complete review and update of measure | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
183 | R_Electronics_Television | RESIDENTIAL: Television | Complete review and update of measure | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
184 | C_BEnvelope_Window Film | COMMERCIAL: Window Film | Complete review and update of measure | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
185 | R_BEnvelope_Cool Wall | RESIDENTIAL: Cool Wall | Addition of new measure | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
186 | R_Light_Solar Tube | RESIDENTIAL: Solar Light Tube | Addition of new measure | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
187 | Master EUL | N/A | Update of EULs for new/revised PY21 measures | Resolved | 2021-03-16 | Revised in PY21 TRM v1.0 | No
188 | N/A | N/A | Revise headers, footers, and page set-up for printing to PDF | Resolved | 2021-03-31 | See file named "Instructions for Printing the Hawaii TRM to a PDF" | No
189 | Cover Page | N/A | Update of cover page for PY22 TRM | Resolved | 2022-06-02 | Revised in PY22 TRM v1.0 | No
190 | TOC | N/A | Update of TOC to include new and modified content for PY22 TRM | Resolved | 2022-03-16 | Revised in PY22 TRM v1.0 | No
191 | Changes from PY21 | N/A | List of changes made for PY22 TRM | Resolved | 2022-03-16 | Revised in PY22 TRM v1.0 | No
192 | Introduction | N/A | Review/update of text to reflect updated dates | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
193 | Signatures | N/A | Update of Signature sheet for PY22 TRM | Resolved | 2022-06-02 | Revised in PY22 TRM v1.0 | No
194 | C&S Tracking | N/A | Addition of new and existing measures and inclusion of several types of building stretch codes | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
195 | Key Metrics | N/A | Update of avoided costs, update of system loss factors, and addition of the new Commercial LED Downlight Retrofit measure to the list of measures with a dual baseline | Resolved | 2022-03-16 | Revised in PY22 TRM v1.0 | No
196 | Master EUL | N/A | Update of EULs for new/revised PY22 measures | TBD |  | Revised in PY22 TRM v1.0
197 | Issues Log | N/A | Update of Issues Log for PY22 TRM | Resolved | 2022-06-02 | Revised in PY22 TRM v1.0 | No
198 | Custom | Custom | Addition of a section about the Custom Project Guidance Document; removal of examples about the custom commercial dishwasher measure and custom commercial heat pump water heater measure since there are now prescriptive options for both measure types | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
199 | C_Appliance_Refrigerator | Commercial Appliance Refrigerator | Complete review and update of measure | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
200 | C_Kitchen_Demand-Controlled Ventilation | Commercial Kitchen Demand-Controlled Ventilation | Complete review and update of measure | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
201 | C_Kitchen_Freezer | Commercial Kitchen Freezer | Complete review and update of measure | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
202 | C_Kitchen_Refrigerator | Commercial Kitchen Refrigerator | Complete review and update of measure | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
203 | C_Kitchen_Dishwasher | Commercial Kitchen Dishwasher | Addition of new measure | Resolved | 2022-03-16 | Revised in PY22 TRM v1.0 | No
204 | C_HVAC_Chiller, C_HVAC_Chiller_WKST | Commercial Chiller and Chiller Worksheet | Temporary change to program eligibility; modifications to the calculator to prevent use for custom chiller projects | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
205 | C_HVAC_AC & Heat Pump, C_HVAC_AC_HP_WKST | Commercial AC and Heat Pump and AC and Heat Pump Worksheet | Temporary change to program eligibility | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
206 | C_Light_Downlight Retrofit | Commercial LED Downlight Retrofit | Addition of new measure | Resolved | 2022-03-16 | Revised in PY22 TRM v1.0 | No
207 | C_WH_Heat Pump | Commercial Heat Pump Water Heater | Addition of new measure | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
208 | R_HVAC_Ceiling Fan | Residential Ceiling Fan | Designation of measure as "inactive" | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
209 | R_HVAC_Smart Thermostat | Residential Smart Thermostat | Complete review and update of measure | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
210 | R_WH_Heat Pump | Residential Heat Pump Water Heater | Expansion of measure to include larger capacity systems | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
211 | N/A | Residential Peer Group Comparison | Removal of TRM entry since Peer program has been discontinued | Resolved | 2022-02-26 | Revised in PY22 TRM v1.0 | No
212 | C_HVAC_VRF, C_HVAC_VRF_WKST | Commercial VRF and VRF Worksheet | Temporary change to program eligibility | Resolved | 2022-04-19 | Revised in PY22 TRM v1.0 | No
213 | Key Metrics | N/A | Removal of Peer program line item from NTG table | Resolved | 2022-04-19 | Revised in PY22 TRM v1.0 | No
214 | R_Light_LED | Residential Lighting: LED | Modification to program criteria | Resolved | 2022-04-19 | Revised in PY22 TRM v1.0 | No
215 | R_HVAC_Central AC Retrofit, R_HVAC_AC_WKST | Residential Central AC Retrofit and Worksheet | New baseline conditions, modified program criteria, and clarifications to existing content; creation of two separate entries - one for Jul-Dec and one for Jan-Jun | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
216 | R_HVAC_Ductless, R_HVAC_AC_WKST | Residential Ductless Split Systems and Worksheet | New baseline conditions and clarifications to existing content; creation of two separate entries - one for Jul-Dec and one for Jan-Jun | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
217 | R_Light_LED | Residential LED | New, temporary dual baseline measure for Molokai and Lanai | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
218 | C&S Tracking | C&S Tracking | New baseline conditions | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
219 | Key Metrics | Net-to-Gross Ratios | New NTGRs for RGRID and BGRID | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
220 | C_Light_Downlight Retrofit | Commercial LED Downlight Retrofit | Clarifications to existing content | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
221 | C_Light_General, C_Light_Exterior, C_Light_Dimmable(Nonlinear LED), C_Lighting_Refrigerated Case, R_Light_LED, R_Light_Linear LED, and R_Light_Security Light | Multiple Lighting | Added language to several measures in the TRM to explain that LED retrofit kit engines qualify as applicable LED replacement lighting | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
222 | C_Light_Energy Advantage | Energy Advantage | Correction to typo | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
223 | R_WH_Heat Pump | Residential Heat Pump Water Heater | Addition of custom occupancy option | Resolved | 2023-02-20 | Revised in PY22 TRM v2.0
224 | C_HVAC_AC & Heat Pump and C_HVAC_AC_HP_WKST | Commercial HVAC: AC & Heat Pump | Update of efficiencies; expansion of measure | Resolved |  | Revised in PY23 TRM v1.0 | No
225 | C_Kitchen_Combination Oven | Commercial Kitchen: Combination Oven | Full measure review and update | Resolved |  | Revised in PY23 TRM v1.0 | No
226 | C_Kitchen_Convection Oven | Commercial Kitchen: Convection Oven | Full measure review and update | Resolved |  | Revised in PY23 TRM v1.0 | No
227 | C_Kitchen_Ice Machine | Commercial Kitchen: Ice Machine | Full measure review and update; expansion of measure | Resolved |  | Revised in PY23 TRM v1.0 | No
228 | C_Kitchen_LF Spray Nozzle | Commercial Kitchen: Low-Flow Spray Nozzle | Full measure review and update | Resolved |  | Revised in PY23 TRM v1.0 | No
229 | C_Kitchen_Freezer | Commercial Kitchen: Freezer | Update of ENERGY STAR criteria | Resolved |  | Revised in PY23 TRM v1.0 | No
230 | C_Kitchen_Refrigerator | Commercial Kitchen: Refrigerator | Update of ENERGY STAR criteria | Resolved |  | Revised in PY23 TRM v1.0 | No
231 | R_Appliance_Clothes Washer | Residential Appliance: Clothes Washer | Full measure review and update | Resolved |  | Revised in PY23 TRM v1.0 | No
232 | R_HVAC_Central AC Retrofit; and R_HVAC_AC_WKST | Residential HVAC: Central AC Retrofit | Update of efficiencies, effective Jul. 1, 2023 | Resolved |  | Revised in PY23 TRM v1.0 | No
233 | Key Metrics | Residential Water Heating: Heat Pump | Consider new NTGR - result was no change to NTGR table in Key Metrics | Resolved |  | No change to PY23 TR v1.0 | No
234 | Key Metrics | Greenhouse Gas Calculator | Update to use the most recent eGRID data | Resolved |  | Revised in PY23 TRM v1.0 | No
235 | C&S Tracking | Codes & Standards Tracking | Update of the set of baseline conditions in effect for PY23 | Resolved |  | Revised in PY23 TRM v1.0 | No
236 | C_PlugProcess_Water Cooler Tmr | Commercial Plug and Process: Water Cooler Timer | Label as inactive | Resolved |  | Revised in PY23 TRM v1.0 | No
237 | R_HVAC_Ductless; R_HVAC_Central AC Retrofit; and R_HVAC_AC_WKST | Residential HVAC: Central AC Retrofit and Residential HVAC: Ductless | Remove the measure sheets that have a sunset date of December 31, 2022 or June 30, 2023 (“R_HVAC_Central AC Retrofit_1,” “R_HVAC_Central AC Retrofit_2,” “R_HVAC_Ductless_1,” “R_HVAC_AC_WKST_1,” and “R_HVAC_AC_WKST_2). At the same time, rename “R_HVAC_Ductless_2, to remove the "_2" extension and remove "Version 2" from the measure title. Add in the PY23 version of the AC Retrofit measure (“R_HVAC_Central AC Retrofit_PY23”) and corresponding calculator (“R_HVAC_AC_WKST_PY23”). | Resolved |  | Revised in PY23 TRM v1.0 | No
238 | C_Light_General | Commercial Lighting, U-bend | Add an option for a single LED U-bend lamp to replace a single fluorescent U-bend lamp | Resolved |  | Revised in PY23 TRM v2.0 | No
239 | R_Appliance_Heat Pump Dryer | Residential Heat Pump Clothes Dryer | Add new measure | Resolved |  | Revised in PY23 TRM v2.0 | No
240 | R_Appliance_Induction Cooktop | Residential Induction Cooktop | Add new measure | Resolved |  | Revised in PY23 TRM v2.0 | No
241 | R_PlugProcess_EV Charger | Residential EV Charger | Add new measure | Resolved |  | Revised in PY23 TRM v2.0 | No
242 | Key Metrics | Greenhouse Gas Calculator | Update of greenhouse gas calculator to use the most recent eGRID data and other minor updates | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
243 | C&S Tracking | Codes & Standards Tracking | Update of the set of baseline conditions in effect for PY24 | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
244 | C_Light_Dimmable (Nonlinear LED) |  | Addition of sunset date | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
245 | C_PumpMotor_ECM |  | Full measure review and update | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
246 | C_Light_Energy Advantage |  | Minor measure updates and clarifications | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
247 | C_Light_General |  | Addition of sunset date and other updates | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
248 | C_Light_Horticulture |  | New measure | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
249 | C_HVAC_VRF and C_HVAC_VRF_WKST |  | Full review and update of measure and worksheet | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
250 | C_Light_Downlight Retrofit |  | Addition of sunset date and removal of early replacement option | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
251 | C_Other_Transformer and C_Other_Transformer_WKST |  | New measure and worksheet | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
252 | C_PumpMotor_VFD Pool Pump |  | Full measure review and update | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
253 | R_WH_Heat Pump |  | Update of baseline conditions and addition of option for custom entry of UEFs | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
254 | R_Light_LED |  | Addition of sunset date and removal of dual baseline option for underserved markets | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
255 | R_Light_Security Light |  | Addition of sunset date and removal of dual baseline measure | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
256 | R_WH_SWH |  | Addition of option for custom entry of household occupants and other minor updates | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
257 | R_PumpMotor_VFD Pool Pump |  | Full measure review and update | Resolved | 2024-04-12 | Revised in PY24 TRM v1.0 | No
258 | Key Metrics | Avoided Costs | Addition of PY25-PY27 Avoided Costs | Resolved | 2025-06-26 | Revised in PY24 TRM v1.2 | No
259 | R_Light_LED |  | Addition of new deemed savings for ES4H program | Resolved | 2025-06-26 | Revised in PY24 TRM v2.0 | No
260 | R_HVAC_Solar Attic Fan |  | Addition of savings for single family attached homes and clarification of the descriptions of CEER and SEER in the "Definitions & Assumptions" table | Resolved | 2025-06-26 | Revised in PY24 TRM v2.0 | No
261 | R_HVAC_Whole House Fan |  | Clarification of the descriptions of CEER and SEER in the "Definitions & Assumptions" table | Resolved | 2025-06-26 | Revised in PY24 TRM v2.0 | No
262 | C_CA_Receiver Tank |  | New measure | Resolved | 2025-06-26 | Revised in PY24 TRM v2.0 | No
263 | C_CA_No-Loss Condensate Drain |  | New measure | Resolved | 2025-06-26 | Revised in PY24 TRM v2.0 | No
264 | C_CA_VFD Compressor |  | New measure | Resolved | 2025-06-26 | Revised in PY24 TRM v2.0 | No
265 | Cover Page |  | Update of cover page | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
266 | TOC |  | Update of TOC to include new and modified content | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
267 | Changes from PY24 |  | List of changes made for PY25 TRM | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
268 | Introduction |  | Review/update of text to reflect updated dates for PY25 TRM | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
269 | Signatures |  | Update of Signature sheet for PY25 TRM | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
270 | C&S Tracking |  | Update of the set of baseline conditions in effect for PY25 | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
271 | Key Metrics |  | Update of greenhouse gas emission rates, system loss factors, and avoided costs | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
272 | PY25-PY27 Avoided Costs |  | Removal of sheet since the values are now in the Key Metrics sheet | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
273 | Master EUL |  | Update of EULs for revised PY25 measures | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
274 | Custom |  | Update of custom chiller text | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
275 | Issues Log |  | Update of Issues Log for PY25 TRM | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
276 | C_Light_General |  | Full update of measure, including removal of retired screw-base measures and addition of sunset dates for pin-base bulb measure and some linear lamp measures | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
277 | C_Light_Dimmable (Nonlinear LED) |  | Removal of retired screw-base lamp measure; update of pin-base lamp measure and addition of sunset date | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
278 | C_Lighting_Refrigerated Case |  | Update of lifetime savings and addition of sunset dates | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
279 | C_Light_Downlight Retrofit |  | Removal of measure (sunset date was Dec. 31, 2024) | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
280 | C_HVAC_VRF and C_HVAC_VRF_WKST |  | Update of resource list; removal of extraneous information from the calculator; did not reinstate full load efficiency requirement | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
281 | C_HVAC_AC & Heat Pump & C_HVAC_AC_HP_WKST |  | Update of resource list; did not reinstate full load efficiency requirement | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
282 | C_HVAC_Chiller & C_HVAC_Chiller_WKST |  | Expansion of measure to allow greater system capacities; did not reinstate full load efficiency requirement | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
283 | C_HVAC_Window AC & C_HVAC_WindowAC_WKST |  | Update to meet ENERGY STAR 5.0 criteria; did not reinstate the full load efficiency requirement | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
284 | C_Kitchen_Ice Machine |  | Correction to formulas used to calculate savings | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
285 | R_Appliance_Air Purifier |  | Full update of measure | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
286 | R_HVAC_Dehumidifier |  | Full update of measure | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
287 | R_Electronics_Soundbar |  | Full update of measure | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
288 | R_HVAC_Window AC & R_HVAC_AC_WKST |  | Update to meet ENERGY STAR 5.0 criteria | Resolved | 2025-06-26 | Revised in PY25 TRM v1.0 | No
136 | Cover Page |  | Update of cover page | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
137 | TOC |  | Update of TOC to include new and modified content | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
138 | Changes from PY25 |  | List of changes made for PY26 TRM | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
139 | Introduction |  | Minor revisions to text | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
140 | Signatures |  | Update for PY26 TRM | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
141 | C&S Tracking |  | Update of the set of baseline conditions in effect for PY26 | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
142 | Key Metrics |  | New section on calculating TRB for early replacement fluorescent lighting; other minor updates | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
143 | Master EUL |  | Update of EULs for new PY26 measures | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
144 | Issues Log |  | Update of Issues Log for PY26 TRM | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
145 | C_BEnvelope_Window Film |  | Full measure review and update | Resolved | 2026-06-08 | Revised in PY26 TRM v1.0 | Yes
146 | C_Kitchen_DCV |  | Full measure review and update | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
147 | C_HVAC_Chiller & C_HVAC_Chiller_WKST |  | Revision of language to refer to the current Hawaii State Energy Code | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
148 | C_HVAC_Window AC & C_HVAC_WindowAC_WKST |  | Update of baseline and high efficiency requirements | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
149 | C_Light_General |  | Addition of sunset dates for early replacement measures with fluorescent lamps in the baseline; removal of replace-on-burnout measures that reached their sunset date | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
150 | C_Light_Dimmable (Nonlinear LED) |  | Removal of measure since it reached its final sunset date | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
151 | C_Light_Occupancy Sensor |  | Update of default lighting type controlled with an occupancy sensor from linear fluorescent lamps to linear LED lamps | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
152 | C_Light_Energy Advantage |  | Update of language and algorithms to reflect fluorescent lighting ban | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
153 | C_HVAC_FEI-Certified Fan |  | Addition of new measure | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
154 | C_HVAC_DX-DOAS |  | Addition of new measure | Resolved | 2026-06-09 | Revised in PY26 TRM v1.0 | Yes
155 | C_WH_Smart Circ Pump |  | Addition of new measure | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
156 | C_Other_Transformer |  | Revision of program criteria to require transformers to exceed code for applications where average loading is greater than 35% | Resolved | 2026-06-09 | Revised in PY26 TRM v1.0 | Yes
157 | R_Appliance_Cooktop |  | Creation of new measure that combines a revised version of the previous induction cooktop measure with a new non-induction cooktop measure | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
158 | R_BEnvelope_Cool Wall |  | Revision of language to refer to the current Hawaii State Energy Code | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
159 | R_HVAC_Window AC & R_HVAC_AC_WKST |  | Update of baseline and high efficiency requirements | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
160 | R_HVAC_Ductless & R_HVAC_AC_WKST |  | Conversion of the efficiency metrics from SEER and EER to SEER2 and EER2 | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
161 | R_HVAC_Central AC Retrofit & R_HVAC_AC_WKST |  | Removal of the pre-2006 early replacement baseline option | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
162 | R_Light_Linear LED |  | Update of the deemed savings values for direct install linear LED lighting | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
163 | R_Light_Security Light |  | Update of the deemed savings values for direct install linear LED lighting | Resolved | 2026-06-03 | Revised in PY26 TRM v1.0 | Yes
164 | EFLH & CF |  | Addition of EFLHs and CFs for commercial building fans and dedicated outdoor air systems | Resolved | 2026-06-09 | Revised in PY26 TRM v1.0 | Yes

## Cover Page
Hawai‘i Energy Efficiency Program
July 1, 2026 through June 30, 2027
Technical Reference Manual (TRM)
PY 2026
V1.0
Measure Savings Calculations
June 30, 2026

## TOC
TABLE OF CONTENTS
General Information
Cover Page *
Changes from PY25 *
Introduction *
Signatures *
Glossary
Codes & Standards Tracking *
Key Metrics *
Master EUL *
Savings Factors
EFLH & CF *
Custom
Commercial Measures | Residential Measures
Appliance | Appliance
Refrigerator | Clothes Washer
Building Envelope | Heat Pump Clothes Dryer
Cool Roof | Clothes Dryer
Window Film * | Refrigerator
Kitchen | Dishwasher
Combination Oven | Air Purifier
Convection Oven | Cooktop *
Demand-Controlled Ventilation * | Building Envelope
Electric Griddle | Cool Wall *
Electric Steam Cooker | Electronics
Fryer | Television
Hot Food Holding Cabinet | Soundbar
Ice Machine | HVAC
Low-Flow Spray Nozzle | Window AC *
Freezer | Ductless Split Systems *
Refrigerator | AC Worksheet *
Dishwasher | Central AC Retrofit *
Energy Study Grant | Central AC Tune Up
Design Assistance | Ceiling Fan (Inactive)
Energy Study | Smart Thermostat
HVAC | Solar Attic Fan
Chiller * | Whole House Fan
Chiller Worksheet * | Dehumidifier
AC & Heat Pump | Lighting
AC & Heat Pump Worksheet | LED
Window AC * | Occupancy Sensor
Window AC Worksheet * | Linear LED *
Variable Frequency Drive Water Pump | Security Light *
Variable Refrigerant Flow AC | Holiday String Light
VRF Worksheet | Solar Light Tube
Energy Management System | Plug / Process
FEI-Certified Standalone Fan *(NEW)* | Advanced Power Strip
DX-DOAS *(NEW)*
Lighting | Switch Plug
General * | Switch Plug Calculation
Exterior | EV Charger
Refrigerated Case Light | Pump / Motor
Occupancy Sensor * | Variable Frequency Drive Pool Pump
Stairwell Bi-Level | Water Heating
Horticulture Lighting | Heat Pump
Energy Advantage * | Solar Water Heater
Plug / Process | Solar Water Heater Tune Up
Anti-Sweat Heater Control | Faucet Aerator
Vending Miser | Low-Flow Showerhead
Water Cooler Timer (Inactive)
Case Night Cover
Pump / Motor
Variable Frequency Drive Booster Pump
Electronically Commutated Motors
Premium Efficiency Motors
Variable Frequency Drive Pool Pump
Refrigeration
Evaporator Fan Motor Controls
Adding Doors to Refrigerated Cases
Floating Head Pressure Controls
Sub-metering
Condominium
Small Business
Water Heating
Solar
Heat Pump Water Heater
Smart Circulator Pump *(NEW)*
Compressed Air
Air Receiver Tank
No-Loss Condensate Drain
Variable Frequency Drive Compressor
Other
Re¦Retro-Commissioning
Distribution Transformer *
Transformer Worksheet
*Updated for PY26 TRM
*(NEW)* = Added to PY26 TRM

## Changes from PY25
MAJOR CHANGES FROM PY2025 TO PY2026 TRM
Return to TOC
Tab Name | Updates
Cover Page | Update of cover page
TOC | Update of TOC to include new and modified content
Changes from PY25 | List of changes made for PY26 TRM
Introduction | Minor revisions to text
Signatures | Update for PY26 TRM
C&S Tracking | Update of the set of baseline conditions in effect for PY26
Key Metrics | New section on calculating TRB for early replacement fluorescent lighting; other minor updates
Master EUL | Update of EULs for new PY26 measures
EFLH & CF | Addition of EFLHs and CFs for commercial building fans and dedicated outdoor air systems.
Issues Log | Update of Issues Log for PY26 TRM
C_BEnvelope_Window Film | Full measure review and update
C_Kitchen_DCV | Full measure review and update
C_HVAC_Chiller & C_HVAC_Chiller_WKST | Revision of language to refer to the current Hawaii State Energy Code
C_HVAC_Window AC & C_HVAC_WindowAC_WKST | Update of baseline and high efficiency requirements
C_Light_General | Addition of sunset dates for early replacement measures with fluorescent lamps in the baseline; removal of replace-on-burnout measures that reached their sunset date
C_Light_Dimmable (Nonlinear LED) | Removal of measure since it reached its final sunset date
C_Light_Occupancy Sensor | Update of default lighting type controlled with an occupancy sensor from linear fluorescent lamps to linear LED lamps
C_Light_Energy Advantage | Update of language and algorithms to reflect fluorescent lighting ban
C_HVAC_FEI-Certified Fan | Addition of new measure
C_HVAC_DX-DOAS | Addition of new measure
C_WH_Smart Circ Pump | Addition of new measure
C_Other_Transformer | Revision of program criteria to require transformers to exceed code for applications where average loading is greater than 35%
R_Appliance_Cooktop | Creation of new measure that combines a revised version of the previous induction cooktop measure with a new non-induction cooktop measure
R_BEnvelope_Cool Wall | Revision of language to refer to the current Hawaii State Energy Code
R_HVAC_Window AC & R_HVAC_AC_WKST | Update of baseline and high efficiency requirements
R_HVAC_Ductless & R_HVAC_AC_WKST | Conversion of the efficiency metrics from SEER and EER to SEER2 and EER2
R_HVAC_Central AC Retrofit & R_HVAC_AC_WKST | Removal of the pre-2006 early replacement baseline option
R_Light_Linear LED | Update of the deemed savings values for direct install linear LED lighting
R_Light_Security Light | Update of the deemed savings values for direct install linear LED lighting

## Introduction
INTRODUCTION
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM.
TECHNICAL REFERENCE MANUAL (TRM)
All energy efficiency programs need to estimate the amount of energy saved (kWh) and demand reduced (kW) for standard measures. This allows an effective program to promote these standard measures across markets with an incentive amount that is appropriate for the energy and/or demand impacts. The TRM Administrator, who works with the EM&V Consultant, maintains estimates of these energy and demand impacts in the TRM.
The TRM is intended to be a flexible and living document. New measures may be added as new program designs are implemented. These measures are often not yet characterized, so new information will be gathered through evaluations or research. Savings for current measures may change as the market evolves.
There are three main reasons to update TRM measures:
| • | New Measure Additions – As Hawai‘i Energy introduces new measures into the portfolio, the measures will be characterized and added to the TRM. In addition, new program design and new areas of interest (e.g., Market Transformation) may result in the need for new measure characterization.
| • | Existing Measure Updates – Updates will be required for a number of reasons. Examples include increase in the federal or state code or standard for efficiency of a measure; new information from field tests; altered qualification criteria; increase in measure priority; changes in program delivery (e.g., direct installation to point-of-sale); move from custom to deemed or vice versa; decrease in measure cost; or a new evaluation that provides a better value of an assumption for a variable. As programs mature, characterizations need to be updated to meet the changes in the market and the program.
| • | Retiring Existing Measures – Existing TRM measures may be removed from the Hawai‘i Energy portfolio when the economics of a measure become such that it is no longer cost-effective or the free-rider rate is too high, or for other reasons. Before retiring an existing TRM measure, there should be agreement among the Commission, EEM, Hawai‘i Energy, and the EM&V Consultant.
Annually, the TRM Administrator will provide a review of the TRM and make recommendations based on current market research, in-field savings verification of measures, and evolving program priorities. After prioritizing recommended updates in collaboration with Hawai‘i Energy, the EEM, the Technical Advisory Group (TAG), and the Commission, the TRM Administrator makes the improvements and then they are implemented in the subsequent program year. In some years, the TRM Administrator makes mid-year updates to reflect new measure additions and other time-sensitive changes; mid-year updates apply to the current program year. Refer to the latest Hawai'i Energy Technical Reference Manual Framework document for more information on the TRM review and update process.
The following subsection describes how the TRM was developed and the key assumptions that were used in estimating the energy (kWh) savings and peak demand (kW) reduction impacts claimed by the Program.
Overview of the TRM Derivation
Each measure in the TRM includes a description of the baseline case and the high-efficiency case for the measure. The energy saved is the difference between the energy use for the baseline case and the energy use for the high-efficiency case. Similarly, the peak demand reduction is the difference between the coincident peak demand for the baseline case and the coincident peak demand for the high-efficiency case. For some measures and program delivery approaches, a dual baseline is needed to account for baseline changes that occur during the life of the measure. Lifetime energy savings reflect the cumulative saving accrued for the life of the measure.
Customer level energy and peak demand estimates are a function of many variables. When practical, assumptions for key variables used in the estimation approaches are based on Hawaii-specific data. Where Hawaii data is not available or it is cost-prohibitive to obtain, data from similar programs in similar climate zones is used with appropriate adjustments based on engineering judgment.
The savings estimates used in the initial Hawai‘i Energy TRM were drawn largely from the KEMA Evaluation Report for 2005 through 2007. At that time, the KEMA report was the most recent information available on specific markets. The values contained within that report were built upon previous evaluation reports and in-field measurements.
Because that report used “average” field measured data instead of generalizable engineering equations to estimate savings for many measures, the approaches provided in the TRM attempted to develop savings calculations based on typical measure characteristics. The primary use of the KEMA report values was to guide development of the first TRM, including market assumptions, especially for the baseline energy use, to more accurately estimate the typical savings.
Over the years, updates have been made to most measures and aspects of the TRM to reflect program modifications, evolving market conditions, changes to codes and standards, and availability of newer data from program evaluations and benchmarking against industry best practices. However, prior to program year 2019 (PY19), the last major TRM review and update was conducted during the 2012 program year. Given this timeframe and general industry practice, the TRM was due for a major review and update. The TRM Administrator, working with the current EM&V Consultant (ICF, formerly doing business as AEG), carried out comprehensive updates for the PY19 through PY26 TRMs, along with developing a TRM Framework to guide ongoing updates.
AEG (now ICF) referred to over 100 resources during the PY19 through PY26 TRM updates. A few of the key information sources include the following:
| • | Uniform Methods Project
| • | U.S. Department of Energy
| • | Environmental Protection Agency
| • | American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE)
| • | International Energy Conservation Code
| • | California Public Utilities Commission, Database for Energy Efficiency Resources (DEER)
| • | Regional Technical Forum, Library of Unit Energy Savings Measures
| • | Multiple Technical Reference Manuals for jurisdictions across the U.S.
| • | Various memorandums prepared by former EM&V Consultant, Opinion Dynamics
Additionally, the primary sources used to update key parameters with Hawaii-specific data are listed below:
| • | Hawai‘i Energy program data and annual verification results.
| • | Commercial and Residential Hourly Load Profiles for all TMY3 Locations in the United States, OpenEI Datasets, Open Data Catalog, Office of Energy Efficiency and Renewable Energy, U.S. Department of Energy. Available at: https://data.openei.org/submissions/153.
| • | National Laboratory of the Rockies (formerly known as National Renewable Energy Laboratory). Building Energy Optimization (BEopt) Software. Version 2.8.0.0. U.S. Department of Energy. January 2018. Available at: https://www.nlr.gov/buildings/beopt. AEG (now ICF) developed a prototype home and ran various simulations using Honolulu weather data.
| • | Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, Prepared by Evergreen Economics, February 26, 2014.
| • | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for the Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
| • | State of Hawaii Market Potential Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.

## Signatures
SIGNATURES
Return to TOC
Applicable Program Year: | PY2026 (July 1, 2026 - June 30, 2027)
Publication Date: | June 30, 2026
Version Number: | PY26.1.0
Approvals:
Hawai‘i Energy
Anthony Zolfo |  | Energy Engineer, Hawaiʻi Energy | 2026-06-09
Name |  | Title, Organization | Date
Independent EM&V Contractor
Kelly Parmenter |  | TRM Lead, ICF | 2026-06-08
Name |  | Title, Organization | Date
Energy Efficiency Manager
Jennifer Barnes |  | Director, West Monroe | 2026-06-25
Name |  | Title, Organization | Date
Hawaii Public Utilities Commission
Ashley Norman |  | Utility Analyst / PBF Contracts Liason, Hawaii PUC | 2026-06-25
Name |  | Title, Organization | Date

## Glossary
GLOSSARY
Return to TOC
UPDATE STATUS
Updated in Spring 2024 for the PY24 TRM.
TERM |  | DEFINITION
Annual Operating Hours (AOH) |  | See “Operating Hours” definition. Also referred to as “Hours of Use.”
Avoided Costs |  | Essentially the marginal cost for a public utility to produce one more unit of power. Because Qualifying Facilities (QFs) reduce the utility's need to produce this additional power themselves, the price utilities pay for QF power has been set to the avoided, or marginal, cost.
Baseline |  | Conditions, such as energy consumption and demand, which would have occurred without implementation of the subject energy efficiency measure. Baseline conditions are sometimes referred to as the counterfactual. There are several baseline options and a range of definitions for these options used in the efficiency industry.
Coefficient of Variation |  | The sample standard deviation divided by the sample mean (Cv = σ/μ).
Coincident Demand |  | The demand of a device, circuit, end-use, building, or population that occurs at the same time as the utility’s system peak load.
Coincidence Factor (CF) |  | The factor used to determine the coincident peak demand reduction. It represents the fraction of the full load demand that corresponds with utility system peak period. Range = 0-1. See also “System Peak Period” and “Coincident Peak Demand Reduction” definitions.
Coincident Peak Demand Reduction |  | The reduction in peak electricity use in units of kW from the baseline to the use associated with the energy-efficient measure installation, where the reduction in peak electricity use occurs simultaneously with the servicing utility system’s maximum use during a specific period. Hawai‘i Energy’s current definition for coincident peak demand savings is the average demand savings that occur, from implementation of an efficiency measure, during the non-holiday, weekday hours between 5 and 9 PM. This aligns with HECO’s System Peak Period. See also “System Peak Period” definition.
Commission |  | The State of Hawaii Public Utilities Commission (HPUC) is a quasi-judicial body responsible for guiding the development of state utility policies that best serve the long-term interest of Hawai‘i utility ratepayers, with the goal of the provision of high quality public utility service in Hawai‘i at reasonable costs.
Common Practice |  | The predominant technology(ies) implemented or practice(s) undertaken in a particular region or sector. Common practices can be used to define a baseline.
Connected Load |  | The maximum wattage of the equipment, under normal operating conditions.
Cost-effectiveness |  | An indicator of the relative performance or economic attractiveness of any energy efficiency investment or practice. The present value of the estimated benefits produced by an energy efficiency program is compared to the estimated total costs to determine if the proposed investment or measure is desirable from a variety of perspectives (e.g., whether the estimated benefits exceed the estimated costs from a societal perspective).
Custom Measures |  | Energy efficiency measures that provide efficiency solutions to unique situations that are not amendable to fully deemed savings values or for which an individualized savings determination approach is preferable. Custom measures rely on site-specific information (e.g., hours of operation, horsepower, existing equipment efficiency) that determines their impacts (e.g., energy savings).
Customer Level Savings (Gross at the Meter) |  | The tracked savings unadjusted for free-ridership or spillover, and not accounting for transmission and distribution losses. These are the savings defined by the TRM.
Deemed Calculation |  | Agreed-to engineering algorithm(s) used to calculate energy and/or demand savings associated with installed efficiency measure(s). Referred to in some TRMs as stipulated algorithm(s), standard protocols, or site-specific protocols. Deemed calculations that use only deemed variables or factors define fully deemed savings values. Deemed calculations are used to determine partially deemed savings values when used with a combination of (1) deemed variables/factors and (2) site- or project-specific variables/factors.
Deemed Savings Method |  | The process used to derive fully deemed savings values.
Deemed Savings Values |  | Predetermined estimates of energy or peak demand savings attributable to individual energy efficiency measures implemented in a particular type of building, application, climate zone, etc. Referred to in some TRMs as unit energy savings or stipulated savings values. These are documented, numerical values for specific energy efficiency measures, often in the form of per-unit savings that define the agreed-upon performance of an individual energy efficiency measure. Deemed savings values may be either:
• |  | Fully deemed savings values—values that are fixed regardless of any site- or project-specific conditions, variables, or factors, or
• |  | Partially deemed (semi-prescriptive) savings values—values determined with algorithms, which have as inputs some combination of (1) deemed variables or factors and (2) site- or project-specific conditions, variables, and factors.
Deemed Variable |  | Values for input assumptions that determine the performance of an energy efficiency measure under different operating conditions, applications, climates, etc. Also referred to as a stipulated variable.
Default Value |  | When a measure indicates that an input to a prescriptive savings algorithm may take on a range of values, an average value is also provided in many cases. This value is considered the default input to the algorithm, and should be used when the other alternatives listed in the measure are not applicable.
Demand Savings |  | See the “Coincident Peak Demand Reduction” definition.
Demand-Side Management |  | Strategies used to manage energy demand, including energy efficiency, load management, fuel substitution, and load building.
Early Retirement; Early Replacement |  | When equipment that is still functioning is replaced early because of a program intervention and energy savings benefits, this is referred to as "early retirement" or "early replacement." The remaining life of the existing equipment is estimated and adjustments are made to the benefits and the costs. An early retirement scenario occurs when existing, functional, actively used equipment is replaced with similar, higher efficiency equipment. The equipment being replaced should have at least one year of remaining useful life (RUL). In this case, a dual baseline will have to be considered, which uses the pre-existing equipment as the baseline for savings during the RUL period, and code requirement/industry standard practice baseline for estimating the balance of the EUL period for the new equipment.
Effective Useful Life (EUL) |  | The median number of years that a measure is in place and operational after installation. This definition implicitly includes equipment life and measure persistence (defined below) but not savings persistence. (Definition is from the Uniform Methods Project.) See also “Savings Persistence” definition.
• |  | "Equipment life” is the number of years installed equipment will operate before it fails.
• |  | "Measure persistence” takes into account business turnover, early retirement or failure of the installed equipment, and any other reason the measure would be removed or discontinued.
Energy Efficiency |  | "Energy efficiency" refers to measures that reduce the amount of energy required to achieve a given task or end use.
Energy Efficiency Manager (EEM) |  | The Energy Efficiency Manager team is an independent contractor team that assists the Commission with the administration of contracts with the Program Administrator and the EM&V Contractor.
Energy Savings |  | Reduction in energy use as compared to a baseline consumption. Electricity savings are generally expressed in units of kWh.
Equivalent Full Load Hours (EFLH) |  | The equivalent hours that equipment would need to operate at its peak capacity in order to consume its estimated annual kWh consumption (annual kWh/connected kW).
Evaluation or Evaluation, Measurement and Verification (EM&V) |  | Evaluation is an applied inquiry process for collecting and synthesizing evidence that culminates in conclusions about the state of affairs, accomplishments, value, merit, worth, significance, or quality of a program, product, person, policy, proposal, or plan. Impact evaluation in the energy efficiency arena is an investigation process to determine energy or demand impacts achieved through the program activities, encompassing, but not limited to: savings verification, measure level research, and program level research. Additionally, evaluation may occur outside of the bounds of this TRM structure to assess the design and implementation of the program.
EM&V Contractor |  | The EM&V Contractor is an entity designated by the Commission to provide independent evaluation, measurement, and verification services for the Public Benefits Fee (PBF) Programs, Energy Efficiency Portfolio Standard (EEPS) and other programs and/or activities as directed by the Commission. The EM&V Contractor reports to the EEM.
Failure and Failure Rate |  | “Failure” is defined as an instance where an implementation contractor reports that a measure has been installed, but a subsequent inspection finds that the equipment is non-operational and/or not properly installed and that difference has not been accounted for elsewhere.
“Failure rate” should be defined as the percent of inspected installation sites where any equipment fails inspection (i.e., the equipment is either not installed or not operating) and that possibility has not been otherwise accounted for.
Note, the definition of failure is intended to not count issues related to persistence or normal measure lives.
Free-ridership |  | Program savings attributable to free-riders (program participants who would have implemented a program measure or practice in the absence of the program). (Definition is from Uniform Methods Project.)
Gross Savings |  | The difference in energy consumption with the energy efficiency measures promoted by the program in place versus what consumption would have been without those measures in place. (Definition is from Uniform Methods Project.)
Hawai‘i Energy |  | Hawai‘i Energy is the brand name for the third-party administered ratepayer-funded conservation and energy efficiency programs for Hawai‘i, Honolulu and Maui counties.
High Efficiency |  | General term for technologies and processes that require less energy, water, or other inputs to operate.
Hours of Use (HOU) |  | See “Operating Hours” definition. Also referred to as “Annual Operating Hours.”
Impact Evaluation |  | An assessment of the program-specific, directly or indirectly induced changes (e.g., changes in energy use and/or demand) associated with an energy efficiency program.
In-Service Rate (ISR) |  | Some measure types require special attention because ISRs, or installation rates, have been found to be relatively low. For example, the ISR represents the percentage of incented residential lighting products that are ultimately installed by program participants. ISRs vary substantially based on the program delivery mechanism, but they are particularly important in giveaway or upstream programs where the customer is responsible for installation. ISRs should be included in TRM calculations for relevant measure types.
Interactive Effects |  | Energy effects from an energy efficiency measure that occur outside the measurement boundary of the individual measure. For example, there are interactive effects between lighting and HVAC equipment, since efficient lighting installed in conditioned spaces decreases air conditioning loads, but increases heating loads.
Interactive Effects Factor (IE, IEF, or IF) |  | The metric used to measure interactive effects. See also "Interactive Effects."
Key Stakeholder Group |  | The Hawai‘i TRM development and update process is guided by a group of key stakeholders—Hawai‘i Energy, the Commission, the EEM, and the EM&V Consultant (“Key Stakeholder Group”). This group oversees and manages the project, comments on work products, and ensures that the TRM meets the needs of the Hawai‘i stakeholders. The Key Stakeholder Group participates in every aspect of the development of the TRM and the TRM Framework. Group members provide data and technical input, review draft savings calculations, and attend teleconferences to review, comment, and participate in the development of the TRM and TRM Framework.
Lifetime |  | The number of years (or hours) that the new high efficiency equipment is expected to function. These are generally based on engineering lives, but sometimes adjusted based on expectations about frequency of removal, remodeling or demolition. Two important distinctions fall under this definition: Effective Useful Life (EUL) and Remaining Useful Life (RUL). See the “Effective Useful Life” and “Remaining Useful Life” definitions.
Lifetime Savings |  | Savings may vary over the lifetime of a measure. Savings estimate should typically apply throughout the period between measure delivery and the end of the measure lifetime. If the RUL of a pre-conditions measure is expected to be greater than 0 years but less than 25 years (0<RUL<25 years), then two baselines must be used in estimating lifetime savings. The first baseline applies between measure-delivery and when the RUL of the pre-condition expires. The second baseline applies between expiration of the RUL and the end of the measure lifetime. For example, an air compressor might be scheduled for replacement in 3 years, but is replaced sooner with a more efficient model. The lifetime of the efficient air compressor might be 20 years; however, the RUL would be 3. The first baseline applies to years 1 through 3. A second baseline is applied in years 4 through 20.
Load Factor (LF) |  | The fraction of full load (wattage) for which the equipment is typically run.
Logic Model |  | A graphical depiction and description of the logical relationships between the inputs, activities, outputs, and outcomes of a program.
Market Effects |  | Changes in the structure of a market or the behavior of participants in a market that is reflective of an increase in the adoption of energy efficient products, services, or practices and is causally related to market intervention(s) (e.g., programs).
Market Penetration |  | A measure of the diffusion of a technology, product, or practice in a defined market, as represented by the percentage of annual sales for a product or practice, the percentage of the existing installed stock for a product or category of products, or the percentage of existing installed stock that uses a practice.
Market Saturation |  | A percentage indicating the proportion of a specified end-user market that contains a particular product. An example would be the percentage of all households in a given geographical area that have a certain appliance.
Market Transformation Programs |  | Hawai‘i Energy’s EE portfolio includes a suite of programs labeled as “Market Transformation.” These programs aim to provide strategic interventions in the market in order to create lasting efficiencies and ultimately pave the way for the integration of clean energy solutions.
Measure |  | A high efficiency technology or procedure that results in energy savings as compared to the baseline efficiency.
Measure Cost |  | The incremental (for time of sale measures) or full cost (both capital and labor for retrofit measures) of implementing the High Efficiency measure.
Measure Description |  | A detailed description of the technology or procedure and the criteria it must meet to be eligible as an energy efficient measure.
Measure Level Research |  | An evaluation process that takes a deeper look into measure level savings achieved through program activities driven by the goal of providing Hawai‘i-specific research to facilitate updating measure-specific TRM input values or algorithms.
Net Savings |  | The difference in energy consumption with the program in place versus what consumption would have been without the program in place. The factors most often considered in net savings calculations are free-ridership, spillover (both participant and nonparticipant), and market effects. (Definition is from Uniform Methods Project.)
Net-to-Gross (NTG) Ratio or NTGR |  | A ratio of the net impacts to the gross impacts of an energy efficiency measure or program.
Operating Hours |  | The hours that equipment is expected to operate in a given period of time (e.g., day, month, year).
Peak Demand |  | The average demand savings that occur from implementation of an energy efficiency measure during the non-holiday, weekday hours between 5 and 9 PM. This aligns with HECO’s System Peak Period: 5-9 PM on the average weekday throughout the year, regardless of the season or month.
Persistence Factor (PF) |  | The metric used to measure Savings Persistence. Range = 0-100%. See also “Savings Persistence” definition.
Persistence Study |  | A study to assess changes in program impacts over time (including retention and degradation).
Portfolio |  | Either (a) a collection of similar programs addressing the same market (e.g., a portfolio of residential programs), technology (e.g., motor-efficiency programs), or mechanisms (e.g., loan programs) or (b) the set of all programs conducted by one organization, such as a utility (and which could include programs that cover multiple markets, technologies, etc.).
Potential Studies |  | Studies conducted to assess market baselines and savings potentials for different technologies and customer markets. Potential is typically defined in terms of technical potential, market potential, and economic potential.
Prescriptive Measures |  | See “Deemed” measure definitions.
Program |  | A group of projects, with similar characteristics and installed in similar applications. Examples could include a utility program to install energy-efficient lighting in commercial buildings, a developer’s program to build a subdivision of homes that have photovoltaic systems, or a state residential energy efficiency code program.
Program Level Savings (Net Generated) |  | The amount of reduction that can be directly attributed to the programs. It is the system level savings adjusted by the net-to-gross ratio to account for free-ridership and spillover.
Program Year (PY) |  | The time period approved for program implementation. The Hawai‘i Energy program year runs from July 1st to the following June 30th.
Regression Analysis |  | Analysis of the relationship between a dependent variable (response variable) to specified independent variables (explanatory variables). The mathematical model of their relationship is the regression equation.
Remaining Useful Life (RUL) |  | Applies to retrofit or replacement measures. For example, if an existing working refrigerator is replaced with a high efficiency unit, the RUL is an assumption of how many more years the existing unit would have lasted. If the RUL cannot be determined from the age of the measure, the RUL is usually assumed to be 1/3 of the EUL.
Replace on Burnout |  | When a piece of equipment has stopped working and is being replaced, this is referred to as "replace on burnout." The benefits are calculated as the cost of the energy saved by using the efficient measure as compared with the energy that would have been used by an off the shelf (less efficient) "stock" version of the measure.
Retrofit Isolation |  | The savings measurement approach defined in IPMVP Options A and B, as well as ASHRAE Guideline 14, that determines energy or demand savings through the use of meters to isolate the energy flows for the system(s) under consideration. IPMVP Option A involves “Key Parameter Measurement” and IPMVP Option B involves “All Parameter Measurement.”
Savings Persistence |  | The percentage of change in expected savings due to changed operating hours, changed process operations, and/or the performance degradation of equipment efficiency relative to the baseline efficiency option. For example, an industrial plant that reduces operation from two shifts to one shift may then have a savings persistence factor of 50%, as only half of the projected energy savings would be realized. Also, improper operation of the equipment may negatively affect savings persistence, so training and commissioning could improve savings persistence. Finally, most equipment efficiency degrades over time, so annual energy savings may increase or decrease relative to the efficiency degradation of the baseline efficiency option. (Definition is from the Uniform Methods Project.)
Spillover |  | Spillover refers to energy savings that are due to the influence of a program but are not counted in program records. Spillover can be broken out in three categories: 1) Participant Internal Spillover; 2) Participant External Spillover; and 3) Non-Participant Spillover.
System Level Savings (Gross Generated) |  | The gross (unadjusted by the net-to-gross ratio) savings realized at the utility system level and including transmission and distribution losses. In Hawai'i Energy reports prior to 2016, this was simply called gross level savings.
System Loss Factor (SLF) |  | Energy savings at the customer level are equivalent to even greater savings at the power plant busbar (where the electrons enter the grid) due to energy losses during transmission and distribution. The system loss factor (SLF) is defined as marginal electricity losses from the busbar to the customer meter – expressed as a percent of meter-level savings. Each island in Hawai‘i has a different SLF due to differences in infrastructure. SLF values are derived using island-level loss data published for HECO, MECO, and HELCO. The customer-level electricity savings are multiplied by (1+SLF) to get the system-level savings, or savings at the power plant busbar.
System Peak Period |  | HECO’s current definition of system peak period is 5-9 PM on the average non-holiday weekday throughout the year, regardless of the season or month.
Technical Advisory Group |  | TRM and TRM Framework development is guided by a spirit of collaboration and shared goals. The Technical Advisory Group (“TAG”) provides input to this process. The TAG is made up of a broader group of stakeholders, including utilities, the consumer advocate, consultants, and other credible resources.
Technical Reference Manual |  | A resource that contains energy efficiency measure information used in program planning, implementation, tracking, and reporting and evaluation of impacts associated with the subject measures.
Total Resource Benefit (TRB) |  | Total Resource Benefit is the present value of avoided utility costs over the life of the efficiency measures installed through the program. The utilities’ total avoided cost of all saved energy and capacity avoided is called the Total Resource Benefit.
Total Resource Cost (TRC) |  | Total Resource Cost is the customer’s project or incremental cost to purchase and install the energy-efficient equipment or make operational changes above what would have been done anyway.
TRB-TRC Ratio |  | The societal cost test of the TRB/TRC provides a metric of how much “return on investment” is provided by: (1) Saving energy versus generating it (kWh reductions) and (2) Avoiding the need for increased power plant capacity (Peak kW reductions).

## C&S Tracking
Codes and Standards Applicable to the Hawai'i Energy TRM
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM.
Technology | Hawai'i Energy Measure(s) | Capacity/Size | C&S Baseline as of PY26 | Next C&S Baseline | Next Effective Date | Source(s)
Linear Fluorescent Lamps | R_Light_Linear LED | 4-ft medium bipin, ≤ 4,500K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
| C_Light_General | 4-ft medium bipin, > 4,500K and ≤ 7,000K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
| C_Lighting_Refrigerated Case | 2-ft U-shaped, ≤ 4,500K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
| C_Light_Stairwell Bi-Level | 2-ft U-shaped, > 4,500K and ≤ 7,000K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
| C_Light_Energy Advantage | 8-ft slimline, ≤ 4,500K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
|  | 8-ft high output, ≤ 4,500K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
|  | 8-ft high output, > 4,500K and ≤ 7,000K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
|  | 4-ft miniature bipin standard output, ≤ 4,500K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
|  | 4-ft miniature bipin standard output, > 4,500K and ≤ 7,000K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
|  | 4-ft miniature bipin high output, ≤ 4,500K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
|  | 4-ft miniature bipin high output, > 4,500K and ≤ 7,000K | N/A: State ban of linear fluorescent lamps (as of Jan. 1, 2026) |  |  | 10 CFR 430.32 (n); Hawaii HB 192, Act 225, 7/5/2023
General Service Lamps | R_Light_LED (Oahu, Maui, Hawaii) | 1490-2600 lm | N/A: State ban of compact fluorescent lamps (as of Jan. 1, 2025 and Jan. 1, 2026)* |  |  | 10 CFR 430.32 (dd); Hawaii HB 192, Act 225, 7/5/2023
| R_Light_Occupancy Sensor | 1050-1489 lm | N/A: State ban of compact fluorescent lamps (as of Jan. 1, 2025 and Jan. 1, 2026)* |  |  | 10 CFR 430.32 (dd); Hawaii HB 192, Act 225, 7/5/2023
| R_Light_Security Light | 750-1049 lm | N/A: State ban of compact fluorescent lamps (as of Jan. 1, 2025 and Jan. 1, 2026)* |  |  | 10 CFR 430.32 (dd); Hawaii HB 192, Act 225, 7/5/2023
| C_Light_General | 310-749 lm | N/A: State ban of compact fluorescent lamps (as of Jan. 1, 2025 and Jan. 1, 2026)* |  |  | 10 CFR 430.32 (dd); Hawaii HB 192, Act 225, 7/5/2023
Solar Light Tube | R_Light_Solar Tube | Solar light tube, 10", 14", and 21" | 100% LED lamps (as of Jan. 1, 2025) |  |  | 10 CFR 430.32 (dd); Hawaii HB 192, Act 225, 7/5/2023
Exit Signs | C_Light_General | Various | ≤ 5 W per face (as of Jan. 1, 2006) |  |  | 10 CFR 431.206
Chiller | C_HVAC_Chiller | Various | See Table 6.8.1-3, ASHRAE 90.1-2022** | ASHRAE 90.1-2025 | TBD | ASHRAE 90.1
Ceiling Fan and Ceiling Fan Light Kit | R_HVAC_Ceiling Fan | Very small-diameter (VSD), D ≤ 12 in | 21 cfm/W (as of Jan. 21, 2020) |  |  | 10 CFR 430.32 (s)
|  | Very small-diameter (VSD), D > 12 in | 3.16 D −17.04 (as of Jan. 21, 2020) |  |  | 10 CFR 430.32 (s)
|  | Standard | 0.65 D + 38.03 (as of Jan. 21, 2020) |  |  | 10 CFR 430.32 (s)
|  | Hugger | 0.29 D + 34.46 (as of Jan. 21, 2020) |  |  | 10 CFR 430.32 (s)
|  | High-speed small-diameter (HSSD) | 4.16 D + 0.02 (as of Jan. 21, 2020) |  |  | 10 CFR 430.32 (s)
|  | Large-diameter | 0.91 D−30.00 (as of Jan. 21, 2020) |  |  | 10 CFR 430.32 (s)
|  | Ceiling fan light kits, < 120 lm (inactive measure) | 50 lm/W (as of Jan. 21, 2020) |  |  | 10 CFR 430.32 (s)
|  | Ceiling fan light kits, ≥ 120 lm (inactive measure) | 74.0−29.42 × 0.9983lumens lm/W (as of Jan. 21, 2020) |  |  | 10 CFR 430.32 (s)
Central AC Split and Single Package | R_HVAC_Central AC Retrofit | Single-phase split-system AC, <45,000 Btu/h | 14.3 SEER2 (as of Jan. 1, 2023) |  |  | 10 CFR 430.32 (c)
Air-cooled | R_HVAC_Ductless | Single-phase split-system AC, ≥ 45,000 and < 65,000 Btu/h | 13.8 SEER2 (as of Jan. 1, 2023) |  |  | 10 CFR 430.32 (c)
| C_HVAC_AC & Heat Pump | Single-phase single-package AC, < 65,000 Btu/h | 13.4 SEER2 (as of Jan. 1, 2023) |  |  | 10 CFR 430.32 (c)
| C_HVAC_VRF | Three-phase split-system AC, <65,000 Btu/h | 13.4 SEER2 (as of Jan. 1, 2025) |  |  | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Three-phase single-package AC, < 65,000 Btu/h | 13.4 SEER2 (as of Jan. 1, 2025) |  |  | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Commercial packaged AC, ≥ 65,000 and < 135,000 Btu/h | 14.8 IEER (as of Jan. 1, 2023) | 14.3 IVEC | Jan. 1, 2029 | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Commercial packaged AC, ≥ 135,000 and < 240,000 Btu/h | 14.2 IEER (as of Jan. 1, 2023) | 13.8 IVEC | Jan. 1, 2029 | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Commercial packaged AC, ≥ 240,000 Btu/h and < 760,000 Btu/h | 13.2 IEER (as of Jan. 1, 2023) | 12.9 IVEC | Jan. 1, 2029 | 10 CFR 431.97 (b); ASHRAE 90.1
Air-Source Heat Pump | C_HVAC_AC & Heat Pump | Single-phase split-system HP, < 65,000 Btu/h | 14.3 SEER2 (as of Jan. 1, 2023) |  |  | 10 CFR 430.32 (c)
| C_HVAC_VRF | Single-phase single-package HP, < 65,000 Btu/h | 13.4 SEER2 (as of Jan. 1, 2023) |  |  | 10 CFR 430.32 (c)
|  | Three-phase split-system HP, <65,000 Btu/h | 14.3 SEER2 (as of Jan. 1, 2025) |  |  | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Three-phase single-package HP, < 65,000 Btu/h | 13.4 SEER2 (as of Jan. 1, 2025) |  |  | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Commercial packaged HP, ≥ 65,000 and < 135,000 Btu/h | 14.1 IEER (as of Jan. 1, 2023) | 13.4 IVEC; 6.2 IVHE | Jan. 1, 2029 | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Commercial packaged HP, ≥ 135,000 and < 240,000 Btu/h | 13.5 IEER (as of Jan. 1, 2023) | 13.1 IVEC; 6.0 IVHE | Jan. 1, 2029 | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Commercial packaged HP, ≥ 240,000 and < 760,000 Btu/h | 12.5 IEER (as of Jan. 1, 2023) | 12.1 IVEC; 5.8 IVHE | Jan. 1, 2029 | 10 CFR 431.97 (b); ASHRAE 90.1
Water-Source Heat Pump | C_HVAC_AC & Heat Pump | Commercial packaged HP, < 17,000 Btu/h | 12.2 EER (as of Oct. 9, 2015) |  |  | 10 CFR 431.97 (b); ASHRAE 90.1
| C_HVAC_VRF | Commercial packaged HP, ≥ 17,000 and < 65,000 Btu/h | 13.0 EER (as of Oct. 9, 2015) |  |  | 10 CFR 431.97 (b); ASHRAE 90.1
|  | Commercial packaged HP, ≥ 65,000 and < 135,000 Btu/h | 13.0 EER (as of Oct. 9, 2015) |  |  | 10 CFR 431.97 (b); ASHRAE 90.1
PTAC | C_HVAC_AC & Heat Pump | Standard, < 7,000 Btu/h | 11.9 EER (as of Jan. 1, 2017) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Standard, ≥ 7,000 and ≤ 15,000 Btu/h | EER = 14.0 − 0.3 * Cap / 1000 (as of Jan. 1, 2017) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Standard, > 15,000 Btu/h | 9.5 EER (as of Jan. 1, 2017) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Non-Standard, < 7,000 Btu/h | 9.4 EER (as of Oct. 7, 2010) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Non-Standard, ≥ 7,000 and ≤ 15,000 Btu/h | EER = 10.9 − 0.213 * Cap / 1000 (as of Oct. 7, 2010) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Non-Standard, > 15,000 Btu/h | 7.7 EER (as of Oct. 7, 2010) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
PTHP | C_HVAC_AC & Heat Pump | Standard, < 7,000 Btu/h | 11.9 EER (as of Oct. 8, 2012) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Standard, ≥ 7,000 and ≤ 15,000 Btu/h | EER = 14.0 − 0.3 * Cap / 1000 (as of Oct. 8, 2012) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Standard, > 15,000 Btu/h | 9.5 EER (as of Oct. 8, 2012) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Non-Standard, < 7,000 Btu/h | 9.3 EER (as of Oct. 7, 2010) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Non-Standard, ≥ 7,000 and ≤ 15,000 Btu/h | EER = 10.8 − 0.213 * Cap / 1000 (as of Oct. 7, 2010) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
|  | Non-Standard, > 15,000 Btu/h | 7.6 EER (as of Oct. 7, 2010) |  |  | 10 CFR 431.97 (c); ASHRAE 90.1
Vertical AC and Heat Pump | C_HVAC_AC & Heat Pump | Single-package, < 65,000 Btu/h | 11.0 EER (as of Sep. 23, 2019) |  |  | 10 CFR 431.97 (d); ASHRAE 90.1
|  | Single-package, ≥ 65,000 and < 135,000 Btu/h | 10.0 EER (as of Oct. 9, 2015) |  |  | 10 CFR 431.97 (d); ASHRAE 90.1
|  | Single-package, ≥ 135,000 and < 240,000 Btu/h | 10.0 EER (as of Oct. 9, 2016) |  |  | 10 CFR 431.97 (d); ASHRAE 90.1
Direct Expansion-Dedicated Outdoor Air System | C_HVAC_DX-DOAS | Air-cooled (AC), without ventilation energy recovery system (VERS) | 3.8 ISMRE2 (as of May 1, 2024) |  |  | 10 CFR 431.97(h); ANSI/AHRI Standard 920
|  | Air-cooled (AC), with VERS | 5.0 ISMRE2 (as of May 1, 2024) |  |  | 10 CFR 431.97(h); ANSI/AHRI Standard 920
|  | Air-source heat pump (ASHP), without VERS | 3.8 ISMRE2 (as of May 1, 2024) |  |  | 10 CFR 431.97(h); ANSI/AHRI Standard 920
|  | Air-source heat pump (ASHP), with VERS | 5.0 ISMRE2 (as of May 1, 2024) |  |  | 10 CFR 431.97(h); ANSI/AHRI Standard 920
|  | Water-cooled (WC), without VERS | 4.7 ISMRE2 (as of May 1, 2024) |  |  | 10 CFR 431.97(h); ANSI/AHRI Standard 920
|  | Water-cooled (WC), with VERS | 5.1 ISMRE2 (as of May 1, 2024) |  |  | 10 CFR 431.97(h); ANSI/AHRI Standard 920
|  | Water-source heat pump (WSHP), without VERS | 3.8 ISMRE2 (as of May 1, 2024) |  |  | 10 CFR 431.97(h); ANSI/AHRI Standard 920
|  | Water-source heat pump (WSHP), with VERS | 4.6 ISMRE2 (as of May 1, 2024) |  |  | 10 CFR 431.97(h); ANSI/AHRI Standard 920
Room AC | R_HVAC_Window AC | Room AC, w/o reverse cycle, with louvered sides, <6,000 Btu/h | 13.1 CEER (as of May 2026) |  |  | 10 CFR 430.32 (b)
|  | Room AC, w/o reverse cycle, with louvered sides, 6,000-7,900 Btu/h | 13.7 CEER (as of May 2026) |  |  | 10 CFR 430.32 (b)
| C_HVAC_Window AC | Room AC, w/o reverse cycle, with louvered sides, 8,000-13,900 Btu/h | 16.0 CEER (as of May 2026) |  |  | 10 CFR 430.32 (b)
| R_HVAC_Ductless | Room AC, w/o reverse cycle, with louvered sides, 14,000-19,900 Btu/h | 16.0 CEER (as of May 2026) |  |  | 10 CFR 430.32 (b)
|  | Room AC, w/o reverse cycle, with louvered sides, 20,000-27,900 Btu/h | 13.8 CEER (as of May 2026) |  |  | 10 CFR 430.32 (b)
Dehumidifier | R_HVAC_Dehumidifier | Portable, ≤ 25 pints/day | IEF = 1.30 (as of Jun. 13, 2019) |  |  | 10 CFR 430.32 (v)
|  | Portable, 25.01 - 50.00 pints/day | IEF = 1.60 (as of Jun. 13, 2019) |  |  | 10 CFR 430.32 (v)
|  | Portable, > 50 pints/day | IEF = 2.80 (as of Jun. 13, 2019) |  |  | 10 CFR 430.32 (v)
|  | Whole-home, ≤ 8.0 cu ft case volume | IEF = 1.77 (as of Jun. 13, 2019) |  |  | 10 CFR 430.32 (v)
|  | Whole-home, > 8.0 cu ft case volume | IEF = 2.41 (as of Jun. 13, 2019) |  |  | 10 CFR 430.32 (v)
Residential Electric Storage Water Heater | R_WH_Heat Pump | ≥ 20 and ≤ 55 gal, Very Small Draw | UEF = 0.8808 − (0.0008 * Vr) (as of Apr. 16, 2015) | UEF = 2.30 | May 6, 2029 | 10 CFR 430.32 (d)
| R_WH_SWH | ≥ 20 and ≤ 55 gal, Low | UEF = 0.9254 − (0.0003 * Vr) (as of Apr. 16, 2015) | UEF = 2.30 | May 6, 2029 | 10 CFR 430.32 (d)
|  | ≥ 20 and ≤ 55 gal, Medium | UEF = 0.9307 − (0.0002 * Vr) (as of Apr. 16, 2015) | UEF = 2.30 | May 6, 2029 | 10 CFR 430.32 (d)
|  | ≥ 20 and ≤ 55 gal, High | UEF = 0.9349 − (0.0001 * Vr) (as of Apr. 16, 2015) | UEF = 2.30 | May 6, 2029 | 10 CFR 430.32 (d)
|  | > 55 and ≤ 120 gal, Very Small Draw | UEF = 1.9236 − (0.0011 * Vr) (as of Apr. 16, 2015) | UEF = 2.50 | May 6, 2029 | 10 CFR 430.32 (d)
|  | > 55 and ≤ 120 gal, Low | UEF = 2.0440 − (0.0011 * Vr) (as of Apr. 16, 2015) | UEF = 2.50 | May 6, 2029 | 10 CFR 430.32 (d)
|  | > 55 and ≤ 120 gal, Medium | UEF = 2.1171 − (0.0011 * Vr) (as of Apr. 16, 2015) | UEF = 2.50 | May 6, 2029 | 10 CFR 430.32 (d)
|  | > 55 and ≤ 120 gal, High | UEF = 2.2418 − (0.0011 * Vr) (as of Apr. 16, 2015) | UEF = 2.50 | May 6, 2029 | 10 CFR 430.32 (d)
Commercial Electric Water Heater | C_WH_Solar | Residential-duty ≤ 12 kW, Resistance, Storage | Same as residential | Same as residential | May 6, 2029 | 10 CFR 430.32 (d)
| C_WH_Heat Pump | Residential-duty ≤ 24 amps and ≤ 250 volts, Heat Pump, Storage | Same as residential | Same as residential | May 6, 2029 | 10 CFR 430.32 (d)
|  | Commercial-duty, Electric Storage, All Sizes | Max standby loss = 0.30 + 27/Vm (%/hr) (as of Oct. 29, 2003) | (No Change) | Oct. 6, 2026 | 10 CFR 431.110
Faucet Aerator | R_WH_Faucet Aerator | Lavatory faucets and replacement aerators | 1.2 gpm (as of Jan. 1, 2021) |  |  | 10 CFR 430.32 (o); Hawaii HB 556, Act 141 6/26/2019
|  | Kitchen faucets and replacement aerators | 1.8 gpm (as of Jan. 1, 2021) |  |  | 10 CFR 430.32 (o); Hawaii HB 556, Act 141 6/26/2019
Low-Flow Showerhead | R_WH_LFShowerhead | Showerheads, flowing pressure of 80 psi | 1.8 gpm (as of Jan. 1, 2021) |  |  | 10 CFR 430.32 (o); Hawaii HB 556, Act 141 6/26/2019
Dishwasher | R_Appliance_Dishwasher | Compact Dishwasher | EF = 0.62 (max of 222 kWh/yr) (as of May 30, 2013) | Max of 174 kWh/yr, 3.1 gal/cycle | Apr. 23, 2027 | 10 CFR 430.32 (f)
|  | Standard Dishwasher | EF = 0.46 (max of 307 kWh/yr) (as of May 30, 2013) | Max of 223 kWh/yr, 3.3 gal/cycle | Apr. 23, 2027 | 10 CFR 430.32 (f)
Clothes Washer | R_Appliance_Clothes Washer | Automatic, Top-loading, Compact, < 1.6 ft3 capacity | IMEF = 1.15 (as of Jan. 1, 2018) | EER = 3.79 lb/kWh/cycle; WER = 0.29 lb/gal/cycle | Mar. 1, 2028 | 10 CFR 430.32 (g)
|  | Automatic, Top-loading, Standard, ≥ 1.6 ft3 capacity | IMEF = 1.57 (as of Jan. 1, 2018) | EER = 4.27 lb/kWh/cycle; WER = 0.57 lb/gal/cycle | Mar. 1, 2028 | 10 CFR 430.32 (g)
|  | Automatic, Front-loading, Compact, < 1.6 ft3 capacity | IMEF = 1.13 (as of Jan. 1, 2018) |  |  | 10 CFR 430.32 (g)
|  | Automatic, Front-loading, Standard, ≥ 1.6 ft3 capacity | IMEF = 1.84 (as of Jan. 1, 2018) |  |  | 10 CFR 430.32 (g)
|  | Automatic, Front-loading, Compact, < 3.0 ft3 capacity |  | EER = 5.02 lb/kWh/cycle; WER = 0.71 lb/gal/cycle | Mar. 1, 2028 | 10 CFR 430.32 (g)
|  | Automatic, Front-loading, Standard, ≥ 3.0 ft3 capacity |  | EER = 5.52 lb/kWh/cycle; WER = 0.77 lb/gal/cycle | Mar. 1, 2028 | 10 CFR 430.32 (g)
Clothes Dryer | R_Appliance_Clothes Dryer | Vented Electric, Standard, ≥ 4.4 ft3 capacity | CEF = 3.73 (as of Jan. 1, 2015) |  |  | 10 CFR 430.32 (h)
| R_Appliance_Heat Pump Dryer | Electric, Standard, ≥ 4.4 ft3 capacity |  | CEFD2 = 3.93 | Mar. 1, 2028 | 10 CFR 430.32 (h)
|  | Vented Electric, Compact (120V), < 4.4 ft3 capacity | CEF = 3.61 (as of Jan. 1, 2015) |  |  | 10 CFR 430.32 (h)
|  | Electric, Compact (120V), < 4.4 ft3 capacity |  | CEFD2 = 4.33 | Mar. 1, 2028 | 10 CFR 430.32 (h)
|  | Vented Electric, Compact (240V), < 4.4 ft3 capacity | CEF = 3.27 (as of Jan. 1, 2015) | CEFD2 = 3.57 | Mar. 1, 2028 | 10 CFR 430.32 (h)
|  | Vented Gas, Standard, ≥ 4.4 ft3 capacity | CEF = 3.3 (as of Jan. 1, 2015) | CEFD2 = 3.48 | Mar. 1, 2028 | 10 CFR 430.32 (h)
|  | Vented Gas, Compact, < 4.4 ft3 capacity |  | CEFD2 = 2.02 | Mar. 1, 2028 | 10 CFR 430.32 (h)
|  | Ventless Electric, Compact (240V), < 4.4 ft3 capacity | CEF = 2.55 (as of Jan. 1, 2015) | CEFD2 = 2.68 | Mar. 1, 2028 | 10 CFR 430.32 (h)
|  | Ventless Electric, Combination Washer-Dryer | CEF = 2.08 (as of Jan. 1, 2015) | CEFD2 = 2.33 | Mar. 1, 2028 | 10 CFR 430.32 (h)
Refrigerator/Freezer | R_Appliance_Refrigerator | Refrigerators and refrigerator-freezers, ≤ 39 cu ft | Varies (see Standard effective Sep. 15, 2014) | See standards effective Jan. 31, 2029/2030 | Jan. 31, 2029/2030 | 10 CFR 430.32 (a)
| C_Appliance_Refrigerator | Freezers, ≤ 30 cu ft | Varies (see Standard effective Sep. 15, 2014) | See standards effective Jan. 31, 2029/2030 | Jan. 31, 2029/2030 | 10 CFR 430.32 (a)
Air Purifier (Air Cleaner) | R_Appliance_Air Purifier | 10 ≤ PM2.5 CADR < 100 | IEF (PM2.5 CADR/W) = 1.9 (as of Dec. 31, 2025) |  |  | 10 CFR 430.32 (ee)
|  | 100 ≤ PM2.5 CADR < 150 | IEF (PM2.5 CADR/W) = 2.4 (as of Dec. 31, 2025) |  |  | 10 CFR 430.32 (ee)
|  | PM2.5 CADR ≥ 150 | IEF (PM2.5 CADR/W) = 2.9 (as of Dec. 31, 2025) |  |  | 10 CFR 430.32 (ee)
Electric Cooktop | R_Appliance_Induction Cooktop | Smooth Element, Stand-alone or in Combined Cooking Products | N/A | Max. IAEC = 207 kWh/yr | Jan. 31, 2028 | 10 CFR 430.32 (j)
R_Appliance_Non-Induction Cooktop
Commercial Refrigeration/Freezers | C_Kitchen_Refrigerator | Various | See standards effective Mar. 27, 2017 |  |  | 10 CFR 431.66
C_Kitchen_Freezer
Commercial Ice Maker | C_Kitchen_Ice Machine | Various | See standards effective Jan. 28, 2018 |  |  | 10 CFR 431.136
Commercial Pre-Rinse Spray Valve | C_Kitchen_LF Spray Nozzle | Product Class 1 (≤5.0 ozf) | 1.00 gpm (as of Jan. 28, 2019) |  |  | 10 CFR 431.266
|  | Product Class 2 (>5.0 ozf and ≤8.0 ozf) | 1.20 gpm (as of Jan. 28, 2019) |  |  | 10 CFR 431.266
|  | Product Class 3 (>8.0 ozf) | 1.28 gpm (as of Jan. 28, 2019) |  |  | 10 CFR 431.266
Vending Machine | C_PlugProcess_Vending Miser | Class A | Max kWh/day = 0.052 × V + 2.43 (as of Jan. 8, 2019) |  |  | 10 CFR 431.296
|  | Class B | Max kWh/day = 0.052 × V + 2.20 (as of Jan. 8, 2019) |  |  | 10 CFR 431.296
|  | Combination A | Max kWh/day = 0.086 × V + 2.66 (as of Jan. 8, 2019) |  |  | 10 CFR 431.296
|  | Combination B | Max kWh/day = 0.111 × V + 2.04 (as of Jan. 8, 2019) |  |  | 10 CFR 431.296
Motors | C_PumpMotor_ECM | Various | See standards effective Jun. 1, 2016 | See standards effective Jun. 1, 2027 | Jun. 1, 2027 | 10 CFR 431.25
C_PumpMotor_PE Motor
Dedicated-Purpose Pool Pump | R_PumpMotor_VFD Pool Pump | Self-priming pool filter pumps, 0.711 hp ≤ hhp < 2.5 hp, single phase | WEF = −2.30 * ln (hhp) + 6.59 (as of Jul. 19, 2021) |  |  | 10 CFR 431.465 (f)
|  | Self-priming pool filter pumps, hhp ≤ 0.13 hp, single phase | WEF = 5.55 (as of Jul. 19, 2021) |  |  | 10 CFR 431.465 (f)
| C_PumpMotor_VFD Pool Pump | Self-priming pool filter pumps, 0.13 hp < hhp < 0.711 hp, single phase | WEF = −1.30 * ln (hhp) + 2.90 (as of Jul. 19, 2021) |  |  | 10 CFR 431.465 (f)
|  | Non-self-priming pool filter pumps, hhp ≤ 0.13 hp | WEF = 4.60 (as of Jul. 19, 2021) |  |  | 10 CFR 431.465 (f)
|  | Non-self-priming pool filter pumps, 0.13 hp < hhp < 2.5 hp | WEF = −0.85 * ln (hhp) + 2.87 (as of Jul. 19, 2021) |  |  | 10 CFR 431.465 (f)
|  | Pressure cleaner booster pumps | WEF = 0.42 (as of Jul. 19, 2021) |  |  | 10 CFR 431.465 (f)
|  | Dedicated-purpose pool pump motor, total horsepower (THP) < 0.5 | Full-load efficiency ≥ 69% (as of Sep. 29, 2025) |  |  | 10 CFR 431.485 (b)
|  | Small-size dedicated-purpose pool pump motor, 0.5 ≤ THP < 1.15 |  | Must be a variable speed control motor | Sep. 28, 2027 | 10 CFR 431.485 (c)
|  | Standard-size dedicated-purpose pool pump motor, 1.15 ≤ THP < 5 | Must be a variable speed control motor (as of Sep. 29, 2025) |  |  | 10 CFR 431.485 (c)
Pumps | C_HVAC_VFD Water Pump | Various | See standards effective Jan. 27, 2020 |  |  | 10 CFR 431.465 (b)
C_PumpMotor_VFD Booster Pump
Distribution Transformer | Custom | Various | See standards effective Jan. 1, 2016 | See standards effective Apr. 23, 2029 | Apr. 23, 2029 | 10 CFR 431.196
New Construction / Major Renovation | Custom | Various | 2018 IECC w/ Hawaii State and County Amendments (all Counties as of 2024) | 2021 IECC w/ Hawaii State and County Amendments | TBD | IECC; Energy Conservation Code of Hawaii
| R_BEnvelope_Cool Wall | Various | Section R407, Hawaii Energy Code 2018 (all Counties as of 2024) |  |  | IECC; Energy Conservation Code of Hawaii
Computer | Not a Hawai'i Energy Measure | Various | Shall meet the requirements set forth in California Code of Regulations, Title 20, Section 1605.3, as amended (as of Jan. 1, 2021). |  |  | Hawaii HB 556, Act 141 6/26/2019. See also Hawaii SB 691, Act 224, 7/5/2023.
Computer Monitor | Not a Hawai'i Energy Measure | Various | Shall meet the requirements set forth in California Code of Regulations, Title 20, Section 1605.3, as amended (as of Jan. 1, 2021). |  |  | Hawaii HB 556, Act 141 6/26/2019. See also Hawaii SB 691, Act 224, 7/5/2023.
High Color Rendering Index Fluorescent Lamps | Not a Hawai'i Energy Measure | Various | Shall meet the minimum efficacy requirements contained in Section 430.32(n)(4) of Title 10 of the Code of Federal Regulations as in effect on January 3, 2017, as measured in accordance with Appendix R to Subpart B of Part 430 of Title 10 of the Code of Federal Regulations - "Uniform Test Method for Measuring Average Lamp Efficacy (LE), Color Rendering Index (CRI), and Correlated Color Temperature (CCT) of Electric Lamps" - as amended (as of Jan. 1, 2021). |  |  | Hawaii HB 556, Act 141 6/26/2019. See also Hawaii SB 691, Act 224, 7/5/2023.
Spray Sprinkler Bodies | Not a Hawai'i Energy Measure | Various | Those that are not specifically excluded from the scope of the Environmental Protection Agency's WaterSense Specification for Spray Sprinkler Bodies, Version 1.0, shall include an integral pressure regulator and shall meet the water efficiency and performance criteria and other requirements of that specification, as amended (as of Jan. 1, 2021). |  |  | Hawaii HB 556, Act 141 6/26/2019. See also Hawaii SB 691, Act 224, 7/5/2023.
Portable Electric Spa | Not a Hawai'i Energy Measure | Various | Hawaii Adoption of ANSI/ASAP/ICC 14-2019 (as of Jan. 1, 2025) |  |  | Hawaii SB 691, Act 224, 7/5/2023
Electric Vehicle Supply Equipment | Not a Hawai'i Energy Measure | Various | N/A
Residential Ventilating Fan | Not a Hawai'i Energy Measure | Various | Hawaii Adoption of ENERGY STAR V3.2 (as of Jan. 1, 2025) |  |  | Hawaii SB 691, Act 224, 7/5/2023
Portable Air Conditioner | Not a Hawai'i Energy Measure | Single-duct and dual-duct portable air conditioners | CEER = 1.04 * SACC / (3.7117 * SACC0.6384), (as of Jan. 10, 2025) |  |  | 10 CFR 430.32 (cc)
Residential Stretch Codes (Could apply to retrofits in existing buildings as well as new construction) | Related to R_WH_Heat Pump | Demand responsive water heating | See 10 CFR 430.32 (d) | R403 Requires grid-integrated controls on residential style electric storage water heaters (37-120 gallons). | TBD | Draft Amendments for the Development of the 2024 IECC, https://www.codesforclimate.org/wp-content/uploads/2021/09/Electrification-Options-for-City-Review.pdf
| Related to R_HVAC_Smart Thermostat and other R_HVAC Measures | Demand responsive thermostats | See 10 CFR 430.32 (c) | R403 Requires grid-integrated controls on space heating and cooling systems that adjust temperature within 4-degrees. | TBD
| Not a Hawai'i Energy Measure | Solar readiness | N/A | R404 Requires single- and two-family solar readiness. Requires multifamily to comply with a sister provision under commercial section of energy code. | TBD
| Not a Hawai'i Energy Measure | Electric vehicles | N/A | R404 Requires single- and two-family EV charging. Requires multifamily to comply with a sister provision under commercial section of energy code. | TBD
| Not a Hawai'i Energy Measure | Energy storage readiness | N/A | R404 Requires single- and two-family energy storage readiness. | TBD
Commercial Stretch Codes (Could apply to retrofits in existing buildings as well as new construction) | Related to C_HVAC Measures | Demand responsive thermostats | See ASHRAE 90.1, 10 CFR 431.97 (b) and 10 CFR 430.32 (c) | C403 Requires grid-integrated controls on space heating and cooling systems that adjust temperature within 4-degrees | TBD | Draft Amendments for the Development of the 2024 IECC, https://www.codesforclimate.org/wp-content/uploads/2021/09/Electrification-Options-for-City-Review.pdf
| Related to C_WH_Heat Pump | Demand responsive water heating | See 10 CFR 431.110 and 10 CFR 430.32 (d) | C404 Requires grid-integrated controls on residential style electric storage water heaters (37-120 gallons). | TBD
| Not a Hawai'i Energy Measure | Electric vehicles | N/A | C405 Requires EV charging for all commercial building types. | TBD
| Not a Hawai'i Energy Measure | Energy storage readiness | N/A | C405 Requires commercial and multifamily energy storage readiness. | TBD
| Not a Hawai'i Energy Measure | Solar and storage inverters | N/A | C405 Requires solar and energy storage systems be equipped with smart inverters for grid-integrated controls. | TBD
* The Jan. 1, 2025 date applies to screw and bayonet base compact fluorescent lamps. The Jan. 1, 2026 date applies to pin-base compact fluorescent lamps.
** The ASHRAE 90.1-2022 chiller standards are the same as in ASHRAE 90.1-2016 and ASHRAE 90.1-2019.) The standards are also consistent with chiller standards in 2018 IECC and 2021 IECC.

## Key Metrics
KEY METRICS
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. The main change is a new section on how to calculate the total resource benefit for early replacement of fluorescent lighting. In addition, the net-to-gross ratio for the upstream residential LED measure was removed since that measure has been retired. The section with avoided cost tables was also slightly updated to highlight the PY26 table and "gray out" the PY25 and PY27 tables.
DEVELOPMENT OF AVOIDED COSTS
Economic benefits to the State of Hawaii from efficiency include the avoided costs associated with the energy that is saved. The value of the energy that is saved is called the Total Resource Benefit (TRB). To estimate the TRB for individual measures, programs or the whole portfolio, future avoided energy costs ($/kWh) and avoided capacity costs ($/kW) need to be estimated.
Proxy Avoided Costs
There are several ways to determine avoided energy and capacity values, with perhaps the best way being an integrated resource planning approach with a capacity expansion model simulating distributed electricity resources competing against conventional generation options. Another approach is to utilize detailed information gathered from historic or projected power purchase agreements. For the results presented here, a less rigorous approach was used in order to determine interim numbers that would only be used for and applicable to Hawai‘i Energy TRB calculations; and then only until HECO’s Integrated Grid Planning (IGP) process is able to provide values that could replace these estimates. Refer to the following memorandum and analysis spreadsheets for details on development of the avoided energy and capacity costs.
• | Recommendations for Avoided Costs for the Sole Purpose of Providing Interim Updates for Calculation of Hawai‘i Energy Program Total Resource Benefits, Memorandum, Prepared for Hawaii Public Utilities Commission, Hawaiian Electric Companies, and Hawai‘i Energy, Prepared by Steve Schiller, Energy Efficiency Manager and Kelly Parmenter, Applied Energy Group, April 25, 2019.
• | PY19-PY21 Avoided Capacity and Energy Cost Calculations, Analysis Spreadsheet, Prepared by Steve Schiller, Energy Efficiency Manager and Kelly Parmenter, Applied Energy Group, April 28, 2019.
• | PY22-PY24 Avoided Capacity and Energy Cost Calculations, Version 2.1, Analysis Spreadsheet, Prepared by Kelly Parmenter, Applied Energy Group, March 10, 2022.
• | PY25-PY27 Avoided Capacity and Energy Cost Calculations, Version 3.0, Analysis Spreadsheet, Prepared by Kelly Parmenter, Applied Energy Group, August 23, 2024.
Table 1 lists the annualized avoided capacity costs by county for PY25, PY26, and PY27. According to page A-6 of the Maui Electric Company (MECO) 2024 Electric Utility System Cost Data Filing that was submitted to the HPUC on June 28, 2024, no firm capacity generation facilities were projected to be added in the 2024-2034 planning horizon for the County of Maui. Therefore, the EEM and ICF teams have assumed the avoided capacity costs for the County of Maui are zero ($0/kW-yr) for the purposes of the PY25-PY27 analysis.
Table 1. Annualized Avoided Capacity Costs
| County |  |  |  | PY |  | Value 1 |  |  | Unit
| Honolulu (Oahu) |  |  |  | PY25 |  | 299 |  |  | $/kW-yr 2025$
[5 empty] | PY26 |  | 306 |  |  | $/kW-yr 2026$
[5 empty] | PY27 |  | 313 |  |  | $/kW-yr 2027$
| Maui |  |  |  | PY25 |  | 0 |  |  | $/kW-yr 2025$
[5 empty] | PY26 |  | 0 |  |  | $/kW-yr 2026$
[5 empty] | PY27 |  | 0 |  |  | $/kW-yr 2027$
| Hawaii |  |  |  | PY25 |  | 139 |  |  | $/kW-yr 2025$
[5 empty] | PY26 |  | 142 |  |  | $/kW-yr 2026$
[5 empty] | PY27 |  | 145 |  |  | $/kW-yr 2027$
| 1Escalation Factor = | [5 empty] | 2.298% |  |  | /yr, from HECO and HELCO 2024 Electric Utility System Cost Data Filings.
Table 1 sources: Annualized values were derived from capacity costs in the following three sources using the methodology described in the PY25-PY27 Avoided Capacity and Energy Cost Calculations, Version 3.0, Analysis Spreadsheet, Prepared by Kelly Parmenter, Applied Energy Group, August 23, 2024.
1. HECO 2024 Electric Utility System Cost Data Filing, submitted to HPUC, June 28, 2024.
2. MECO 2024 Electric Utility System Cost Data Filing, submitted to HPUC, June 28, 2024.
3. HELCO 2024 Electric Utility System Cost Data Filing, submitted to HPUC, June 28, 2024.
Table 2 lists the avoided energy costs by county for PY25, PY26, and PY27. The costs represent mostly fuel costs and a small share of variable O&M costs.
Table 2. Average Annual Avoided Energy Costs
| County |  |  |  | PY |  | Value 1 |  |  | Unit
| Honolulu (Oahu) |  |  |  | PY25 |  | 0.209 |  |  | $/kWh-yr 2025$
[5 empty] | PY26 |  | 0.215 |  |  | $/kWh-yr 2026$
[5 empty] | PY27 |  | 0.221 |  |  | $/kWh-yr 2027$
| Maui |  |  |  | PY25 |  | 0.21 |  |  | $/kWh-yr 2025$
[5 empty] | PY26 |  | 0.216 |  |  | $/kWh-yr 2026$
[5 empty] | PY27 |  | 0.222 |  |  | $/kWh-yr 2027$
| Hawaii |  |  |  | PY25 |  | 0.212 |  |  | $/kWh-yr 2025$
[5 empty] | PY26 |  | 0.218 |  |  | $/kWh-yr 2026$
[5 empty] | PY27 |  | 0.225 |  |  | $/kWh-yr 2027$
| 1Escalation Factor | [5 empty] | 3% |  | /yr
Table 2 sources: Average annual avoided energy cost values were derived from Schedule Q monthly values for Oahu, Maui Division, and Hawaii using July 1, 2023 through June 1, 2024 values. (See https://www.hawaiianelectric.com/documents/billing_and_payment/rates/avoided_energy_cost/avoid_energy_cost_table.pdf). A 3% escalation factor has been used for the avoided energy costs since PY15. The HPUC may decide to change the value in the future. By comparison, the Energy Information Administration (EIA) projects that the Brent crude oil price will increase to $194 per barrel by 2050. This equates to a 2.3% per year escalation relative to 2022 costs. Since oil costs have a large influence on Schedule Q rates (particularly in the short-term), the projected escalation rate of oil costs is a reasonable proxy for the projected escalation of avoided energy costs. Therefore, the 3% escalation factor is within reason.
TOTAL RESOURCE BENEFIT (TRB)
The Total Resource Benefit (TRB) is the estimated total net present value (NPV) of the avoided cost for the utility from the reduced lifetime demand (kW) and energy (kWh) from energy efficiency projects and measures. The avoided cost values should be multiplied by net customer-level savings instead of net system-level savings for estimating the TRB. This is because the avoided costs already account for transmission and distribution (T&D) losses. Per an email from Lisa Giang, HECO, to Steven Schiller dated 12/11/18, “T&D losses are accounted for in the Companies' estimates of the net generation required to meet customer demand. The Companies electricity sales forecasts (e.g. kWh) are assumed to be energy consumption at an end user’s site. The T&D losses incurred to supply electricity to our customers are accounted for in the quantity of generation required by utility and independent power producers by adjusting or increasing the sales forecast by an estimated T&D loss factor.”
The time value of money is represented by a discount rate of 6%. The 6% value has been the historic discount rate since 2013. (The TRMs for 2011 and 2012 don’t indicate a specific rate). The Commission may review and update this discount rate at a later date. The discount rate is used to convert all costs and benefits to a “net present value” for comparing alternative costs and benefits in the same years’ dollars.
Single Baseline Measures
The cumulative NPV values can be used in the TRB calculations for measures with a single baseline. For example, the TRB calculation for a measure installed in Oahu in PY25 with a measure life of 8 years and a single baseline period could use the cumulative NPV values of $1,968/kW and $1.513/kWh from Table 3 in the calculation. Equation 1 below shows the algorithm for calculating the TRB for a single baseline measure.
(1)
Where:
NTGRProg = Net-to-gross ratio for the applicable program. See Table 6 below.
ΔkWh1st yr Gross Cust_Meas = Sum of first year gross customer level energy savings for the measure by County.
ΔkW1st yr Gross Cust_Meas = Sum of first year gross customer level peak demand savings for the measure by County.
[Cumul. NPV avoided energy cost]Meas yr=EUL = Cumulative NPV for avoided energy cost for the final year of the EUL. See Tables 3 through 5 below. Select correct program year. Select value for Measure Year = EUL and for correct County.
[Cumul. NPV avoided capacity cost]Meas yr=EUL = Cumulative NPV for avoided capacity cost for the final year of the EUL. See Tables 3 through 5 below. Select correct program year. Select value for Measure Year = EUL and for correct County.
Dual Baseline Measures
For measures with a dual baseline, the NPV values must be used differently since there are two separate savings periods. One way is to use annual NPV values. For example, if the duration of the first baseline period is 2 years, the annual NPV values for Measure Year 1 and Measure Year 2 would be used in the calculations along with the annual impacts associated with that first 2-year baseline period. Then, if the second baseline period is 6 years (for a total measure life of 8 years), the annual values for Measure Years 3 through 8 would be used with the annual impacts associated with the second 6-year baseline period. Another way is to use the cumulative NPV values in a special manner that accounts for the two separate baseline periods. Equation 2 below shows the algorithm for calculating the TRB for a dual baseline measure using cumulative NPV values.
(2)
Where:
NTGRProg = Net-to-gross ratio for the applicable program. See Table 6 below.
ΔkWh1st BL Gross Cust_Meas = Sum of the first baseline first year gross customer level energy savings for the measure by County.
ΔkW1st BL Gross Cust_Meas = Sum of the first baseline first year gross customer level peak demand savings for the measure by County.
ΔkWh2nd BL Gross Cust_Meas = Sum of the second baseline first year gross customer level energy savings for the measure by County.
ΔkW2nd BL Gross Cust_Meas = Sum of the second baseline first year gross customer level peak demand savings for the measure by County.
[Cumulative NPV avoided energy cost]Meas yr=RUL = a) Early Replacement Projects: Cumulative NPV for avoided energy cost for the final year of the RUL of the pre-existing equipment, OR b) Replace-on-Burnout Projects Subject to Upcoming Codes and Standards: Cumulative NPV for avoided energy cost for the final year of the EUL of the first baseline equipment. See Tables 3 through 5 below. Select correct program year. Select value for correct County and for Measure Year = RUL or first baseline period EUL.
[Cumulative NPV avoided capacity cost]Meas yr=RUL = a) Early Replacement Projects: Cumulative NPV for avoided capacity cost for the final year of the RUL of the pre-existing equipment, OR b) Replace-on-Burnout Projects Subject to Upcoming Codes and Standards: Cumulative NPV for avoided capacity cost for the final year of the EUL of the first baseline equipment. See Tables 3 through 5 below. Select correct program year. Select value for correct County and for Measure Year = RUL or first baseline period EUL.
[Cumulative NPV avoided energy cost]Meas yr=EUL = Cumulative NPV for avoided energy cost for the final year of the high efficiency equipment's EUL. See Tables 3 through 5 below. Select correct program year. Select value for correct County and for Measure Year = high efficiency case EUL.
[Cumulative NPV avoided capacity cost]Meas yr=EUL = Cumulative NPV value for avoided capacity cost for the final year of the high efficiency equipment's EUL. See Tables 3 through 5 below. Select correct program year. Select value for correct County and for Measure Year = high efficiency case EUL.
Early Replacement of Fluorescent Lighting - Special Dual Baseline Case
Early replacement of fluorescent lighting represents a special dual baseline case. For any measures where pre-existing fluorescent lighting is replaced with LED lighting, the second baseline period is assumed to have zero savings. The reason for the zero savings in the second baseline period is the sale of fluorescent bulbs and linear lamps is now banned in Hawaii; therefore, LED lighting is the only remaining choice for new lighting in most applications that formerly used fluorescent lamps. When calculating the TRB for measures involving early replacement of fluorescent lighting with LED lighting, use Equation 3 below.
(3)
Where:
NTGRProg = Net-to-gross ratio for the applicable program. See Table 6 below.
ΔkWh1st BL Gross Cust_Meas = Sum of the first baseline first year gross customer level energy savings for the measure by County.
ΔkW1st BL Gross Cust_Meas = Sum of the first baseline first year gross customer level peak demand savings for the measure by County.
[Cumulative NPV avoided energy cost]Meas yr=RUL = Cumulative NPV for avoided energy cost for the final year of the RUL of the pre-existing fluorescent lighting. See Tables 3 through 5 below. Select correct program year. Select value for correct County and for Measure Year = RUL.
[Cumulative NPV avoided capacity cost]Meas yr=RUL = Cumulative NPV for avoided capacity cost for the final year of the RUL of the pre-existing fluorescent lighting. See Tables 3 through 5 below. Select correct program year. Select value for correct County and for Measure Year = RUL.
Deemed and semi-prescriptive measures requiring a dual baseline approach are listed below, with hyperlinks to the applicable measure sheets.
Deemed and Semi-Prescriptive:
|  | Residential | [11 empty] | Commercial
|  | R_HVAC_Window AC | [11 empty] | C_HVAC_Window AC
|  | - Window AC w/ Recycling | [11 empty] | - Window AC w/ Recycling
|  | R_HVAC_Central AC Retrofit | [11 empty] | C_Light_General
|  | R_WH_Faucet Aerator | [11 empty] | C_Light_Energy Advantage**
|  | R_WH_LFShowerhead | [11 empty] | C_Lighting_Refrigerated Case
|  | R_Appliance_Refrigerator | [11 empty] | C_Other_Transformer
- Refrigerator w/ Turn-In*
- Freezer w/ Turn-In*
R_Light_Linear LED
R_Light_Security Light
*These refrigerator/freezer measures have a combination of two savings pieces, each with different lifetimes
** SBDIL / Energy Advantage lighting projects use custom hours of use (HOU)
Some fully custom measures will also require a dual baseline approach, including the following:
Commercial Chiller, AC, Heat Pump, or VRF with Early Replacement
AVOIDED COST TABLES
Tables 3 through 5 contain the avoided cost data to be used in the TRB calculations for PY25, PY26, and PY27, respectively. Refer to the subsection called "Development of Avoided Costs" for the source of the data and the subsection called "Total Resource Benefits" for instructions on how to use the cost tables. While the three tables show the data for the full triennial period, only one table is used for the given program year. The two tables not in use for the current program year are grayed out.
Table 3. Total Resource Benefit Calculation for PY25 (Do not use for PY26 or PY27)
Discount Rate
6%
[6 empty] | Avoided Capacity Costs Discounted Annual $/kW-yr | [6 empty] | Avoided Energy Costs Discounted Annual $/kWh-yr |  |  |  | Avoided Capacity Costs NPV Cumulative from Final Year |  |  |  | Avoided Energy Costs NPV Cumulative from Final Year
[6 empty] | Oahu |  |  | Maui |  |  | Hawaii | Oahu | Maui | Hawaii |  | Oahu | Maui | Hawaii |  | Oahu | Maui | Hawaii
Year |  |  | Measure Year |  |  | $/kW-yr |  |  | $/kW-yr |  |  | $/kW-yr | $/kWh-yr | $/kWh-yr | $/kWh-yr |  | $/kW | $/kW | $/kW |  | $/kWh | $/kWh | $/kWh
2025 |  |  | 1 |  |  | 299 |  |  | 0 |  |  | 139 | 0.209 | 0.21 | 0.212 |  | 299 | 0 | 139 |  | 0.209 | 0.21 | 0.212
2026 |  |  | 2 |  |  | 282.0755 |  |  | 0 |  |  | 131.1321 | 0.20283 | 0.20377 | 0.20566 |  | 581 | 0 | 270 |  | 0.412 | 0.414 | 0.418
2027 |  |  | 3 |  |  | 266.1089 |  |  | 0 |  |  | 123.7095 | 0.19669 | 0.19758 | 0.20025 |  | 847 | 0 | 394 |  | 0.609 | 0.611 | 0.618
2028 |  |  | 4 |  |  | 251.0462 |  |  | 0 |  |  | 116.7071 | 0.19143 | 0.19227 | 0.19479 |  | 1098 | 0 | 511 |  | 0.8 | 0.804 | 0.813
2029 |  |  | 5 |  |  | 236.836 |  |  | 0 |  |  | 110.101 | 0.18614 | 0.18693 | 0.18931 |  | 1335 | 0 | 621 |  | 0.986 | 0.991 | 1.002
2030 |  |  | 6 |  |  | 223.4302 |  |  | 0 |  |  | 103.8689 | 0.18084 | 0.18158 | 0.18383 |  | 1558 | 0 | 725 |  | 1.167 | 1.172 | 1.186
2031 |  |  | 7 |  |  | 210.7832 |  |  | 0 |  |  | 97.9895 | 0.17554 | 0.17624 | 0.17836 |  | 1769 | 0 | 823 |  | 1.342 | 1.348 | 1.364
2032 |  |  | 8 |  |  | 198.8521 |  |  | 0 |  |  | 92.4429 | 0.17025 | 0.17158 | 0.17358 |  | 1968 | 0 | 915 |  | 1.513 | 1.52 | 1.538
2033 |  |  | 9 |  |  | 187.5963 |  |  | 0 |  |  | 87.2103 | 0.16564 | 0.16689 | 0.16877 |  | 2156 | 0 | 1002 |  | 1.678 | 1.687 | 1.707
2034 |  |  | 10 |  |  | 176.9776 |  |  | 0 |  |  | 82.2739 | 0.161 | 0.16218 | 0.16396 |  | 2333 | 0 | 1084 |  | 1.839 | 1.849 | 1.871
2035 |  |  | 11 |  |  | 166.96 |  |  | 0 |  |  | 77.6169 | 0.15635 | 0.15747 | 0.15914 |  | 2500 | 0 | 1162 |  | 1.996 | 2.007 | 2.03
2036 |  |  | 12 |  |  | 157.5095 |  |  | 0 |  |  | 73.2235 | 0.15171 | 0.15277 | 0.15488 |  | 2657 | 0 | 1235 |  | 2.147 | 2.159 | 2.185
2037 |  |  | 13 |  |  | 148.5938 |  |  | 0 |  |  | 69.0787 | 0.1476 | 0.14859 | 0.15058 |  | 2806 | 0 | 1304 |  | 2.295 | 2.308 | 2.335
2038 |  |  | 14 |  |  | 140.1829 |  |  | 0 |  |  | 65.1686 | 0.14346 | 0.1444 | 0.14628 |  | 2946 | 0 | 1370 |  | 2.438 | 2.452 | 2.481
2039 |  |  | 15 |  |  | 132.248 |  |  | 0 |  |  | 61.4798 | 0.13932 | 0.14021 | 0.14198 |  | 3078 | 0 | 1431 |  | 2.578 | 2.592 | 2.623
2040 |  |  | 16 |  |  | 124.7623 |  |  | 0 |  |  | 57.9998 | 0.13519 | 0.13645 | 0.13811 |  | 3203 | 0 | 1489 |  | 2.713 | 2.729 | 2.761
2041 |  |  | 17 |  |  | 117.7002 |  |  | 0 |  |  | 54.7168 | 0.13148 | 0.13266 | 0.13423 |  | 3321 | 0 | 1544 |  | 2.844 | 2.862 | 2.896
2042 |  |  | 18 |  |  | 111.038 |  |  | 0 |  |  | 51.6197 | 0.12775 | 0.12886 | 0.13035 |  | 3432 | 0 | 1595 |  | 2.972 | 2.99 | 3.026
2043 |  |  | 19 |  |  | 104.7528 |  |  | 0 |  |  | 48.6978 | 0.12402 | 0.12507 | 0.12682 |  | 3536 | 0 | 1644 |  | 3.096 | 3.116 | 3.153
2044 |  |  | 20 |  |  | 98.8234 |  |  | 0 |  |  | 45.9413 | 0.12064 | 0.12163 | 0.12328 |  | 3635 | 0 | 1690 |  | 3.217 | 3.237 | 3.276
2045 |  |  | 21 |  |  | 93.2296 |  |  | 0 |  |  | 43.3409 | 0.11724 | 0.11817 | 0.11973 |  | 3729 | 0 | 1733 |  | 3.334 | 3.355 | 3.396
2046 |  |  | 22 |  |  | 87.9525 |  |  | 0 |  |  | 40.8876 | 0.11384 | 0.11472 | 0.11649 |  | 3816 | 0 | 1774 |  | 3.448 | 3.47 | 3.512
2047 |  |  | 23 |  |  | 82.974 |  |  | 0 |  |  | 38.5732 | 0.11072 | 0.11156 | 0.11322 |  | 3899 | 0 | 1813 |  | 3.559 | 3.582 | 3.626
2048 |  |  | 24 |  |  | 78.2774 |  |  | 0 |  |  | 36.3898 | 0.1076 | 0.10838 | 0.10995 |  | 3978 | 0 | 1849 |  | 3.666 | 3.69 | 3.736
2049 |  |  | 25 |  |  | 73.8466 |  |  | 0 |  |  | 34.33 | 0.10447 | 0.10521 | 0.10694 |  | 4052 | 0 | 1883 |  | 3.771 | 3.795 | 3.842
Table 4. Total Resource Benefit Calculation for PY26 (Do not use for PY25 or PY27)
Discount Rate
6%
[6 empty] | Avoided Capacity Costs Discounted Annual $/kW-yr | [6 empty] | Avoided Energy Costs Discounted Annual $/kWh-yr |  |  |  | Avoided Capacity Costs NPV Cumulative from Final Year |  |  |  | Avoided Energy Costs NPV Cumulative from Final Year
[6 empty] | Oahu |  |  | Maui |  |  | Hawaii | Oahu | Maui | Hawaii |  | Oahu | Maui | Hawaii |  | Oahu | Maui | Hawaii
Year |  |  | Measure Year |  |  | $/kW-yr |  |  | $/kW-yr |  |  | $/kW-yr | $/kWh-yr | $/kWh-yr | $/kWh-yr |  | $/kW | $/kW | $/kW |  | $/kWh | $/kWh | $/kWh
2026 |  |  | 1 |  |  | 306 |  |  | 0 |  |  | 142 | 0.215 | 0.216 | 0.218 |  | 306 | 0 | 142 |  | 0.215 | 0.216 | 0.218
2027 |  |  | 2 |  |  | 288.6792 |  |  | 0 |  |  | 133.9623 | 0.20849 | 0.20943 | 0.21226 |  | 595 | 0 | 276 |  | 0.423 | 0.425 | 0.43
2028 |  |  | 3 |  |  | 272.3389 |  |  | 0 |  |  | 126.3795 | 0.20292 | 0.20381 | 0.20648 |  | 867 | 0 | 402 |  | 0.626 | 0.629 | 0.637
2029 |  |  | 4 |  |  | 256.9235 |  |  | 0 |  |  | 119.2259 | 0.19731 | 0.19815 | 0.20067 |  | 1124 | 0 | 522 |  | 0.824 | 0.827 | 0.837
2030 |  |  | 5 |  |  | 242.3807 |  |  | 0 |  |  | 112.4773 | 0.19169 | 0.19248 | 0.19486 |  | 1366 | 0 | 634 |  | 1.015 | 1.02 | 1.032
2031 |  |  | 6 |  |  | 228.661 |  |  | 0 |  |  | 106.1107 | 0.18607 | 0.18681 | 0.18906 |  | 1595 | 0 | 740 |  | 1.201 | 1.207 | 1.221
2032 |  |  | 7 |  |  | 215.7179 |  |  | 0 |  |  | 100.1044 | 0.18047 | 0.18188 | 0.18399 |  | 1811 | 0 | 840 |  | 1.382 | 1.389 | 1.405
2033 |  |  | 8 |  |  | 203.5075 |  |  | 0 |  |  | 94.4381 | 0.17558 | 0.17691 | 0.1789 |  | 2014 | 0 | 935 |  | 1.558 | 1.565 | 1.584
2034 |  |  | 9 |  |  | 191.9882 |  |  | 0 |  |  | 89.0926 | 0.17066 | 0.17191 | 0.17379 |  | 2206 | 0 | 1024 |  | 1.728 | 1.737 | 1.758
2035 |  |  | 10 |  |  | 181.1209 |  |  | 0 |  |  | 84.0496 | 0.16573 | 0.16692 | 0.16869 |  | 2387 | 0 | 1108 |  | 1.894 | 1.904 | 1.927
2036 |  |  | 11 |  |  | 170.8688 |  |  | 0 |  |  | 79.2921 | 0.16082 | 0.16193 | 0.16417 |  | 2558 | 0 | 1187 |  | 2.055 | 2.066 | 2.091
2037 |  |  | 12 |  |  | 161.197 |  |  | 0 |  |  | 74.8038 | 0.15646 | 0.15751 | 0.15962 |  | 2719 | 0 | 1262 |  | 2.211 | 2.224 | 2.25
2038 |  |  | 13 |  |  | 152.0726 |  |  | 0 |  |  | 70.5696 | 0.15207 | 0.15307 | 0.15505 |  | 2871 | 0 | 1333 |  | 2.363 | 2.377 | 2.406
2039 |  |  | 14 |  |  | 143.4647 |  |  | 0 |  |  | 66.5751 | 0.14768 | 0.14862 | 0.1505 |  | 3015 | 0 | 1399 |  | 2.511 | 2.525 | 2.556
2040 |  |  | 15 |  |  | 135.3441 |  |  | 0 |  |  | 62.8067 | 0.14331 | 0.14463 | 0.1464 |  | 3150 | 0 | 1462 |  | 2.654 | 2.67 | 2.702
2041 |  |  | 16 |  |  | 127.6831 |  |  | 0 |  |  | 59.2516 | 0.13937 | 0.14062 | 0.14229 |  | 3278 | 0 | 1521 |  | 2.794 | 2.811 | 2.845
2042 |  |  | 17 |  |  | 120.4558 |  |  | 0 |  |  | 55.8978 | 0.13541 | 0.1366 | 0.13817 |  | 3398 | 0 | 1577 |  | 2.929 | 2.947 | 2.983
2043 |  |  | 18 |  |  | 113.6375 |  |  | 0 |  |  | 52.7337 | 0.13146 | 0.13258 | 0.13443 |  | 3512 | 0 | 1630 |  | 3.06 | 3.08 | 3.117
2044 |  |  | 19 |  |  | 107.2052 |  |  | 0 |  |  | 49.7488 | 0.12788 | 0.12893 | 0.13068 |  | 3619 | 0 | 1680 |  | 3.188 | 3.209 | 3.248
2045 |  |  | 20 |  |  | 101.137 |  |  | 0 |  |  | 46.9328 | 0.12427 | 0.12526 | 0.12692 |  | 3720 | 0 | 1726 |  | 3.313 | 3.334 | 3.375
2046 |  |  | 21 |  |  | 95.4122 |  |  | 0 |  |  | 44.2763 | 0.12067 | 0.1216 | 0.12347 |  | 3816 | 0 | 1771 |  | 3.433 | 3.456 | 3.498
2047 |  |  | 22 |  |  | 90.0116 |  |  | 0 |  |  | 41.7701 | 0.11737 | 0.11825 | 0.12002 |  | 3906 | 0 | 1812 |  | 3.551 | 3.574 | 3.618
2048 |  |  | 23 |  |  | 84.9166 |  |  | 0 |  |  | 39.4057 | 0.11405 | 0.11489 | 0.11655 |  | 3991 | 0 | 1852 |  | 3.665 | 3.689 | 3.735
2049 |  |  | 24 |  |  | 80.11 |  |  | 0 |  |  | 37.1752 | 0.11074 | 0.11153 | 0.11336 |  | 4071 | 0 | 1889 |  | 3.775 | 3.8 | 3.848
2050 |  |  | 25 |  |  | 75.5754 |  |  | 0 |  |  | 35.071 | 0.10768 | 0.10842 | 0.11015 |  | 4146 | 0 | 1924 |  | 3.883 | 3.909 | 3.958
Table 5. Total Resource Benefit Calculation for PY27 (Do not use for PY25 or PY26)
Discount Rate
6%
[6 empty] | Avoided Capacity Costs Discounted Annual $/kW-yr | [6 empty] | Avoided Energy Costs Discounted Annual $/kWh-yr |  |  |  | Avoided Capacity Costs NPV Cumulative from Final Year |  |  |  | Avoided Energy Costs NPV Cumulative from Final Year
[6 empty] | Oahu |  |  | Maui |  |  | Hawaii | Oahu | Maui | Hawaii |  | Oahu | Maui | Hawaii |  | Oahu | Maui | Hawaii
Year |  |  | Measure Year |  |  | $/kW-yr |  |  | $/kW-yr |  |  | $/kW-yr | $/kWh-yr | $/kWh-yr | $/kWh-yr |  | $/kW | $/kW | $/kW |  | $/kWh | $/kWh | $/kWh
2027 |  |  | 1 |  |  | 313 |  |  | 0 |  |  | 145 | 0.221 | 0.222 | 0.225 |  | 313 | 0 | 145 |  | 0.221 | 0.222 | 0.225
2028 |  |  | 2 |  |  | 295.283 |  |  | 0 |  |  | 136.7925 | 0.21509 | 0.21604 | 0.21887 |  | 608 | 0 | 282 |  | 0.436 | 0.438 | 0.444
2029 |  |  | 3 |  |  | 278.5689 |  |  | 0 |  |  | 129.0495 | 0.20915 | 0.21004 | 0.21271 |  | 887 | 0 | 411 |  | 0.645 | 0.648 | 0.657
2030 |  |  | 4 |  |  | 262.8008 |  |  | 0 |  |  | 121.7448 | 0.20319 | 0.20403 | 0.20655 |  | 1150 | 0 | 533 |  | 0.848 | 0.852 | 0.863
2031 |  |  | 5 |  |  | 247.9253 |  |  | 0 |  |  | 114.8536 | 0.19723 | 0.19802 | 0.2004 |  | 1398 | 0 | 647 |  | 1.046 | 1.05 | 1.064
2032 |  |  | 6 |  |  | 233.8918 |  |  | 0 |  |  | 108.3524 | 0.1913 | 0.19279 | 0.19503 |  | 1631 | 0 | 756 |  | 1.237 | 1.243 | 1.259
2033 |  |  | 7 |  |  | 220.6526 |  |  | 0 |  |  | 102.2193 | 0.18611 | 0.18752 | 0.18963 |  | 1852 | 0 | 858 |  | 1.423 | 1.43 | 1.448
2034 |  |  | 8 |  |  | 208.1629 |  |  | 0 |  |  | 96.4333 | 0.1809 | 0.18223 | 0.18422 |  | 2060 | 0 | 954 |  | 1.604 | 1.613 | 1.632
2035 |  |  | 9 |  |  | 196.3801 |  |  | 0 |  |  | 90.9748 | 0.17568 | 0.17693 | 0.17881 |  | 2257 | 0 | 1045 |  | 1.78 | 1.79 | 1.811
2036 |  |  | 10 |  |  | 185.2642 |  |  | 0 |  |  | 85.8253 | 0.17047 | 0.17165 | 0.17402 |  | 2442 | 0 | 1131 |  | 1.95 | 1.961 | 1.985
2037 |  |  | 11 |  |  | 174.7776 |  |  | 0 |  |  | 80.9672 | 0.16584 | 0.16696 | 0.16919 |  | 2617 | 0 | 1212 |  | 2.116 | 2.128 | 2.154
2038 |  |  | 12 |  |  | 164.8845 |  |  | 0 |  |  | 76.3842 | 0.1612 | 0.16225 | 0.16436 |  | 2782 | 0 | 1289 |  | 2.277 | 2.29 | 2.319
2039 |  |  | 13 |  |  | 155.5514 |  |  | 0 |  |  | 72.0606 | 0.15655 | 0.15754 | 0.15953 |  | 2937 | 0 | 1361 |  | 2.434 | 2.448 | 2.478
2040 |  |  | 14 |  |  | 146.7466 |  |  | 0 |  |  | 67.9817 | 0.1519 | 0.15331 | 0.15519 |  | 3084 | 0 | 1429 |  | 2.586 | 2.601 | 2.634
2041 |  |  | 15 |  |  | 138.4402 |  |  | 0 |  |  | 64.1336 | 0.14773 | 0.14906 | 0.15082 |  | 3222 | 0 | 1493 |  | 2.733 | 2.75 | 2.784
2042 |  |  | 16 |  |  | 130.604 |  |  | 0 |  |  | 60.5034 | 0.14354 | 0.14479 | 0.14646 |  | 3353 | 0 | 1553 |  | 2.877 | 2.895 | 2.931
2043 |  |  | 17 |  |  | 123.2113 |  |  | 0 |  |  | 57.0787 | 0.13935 | 0.14053 | 0.1425 |  | 3476 | 0 | 1610 |  | 3.016 | 3.036 | 3.073
2044 |  |  | 18 |  |  | 116.2371 |  |  | 0 |  |  | 53.8478 | 0.13555 | 0.13666 | 0.13852 |  | 3592 | 0 | 1664 |  | 3.152 | 3.172 | 3.212
2045 |  |  | 19 |  |  | 109.6576 |  |  | 0 |  |  | 50.7998 | 0.13173 | 0.13278 | 0.13453 |  | 3702 | 0 | 1715 |  | 3.283 | 3.305 | 3.346
2046 |  |  | 20 |  |  | 103.4506 |  |  | 0 |  |  | 47.9244 | 0.12791 | 0.1289 | 0.13088 |  | 3805 | 0 | 1763 |  | 3.411 | 3.434 | 3.477
2047 |  |  | 21 |  |  | 97.5949 |  |  | 0 |  |  | 45.2117 | 0.12441 | 0.12535 | 0.12722 |  | 3903 | 0 | 1808 |  | 3.536 | 3.559 | 3.604
2048 |  |  | 22 |  |  | 92.0706 |  |  | 0 |  |  | 42.6525 | 0.1209 | 0.12178 | 0.12355 |  | 3995 | 0 | 1851 |  | 3.657 | 3.681 | 3.728
2049 |  |  | 23 |  |  | 86.8591 |  |  | 0 |  |  | 40.2382 | 0.11738 | 0.11822 | 0.12016 |  | 4082 | 0 | 1891 |  | 3.774 | 3.799 | 3.848
2050 |  |  | 24 |  |  | 81.9425 |  |  | 0 |  |  | 37.9606 | 0.11414 | 0.11493 | 0.11676 |  | 4164 | 0 | 1929 |  | 3.888 | 3.914 | 3.965
2051 |  |  | 25 |  |  | 77.3043 |  |  | 0 |  |  | 35.8119 | 0.11089 | 0.11163 | 0.11336 |  | 4241 | 0 | 1965 |  | 3.999 | 4.026 | 4.078
GROSS-TO-NET CALCULATIONS
The algorithms shown with each measure calculate gross customer electric savings without counting the effects of line losses from the generator to the customer or free ridership. The formula for converting gross customer-level savings to net generation-level savings are as follows:
Net Program kWh = Gross Customer Level ΔkWh × (1 + SLF) x NTGR
Net Program kW = Gross Customer Level ΔkW × (1 + SLF) x NTGR
[6 empty] | Net kWh : | kWh energy savings at generation-level, net of free riders and system losses
[6 empty] | Net kW : | kW savings at generation-level, net of free riders and system losses
[6 empty] | Gross Cust. ΔkWh : | Gross customer level annual kWh savings for the measure
[6 empty] | Gross Cust. ΔkW : | Gross customer level coincident peak demand reduction in kW for the measure
[6 empty] | SLF : | System Loss Factor (see Table 7 in the "System Loss Factor" section below)
[6 empty] | NTGR : | Net-to-Gross Ratio (see Table 6 below)
Net-to-Gross Ratio (NTGR)
In Fall 2018, AEG reviewed the NTGR values by updating the benchmarking approach taken by Evergreen Economics during the PY11 evaluation and leveraging NTGR data collected by Opinion Dynamics in 2018. The benchmarking analysis resulted in a new NTGR of 0.91 for BHTR. More details on the NTGR review and update are in the file named "AEG HPUC NTG Benchmarking Analysis." In Winter 2020, AEG updated the LED Upstream NTGR to include market effects. In Fall 2022, AEG added NTGRs for BGRID and RGRID.
Table 6. Net-to-Gross Ratios by Program
Program | [15 empty] | NTGR
BEEM |  |  | Business Energy Efficiency Measures | [7 empty] | All BEEM Measures |  |  |  |  | 0.75
CBEEM |  |  | Custom Business Energy Efficiency Measures | [7 empty] | All CBEEM Measures |  |  |  |  | 0.75
BESM |  |  | Business Energy Services and Maintenance | [7 empty] | All BESM Measures |  |  |  |  | 0.95
BHTR |  |  | Business Hard-to-Reach | [7 empty] | All BHTR Measures |  |  |  |  | 0.91
BGRID |  |  | Business Grid Services Ready | [7 empty] | All BGRID Measures |  |  |  |  | 1
REEM |  |  | Residential Energy Efficiency Measures | [7 empty] | All REEM Measures |  |  |  |  | 0.79
CREEM |  |  | Custom Residential Energy Efficiency Measures | [7 empty] | All CREEM Measures |  |  |  |  | 0.65
RESM |  |  | Residential Energy Services and Maintenance | [7 empty] | All RESM Measures |  |  |  |  | 0.92
RHTR |  |  | Residential Hard-to-Reach | [7 empty] | All RHTR Measures |  |  |  |  | 1
RGRID |  |  | Residential Grid Services Ready | [7 empty] | All RGRID Measures |  |  |  |  | 1
Sources: |  |  | 1. AEG's 2018 Analysis File named "AEG HPUC NTG Benchmarking Analysis."
2. Evaluation of the Hawai‘i Energy Conservation and Efficiency Programs, Program Year 2011, Evergreen Economics, June 20, 2013, Appendix D: Net-to-Gross Assessment Memo. NTG benchmarking analysis covered four resources: Wisconsin Focus on Energy (2011), CPUC DEER (2006-2007), Massachusetts Energy Efficiency Advisory Council (2010), and NYSERDA (2011-12).
3. Opinion Dynamics, Hawai‘i Baseline and Net-to-Gross Framework, Memorandum, Submitted to Steve Schiller, June 27, 2018.
4. LED Market Transformation Attribution to Hawai’i Energy, Memorandum, Prepared for Energy Efficiency Manager and Hawaii Public Utilities Commission, Prepared by Applied Energy Group, December 15, 2019.
5. AEG's 2022 Analysis File named "Mid-year PY22 TRM - BGRID and RGRID NTG - Analysis File."
SYSTEM LOSS FACTOR (SLF)
Energy savings at the customer level are equivalent to even greater savings at the power plant busbar (where the electrons enter the grid) due to energy losses during transmission and distribution. The system loss factor (SLF) is defined as marginal electricity losses from the busbar to the customer meter – expressed as a percent of meter-level savings. Each island in Hawaii has a different SLF due to differences in infrastructure. SLF values are derived using island-level loss data published for HECO, MECO, and HELCO. The customer-level electricity savings are multiplied by (1+SLF) to get the system-level savings, or savings at the power plant busbar.
Table 7 provides the SLF values updated for the PY25-PY27 TRMs. The values were derived using the following approach:
1. | Obtaining data on "Losses and Unaccounted for Energy" from Hawaiian Electric Company's website <https://www.hawaiianelectric.com/about-us/performance-scorecards-and-metrics/power-supply-and-generation>. (ICF downloaded file named "historical_02_losses.xlsx" on Apr. 13, 2025.) Note that the published losses include “…amount of energy that is lost as heat or through other means (such as theft) or used by the Company between the point where energy generated at power plants enters the grid to the point of measurement at customer’s meters.”
2. | Calculating average loss factors from the data in Step 1 for each island for the last five years (2020-2024).
3. | Adjusting the loss factors in Step 2 to remove losses due to theft and the utility's own electricity consumption in its building and facilities, so that the losses only reflect transmission and distribution losses. An engineering estimate of 0.1% off of each of the values from Step 2 was used for the adjustment.
Table 7. System Loss Factors by Island
System Loss Factors
Hawaii |  |  |  | 5.444%
Lanai |  |  |  | 4.648%
Maui |  |  |  | 4.482%
Molokai |  |  |  | 8.48%
Oahu |  |  |  | 4.544%
For more information on the derivation of the PY25-PY27 SLF values, please refer to ICF's PY25 analysis file titled "PY25 TRM - Key Metrics - Analysis File." For background on the approach originally developed during the PY19 TRM updated, refer to the following memo: Recommendations for PY19 System Loss Factors (SLF) for Hawai‘i Energy Programs Goals and Reporting, Memorandum, Prepared by Steve Schiller, EEM team, Prepared for Ashley Norman and Dave Parsons, HPUC, January 4, 2019.
GREENHOUSE GAS (GHG) CALCULATOR
Use the following calculator to estimate avoided emissions and equivalent avoided barrels of oil due to program-level annual energy savings. The calculator requires users to input Annual Program Level Energy Savings in kWh units. It then uses emission rates from Table 8 to calculate avoided emissions in pounds (lbs) and metric tons (MT). It also uses Table 9 to convert CO2 emissions to equivalent avoided barrels of oil (bbl).
The eGRID emission rates in Table 8 should be updated periodically as new eGRID data becomes available. It is preferable to directly use the eGRID CO2e emission rate to estimate avoided CO2e emissions over using global warming potential (GWP) factors to calculate the CO2 equivalent emission rates for CH4 and NO2 separately and then sum with the CO2 emission rate to estimate the avoided CO2e emissions. There are two main reasons for this: 1) using a single emission rate simplifies the calculation, and 2) since the GWP factors for CH4 and NO2 are occasionally updated by the EPA, using the pre-calculated CO2e emission rate from eGRID ensures the inherent use of the most recent GWP factors in the calculation.
Table 8. State of Hawaii Emission Rates
| Gas | [6 empty] | Total Output Emission Rates
[8 empty] | lbs/MWh |  |  |  |  | MT/MWh i
| CO2 | [6 empty] | 1385.1 |  |  |  |  | 0.62827
| CH4 | [6 empty] | 0.137 |  |  |  |  | 6.2142e-05
| N2O | [6 empty] | 0.022 |  |  |  |  | 9.979e-06
| CO2e ii | [6 empty] | 1394.7 |  |  |  |  | 0.63263
| Annual NOx | [6 empty] | 5 |  |  |  |  | 0.002268
| Ozone Season NOx | [6 empty] | 4.7 |  |  |  |  | 0.0021319
| SO2 | [6 empty] | 4.339 |  |  |  |  | 0.0019681
| Notes: |  |  | i To convert between lbs and metric tons (MT) use this factor: 2,204.62 lbs/MT.
ii The CO2e metric represents equivalent CO2 emissions from CO2, CH4, and N2O emissions. The CH4 and N2O emissions are converted to equivalent CO2 emissions using 100-year global warming potential (GWP) factors that account for the higher GWP of CH4 and N2O relative to CO2. The U.S. EPA periodically updates the 100-year GWP values and the corresponding conversion factors as the Intergovernmental Panel on Climate Change (IPCC) releases new data. For the eGRID 2023 CO2e calculations, the EPA uses GWP values from the Fifth IPCC Assessment Report (AR5, without climate feedback) and assumes CH4 has a GWP of 28 times that of CO2 over 100 years and N2O has a GWP of 265 times that of CO2 for a 100-year timescale.
| Sources: |  |  | 1. U.S. Environmental Protection Agency, Emissions & Generation Resource Integrated Database (eGRID), Summary Data, Table 3. State Output Emission Rates (eGRID2023), Data for State of Hawaii, Created March 27, 2025, Released June 12, 2025, https://www.epa.gov/system/files/documents/2025-06/summary_tables_rev2.pdf.
2. The Emissions & Generation Resource Integrated Database, eGRID Technical Guide with Year 2023 Data, U.S. Environmental Protection Agency, January 2025, https://www.epa.gov/system/files/documents/2025-01/egrid2023_technical_guide.pdf.
Table 9. Conversion of CO2 Emissions to Equivalent Barrels (bbl) of Crude Oil
| 1 bbl Oil = |  |  |  |  | 0.43 |  | MT of CO2
Note: This conversion only uses CO2 emissions and not CO2e emissions from CH4 and N2O.
Source: Greenhouse Gases Equivalencies Calculator - Calculations and References, U.S Environmental Protection Agency, Barrels of Oil Consumed, accessed April 15, 2025, https://www.epa.gov/energy/greenhouse-gas-equivalencies-calculator-calculations-and-references.
GHG Calculator
Input Annual Program Level Energy Savings in kWh/yr:
100000000
Table 10. Equivalent CO2 Emissions:
| Equivalent CO2 Emissions | [6 empty] | lbs |  |  |  |  | MT
| CO2e | [6 empty] | 139470000 |  |  |  |  | 63262.6031
Table 11. Avoided Emissions by Type of Gas:
| Gas | [6 empty] | Total Avoided Emissions
[8 empty] | lbs |  |  |  |  | MT
| CO2 | [6 empty] | 138510000 |  |  |  |  | 62827.1539
| CH4 | [6 empty] | 13700 |  |  |  |  | 6.2142
| N2O | [6 empty] | 2200 |  |  |  |  | 0.9979
| Annual NOx | [6 empty] | 500000 |  |  |  |  | 226.7965
| Ozone Season NOx | [6 empty] | 470000 |  |  |  |  | 213.1887
| SO2 | [6 empty] | 433900 |  |  |  |  | 196.814
Table 12. Avoided Barrels of Oil:
| Barrels of Oil | [6 empty] | 146109.6602
)
〖𝑇𝑅𝐵〗_(𝑆𝑖𝑛𝑔𝑙𝑒 𝐵𝐿 𝑀𝑒𝑎𝑠)=
𝑁𝑇𝐺𝑅_𝑃𝑟𝑜𝑔∗(∆𝑘𝑊ℎ_(1𝑠𝑡 𝑦𝑟 𝐺𝑟𝑜𝑠𝑠 𝐶𝑢𝑠𝑡_𝑀𝑒𝑎𝑠 )∗[𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑒𝑛𝑒𝑟𝑔𝑦 𝑐𝑜𝑠𝑡]_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝐸𝑈𝐿)
+∆𝑘𝑊_(1𝑠𝑡 𝑦𝑟 𝐺𝑟𝑜𝑠𝑠 𝐶𝑢𝑠𝑡_𝑀𝑒𝑎𝑠 )∗[𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑐𝑜𝑠𝑡]_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝐸𝑈𝐿))
)
}
〖𝑇𝑅𝐵〗_(𝐷𝑢𝑎𝑙 𝐵𝐿 𝑀𝑒𝑎𝑠)=
𝑁𝑇𝐺𝑅_𝑃𝑟𝑜𝑔∗{∆𝑘𝑊ℎ_(1𝑠𝑡 𝐵𝐿 𝐺𝑟𝑜𝑠𝑠 𝐶𝑢𝑠𝑡_𝑀𝑒𝑎𝑠 )∗[𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑒𝑛𝑒𝑟𝑔𝑦 𝑐𝑜𝑠𝑡]_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝑅𝑈𝐿)
+∆𝑘𝑊_(1𝑠𝑡 𝐵𝐿 𝐺𝑟𝑜𝑠𝑠 𝐶𝑢𝑠𝑡_𝑀𝑒𝑎𝑠 )∗[𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑐𝑜𝑠𝑡]_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝑅𝑈𝐿)
+∆𝑘𝑊ℎ_(2𝑛𝑑 𝐵𝐿 𝐺𝑟𝑜𝑠𝑠 𝐶𝑢𝑠𝑡_𝑀𝑒𝑎𝑠 )∗〖([𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑒𝑛𝑒𝑟𝑔𝑦 𝑐𝑜𝑠𝑡]〗_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝐸𝑈𝐿)
−[𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑒𝑛𝑒𝑟𝑔𝑦 𝑐𝑜𝑠𝑡]_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝑅𝑈𝐿))
+∆𝑘𝑊_(2𝑛𝑑 𝐵𝐿 𝐺𝑟𝑜𝑠𝑠 𝐶𝑢𝑠𝑡_𝑀𝑒𝑎𝑠 )∗〖([𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑐𝑜𝑠𝑡]〗_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝐸𝑈𝐿)
−[𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑐𝑜𝑠𝑡]_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝑅𝑈𝐿) ")"}
}
〖𝑇𝑅𝐵〗_(𝐷𝑢𝑎𝑙 𝐵𝐿 𝐹𝐿 𝑀𝑒𝑎𝑠)=
𝑁𝑇𝐺𝑅_𝑃𝑟𝑜𝑔∗{∆𝑘𝑊ℎ_(1𝑠𝑡 𝐵𝐿 𝐺𝑟𝑜𝑠𝑠 𝐶𝑢𝑠𝑡_𝑀𝑒𝑎𝑠 )∗[𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑒𝑛𝑒𝑟𝑔𝑦 𝑐𝑜𝑠𝑡]_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝑅𝑈𝐿)
+∆𝑘𝑊_(1𝑠𝑡 𝐵𝐿 𝐺𝑟𝑜𝑠𝑠 𝐶𝑢𝑠𝑡_𝑀𝑒𝑎𝑠 )∗[𝐶𝑢𝑚𝑢𝑙. 𝑁𝑃𝑉 𝑎𝑣𝑜𝑖𝑑𝑒𝑑 𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑐𝑜𝑠𝑡]_(𝑀𝑒𝑎𝑠 𝑦𝑟=𝑅𝑈𝐿)}

## Master EUL
EFFECTIVE USEFUL LIFE
Return to TOC
UPDATE STATUS
A major update was conducted in Fall 2018 for the PY19 TRM. There were subsequent updates during 2020 through 2026 for new measures.
TABLE OF VALUES
Effective Useful Life (EUL) is the median length of time (in years) that an energy efficiency measure is functional. The EUL estimated for each measure is shown in the following table:
Residential Measures
Program |  | Measure Type | Description | EUL (years) | TRM Review/Update Approach
REEM |  | Water Heating | Solar Water Heating | 18 | AEG 2018 Analysis1
|  |  | Heat Pumps | 10 | DEER 20202
|  | Lighting | LED (See R_Light_LED, Table 2) | Varies | Depends on HOU3
|  |  | Occupancy Sensor | 10 | AEG 2018 Analysis
|  |  | Linear LED | 25 | Capped at 25 yr
|  |  | LED Security Light | 6 | Based on HOU
|  |  | LED String Lights | 5 | Engr. Estimate
|  |  | Solar Light Tube | 10 | AEG 2021 Analysis4
|  | HVAC | Ductless Split System | 15 | AEG 2018 Analysis
|  |  | Window AC w/ and w/o recycling | 9 | DEER 2020
|  |  | Ceiling Fans | 5 | Not updated5
|  |  | Solar Attic Fans | 20 | Not updated
|  |  | Whole House Fans | 20 | DEER 2020
|  |  | Dehumidifier - Portable | 10 | AEG 2025 Analysis6
|  |  | Dehumidifier - Whole Home | 12 | AEG 2025 Analysis
|  | Appliances | Refrigerator | 14 | AEG 2018 Analysis
|  |  | Freezer | 17 | AEG 2018 Analysis
|  |  | Refrigerator Turn-In (Remaining Useful Life) | 8 | AEG 2018 Analysis
|  |  | Freezer Turn-In (Remaining Useful Life) | 7 | AEG 2018 Analysis
|  |  | Garage Refrigerator/Freezer Bounty | 14 | Not updated
|  |  | Dishwasher | 11 | DEER 2020
|  |  | Clothes Washer (Tier I/II/III) | 12 | AEG 2023 Analysis7
|  |  | Heat Pump Clothes Dryer | 12 | CA eTRM, Jan 2023
|  |  | Clothes Dryer | 14 | Not updated
|  |  | Air Purifier | 9 | AEG 2025 Analysis
|  |  | Cooktop | 16 | CA eTRM, Jan 2023
|  | Electronics | Television | 6 | AEG 2021 Analysis
|  |  | Set top box | 5 | Not updated
|  |  | Electronics Soundbar | 4 | DEER 2020
|  | Pump / Motor | Pool VFD Controller Pumps | 10 | AEG 2018 Analysis
|  | Plug / Process | Advanced Power Strip and Switch Plug | 5 | AEG 2021 Analysis
|  |  | EV Charger | 10 | NPCC RTF Jul 2023
|  | Control Systems | Room Occupancy Sensors & Timers | 8 | Not updated
|  |  | Peer Group Comparison | 1 | Not updated
|  |  | Whole House Energy Metering | 4 | Not updated
|  |  | Water Cooler Timer | 8 | Not updated
CREEM |  | Custom | Efficiency Project Auction | 5 | Not updated
|  | Building Envelope | Cool Wall | 10 | AEG 2021 Analysis
RESM |  | Design and Audits | Efficiency Inside | 15 | Not updated
|  | Water Heating | Solar Water Heater Tune Up | 5 | No data found8
|  | HVAC | Central Air Conditioning Retrofit | 15 | DEER 2020
|  | HVAC | Central Air Conditioning Tune-Up | 3 | DEER 2020
RHTR |  | Hard to Reach Grants | CFL Exchange | 6 | Not updated
|  |  | Refrigerator Turn-In (Remaining Useful Life) | 8 | AEG 2018 Analysis
|  |  | Freezer Turn-In (Remaining Useful Life) | 7 | AEG 2018 Analysis
|  | Water Heating | Solar Water Heating | 18 | AEG 2018 Analysis
|  | Direct Install | Energy Saving Kits | 6 | Not updated
|  |  | Faucet Aerators | 10 | AEG 2018 Analysis
|  |  | Low Flow Showerheads | 10 | DEER 2020
|  |  | Smart Thermostats | 7 | AEG 2022 Analysis9
Commercial Measures
Program |  | Measure Type | Description | EUL (years) | TRM Review/Update Approach
BEEM |  | Water Heating | Solar Water Heating - Electric Resistance | 18 | AEG 2018 Analysis
|  |  | Solar Water Heating - Heat Pump | 18 | AEG 2018 Analysis
|  |  | Heat Pump - conversion - Electric Resistance | 10 | DEER 2020
|  |  | Heat Pump Upgrade | 10 | DEER 2020
|  |  | Single Family Solar Water Heating | 18 | AEG 2018 Analysis
|  | Lighting | General, Baseline (See C_Light_General, Table 6) | Varies | Depends on HOU
|  |  | General, Efficient Case (See C_Light_General, Table 7) | Varies | Depends on HOU
|  |  | LED Exit Signs | 18 | Lamp Life/8760
|  |  | LED Refrigerator Case Lighting | 8 | Lamp Life/6205
|  |  | LED Street and Parking Lot Fixture | 12 | Lamp Life/4100
|  |  | Occupancy Sensor | 8 | AEG 2018 Analysis
|  |  | Stairwell Bi-Level Dimming Fluorescent | 8 | AEG 2018 Analysis
|  |  | Horticulture Lighting | 10 | AEG 2024 Analysis10
|  | HVAC | Chillers | 22 | AEG 2018 Analysis
|  |  | Chiller Plant Efficiency kW/Ton Meter | 20 | Not updated
|  |  | Garage Active Ventilation Control | 8 | Not updated
|  |  | Package Units | 15 | DEER 2020
|  |  | Window AC | 9 | DEER 2020
|  |  | VFR Split System – New Construction | 20 | AEG 2018 Analysis
|  |  | VFR Split System – Existing | 20 | AEG 2018 Analysis
|  |  | VFD – AHU | 15 | DEER 2020
|  |  | VFD – Chilled Water / Condenser Water | 15 | AEG 2018 Analysis
|  |  | FEI-Certified Standalone Fan | 16 | ICF 2026 Analysis11
|  |  | DX-DOAS | 15 | ICF 2026 Analysis
|  | Water Pumping | VFD Dom Water Booster Packages | 15 | AEG 2018 Analysis
|  |  | VFD Pool Pump | 10 | AEG 2018 Analysis
|  |  | Smart Circulator Pump | 10 | ICF 2026 Analysis
|  | Motors | Premium Efficiency Motors | 15 | DEER 2020
|  |  | ECM w/ Controller – evap fan motors | 15 | Not updated
|  |  | ECM – Fan Coil Fans | 5 | RUL of motor (EUL/3)
|  | Industrial Process | Kitchen Exhaust Hood Demand Ventilation | 15 | AEG 2022 Analysis
|  |  | Refrigerated Case Night Covers | 5 | DEER 2020
|  | Refrigeration | Evaporator Fan Motor Controls, ECM | 15 | AEG 2020 Analysis12
|  |  | Evaporator Fan Motor Controls, SP Motor | 5 | RUL of motor (EUL/3)
|  |  | Adding Doors to Refrigerated Cases | 8 | AEG 2020 Analysis
|  |  | Floating Head Pressure Controls | 15 | DEER 2020
|  | Building Envelope | Window Film | 10 | AEG 2021 Analysis
|  |  | Cool Roof | 15 | DEER 2020
|  | Business Equipment | ENERGY STAR Refrigerator | 14 | AEG 2018 Analysis
|  |  | Clothes Washer | 11 | DEER 2020
|  |  | Energy Savings Kit | 6 | Not updated
|  | Control Systems | Energy Management System (EMS) | 15 | AEG 2018 Analysis
|  |  | Condominium submetering | 8 | Not updated
|  |  | Small Business submetering | 8 | Not updated
|  | Compressed Air | Air Receiver Tank | 15 | AEG 2024 Analysis
|  |  | No-Loss Condensate Drain | 10 | AEG 2024 Analysis
|  |  | VFD Compressor | 13 | AEG 2024 Analysis
CBEEM |  | Custom | Custom <= 5 years | 5 | Not updated
|  |  | Custom > 5 years | 13 | Not updated
|  |  | Efficiency Project Auction | 10 | Not updated
|  |  | Re/Retro Commissioning | 3 | DEER 2020
BESM |  | Design and Audits | Benchmark Metering | 1 | Not updated
|  |  | Decision Maker - Real time submeters | 1 | Not updated
|  |  | Energy Audit | N/A | Not updated
|  |  | Energy Study Implementation - 100% | N/A | Not updated
|  |  | Energy Study Assistance - 50% | N/A | Not updated
|  |  | Design Assistance - 50% | N/A | Not updated
|  |  | Water/Wastewater Catalyst | 15 | Not updated
BHTR |  | Direct Install | SBDI - Lighting, Efficient Case (See C_Light_General, Table 7) | Varies | Depends on HOU
|  |  | SBDI - Lighting, Pre-Existing Baseline RUL (See C_Light_General, Table 8) | Varies | Depends on HOU; RUL = 1/3 EUL
|  |  | Downlight Retrofit (see C_Light_Downlight Retrofit, Table 1) | Varies | Depends on HOU; RUL = 1 year
|  | Grants | Water cooler timer | 5 | Not updated
|  | Restaurant | SBDI - Kitchen Exhaust Hood Demand-Controlled Ventilation | 15 | AEG 2022 Analysis
|  |  | Low flow spray rinse nozzles | 5 | DEER 2020
|  |  | ENERGY STAR Kitchen Equipment | 12 | AEG 2023 Analysis
|  |  | ENERGY STAR Dishwasher (See C_Kitchen_Dishwasher, Table 5) | Varies | AEG 2022 Analysis; Depends on type
|  |  | ENERGY STAR Ice Machine | 10 | AEG 2023 Analysis
|  | Custom | Customized Retrofit | Custom | Not updated
|  |  | Anti-Sweat Heater Controls | 12 | Not updated
|  |  | Transformer | Custom13 | AEG 2018 Analysis
1 AEG 2018 Analysis:
a) Compared all of the EULs in the Hawai‘i Energy PY18 TRM's Master EUL list to DEER2020 EUL values.
b) Compared EULs for all applicable measures in the Hawai‘i Energy PY18 TRM's Master EUL list to EUL analysis conducted by AEG for the residential sector in Fall 2017 and for the commercial sector in Spring 2017. (The previous analysis was performed for two other utility clients, both on the mainland U.S.).
c) For all PY19 priority measures (except lamp replacement), conducted new EUL benchmarking analysis using AEG's DEEM tool (Database of Energy Efficiency Measures) and additional research of TRMs and best practices (see Resources listed below). The EULs for most lamp measures are based on the lamp life and hours of use of the lighting, which varies by building type.
d) For all priority measures, used the median or average value of sources reviewed in Step c as the new PY19 updated EUL. (The median was used in most cases, except for when the average value appeared most representative.)
e) For other non-priority measures for which there was an EUL in DEER2020, used the DEER2020 value as the new PY19 updated EUL.
2 DEER 2020: EUL was verified/updated to DEER 2020 value.
3 Depends on HOU: EUL depends on the rated lamp life and HOU for each specific building type.
4 AEG 2021 Analysis: Conducted EUL benchmarking for new and revised measures.
5 Not updated: EUL for measure was not updated because it was not listed in DEER2020 and/or was not a priority measure for update.
6 AEG 2025 Analysis: Conducted EUL benchmarking for revised air purifier and dehumidifier measures.
7 AEG 2023 Analysis: Conducted EUL benchmarking for revised kitchen measures.
8 No data found: This was a priority measure, but no EUL could be found during benchmarking.
9 AEG 2022 Analysis: Conducted EUL benchmarking for new and revised measures.
10 AEG 2024 Analysis: Conducted EUL benchmarking for new measures as they were introduced.
11 AEG 2026 Analysis: Conducted EUL benchmarking for new measures as they were introduced.
12 AEG 2020 Analysis: Conducted EUL benchmarking for new measures as they were introduced.
13 Default EUL is 30 years for distribution transformers. Documentation that the transformer is underloaded during average and peak operating conditions and is in good working order is required to justify EUL>30 years.
RESOURCES
• | AEG's 2018 Analysis File titled "AEG HPUC EUL Analysis."
• | AEG's 2020 Analysis Files titled "AEG HPUC - New Com Refrig Measures - Analysis File."
• | California Public Utilities Commission, Database of Energy Efficiency Resources, 2020 update, (DEER2020), READI v.2.5.0, Ex Ante Database Support Table Export, EUL_basis, created on 8/24/2018, available here: www.deeresources.com/index.php/homepage. Spreadsheet.
• | CEE High Efficiency Residential Swimming Pool Initiative, Consortium for Energy Efficiency, Boston, MA, January 2013, page 18. States life of 5-7 years for motor when used year-round per personal communication with Regal Beloit, Aug. 12.
• | Connecticut's 2018 Program Savings Document, 13th Edition, filed December 15, 2017. https://www.energizect.com/sites/default/files/2018-PSD-FINAL-121217.pdf.
• | ENERGY STAR, Pool Pump Calculator, last updated 2013, accessed Fall 2018, available here: https://www.energystar.gov/products/other/pool_pumps. Spreadsheet.
• | Hagerman, Joseph, Department of Energy Building Technologies Program, Presentation: "Circulator Pumps, Appliance Standards and Rulemaking", Federal Advisory Committee (ASRAC) Working Group, Fifth Meeting, July 12-13, 2016. EERE-2016-BT-STD-0004.
• | IESO Prescriptive Measures and Assumptions List. Independent Electricity System Operator. January 1, 2015. Document.
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0, Volume 3: Residential Measures, FINAL, Feb. 8, 2017.
• | Michigan Energy Measure Database, v. 2018, https://www.michigan.gov/mpsc/0,4639,7-159-52495_55129---,00.html, filename: "mi_master_measure_database_2018-112917_609672_7"
• | Mid-Atlantic Technical Reference Manual, Version 8, Final, May 2018.
• | Navigant Consulting, Inc. EIA Appendix A - Technology Forecast Updates - Residential and Commercial Building Technologies - 2011 Reference Case. U.S. Energy Information Administration, U.S. Department of Energy. September 22, 2011. Document.
• | Navigant Consulting, Inc. EIA Appendix A - Technology Forecast Updates - Residential and Commercial Building Technologies - Reference Case. U.S. Energy Information Administration, U.S. Department of Energy. March 2014. Document.
• | New Mexico Technical Resource Manual for the Calculation of Energy Efficiency Savings, 2016. Section 3.5. p.31. Cites DEER 2008 as source for EUL.
• | Northwest Power Conservation Council (NWPCC). Commercial VRF, Version 6 - Seventh Power Plan Conservation Supply Workbooks. February 25, 2016. Spreadsheet.
• | Northwest Power Conservation Council (NWPCC). Residential Refrigerator/Freezer, Version 4 - Seventh Power Plan Conservation Supply Workbooks. February 25, 2016. Spreadsheet.
• | Northwest Power Conservation Council (NWPCC). Residential Single Family Heat Pump, Version 5 - Seventh Power Plan Conservation Supply Workbooks. February 25, 2016. Spreadsheet.
• | Pool Pumps Summary - Calmac.org, www.calmac.org/publications/Pool_Pumps_RSW_II_6-15-2015_FINAL.xlsx. Spreadsheet.
• | Public Service Company of Colorado. 2017/2018 Demand-Side Management Plan. Colorado Public Utilities Commission. July 1, 2016. Document.
• | Regional Technical Forum. Air Source Heat Pump Upgrades SF - Unit Energy Savings Workbook, Version 4.2. Northwest Power and Conservation Council. December 05, 2017. Spreadsheet.
• | Regional Technical Forum. Commercial Grocery Display Case Lighting - Unit Energy Savings Workbook, Version 1.1. Northwest Power and Conservation Council. Oct. 1, 2018. Spreadsheet.
• | Regional Technical Forum. ComResCirculatorPumps_1_2.xlsm. Northwest Power and Conservation Council. Sep 26, 2017. Spreadsheet.
• | Regional Technical Forum. Efficient Pool Pumps - Unit Energy Savings Workbook, Version 2.1. Northwest Power and Conservation Council. February 27, 2018. Spreadsheet.
• | Regional Technical Forum. New Manufactured Homes and HVAC - Unit Energy Savings Workbook, Version 3.4. Northwest Power and Conservation Council. June 15, 2017. Spreadsheet.
• | Regional Technical Forum. ResFridgeFreezeDecommissioning_v5_1.xlsm. Northwest Power and Conservation Council. January 12, 2018. Spreadsheet. RULs are from 2018 analysis of detailed RUL data in DOE Technical Support Document, REFRIGERATORS, REFRIGERATOR-FREEZERS, AND FREEZERS, November 2009.
• | Regional Technical Forum. Residential Refrigerator and Freezers - Unit Energy Savings Workbook, Version 4.3. Northwest Power and Conservation Council. December 5, 2016. Spreadsheet.
• | Savings Calculator for ENERGY STAR Appliances, Available at: https://www.energystar.gov/sites/default/files/asset/document/appliance_calculator.xlsx. Accessed October 16, 2018.
• | Southern California Edison. Non-DEER Workpaper - Smart/Connected Refrigerator, SCE17AP009 Version 0. California Public Utilities Commission Database of Energy Efficiency Resources. March 17, 2017. Document.
• | Southern California Edison. Non-DEER Workpaper - VFD Retrofit to Central Plant Systems, SCE17HC039 Version 0. California Public Utilities Commission Database of Energy Efficiency Resources. January 01, 2017. Document.
• | State of Minnesota, Technical Reference Manual for Energy Conservation Improvement Programs, Version 2.2, May 2, 2018.
• | Tennessee Valley Authority Technical Reference Manual, Version 6.0, Oct. 1, 2017.
• | U.S. Energy Information Administration. Annual Energy Outlook 2018, National Energy Modeling System (NEMS) Input Files. U.S. Department of Energy. February 6, 2018. Spreadsheet.
• | U.S. Department of Energy, Energy Efficiency & Renewable Energy, Building Technologies Office, "Energy Savings Potential and Research & Development Opportunities for Commercial Refrigeration," September 2009.
• | Vermont Energy Investment Corporation. Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 5.0. Illinois Energy Efficiency Stakeholder Advisory Group. February 2016. Document.

## Savings Factors
SAVINGS FACTORS
Return to TOC
UPDATE STATUS
Updated in Fall 2018 for PY19 TRM.
Measure Interactive Effects
The TRM provides specific savings algorithms for many prescriptive measures. When a customer installs a prescriptive measure, the savings are determined according to these algorithms. In some cases these algorithms include the effects of interactions with other measures or end-uses.
For “custom” measures, Hawai‘i Energy performs site-specific customized calculations. In this case, Hawai‘i Energy takes into account interactions between measures (e.g., individual savings from installation of window film and replacement of a chiller are not additive because the first measure reduces the cooling load met by the second measure).
Hawai‘i Energy will calculate total savings for the package of custom measures being installed, considering interactive effects, either as a single package or in rank order of prescriptive and custom measures. That is, if a project includes both prescriptive and custom measures, the prescriptive measures will be calculated in the normal manner. However, the prescriptive measures will be assumed to be installed prior to determining the impacts for the custom measures.
Lighting/Cooling Interactive Effects Factors (IE)
The lighting/cooling interactive effects factors for demand (IEC,D) and energy (IEC,E) were updated for the PY19 TRM. Refer to the AEG analysis file titled "AEG HPUC Update of Com-Lighting Measures - Analysis file" for more information.
Table 1: Lighting/Cooling Load Interactive Effects Factors by Building Type, IEC,D and IEC,E
Building Type |  | Omni-Directional, Directional, and Decorative |  | High Bay, Linear, U-Bend, Troffer
|  | IEC,D | IEC,E | IEC,D | IEC,E
Misc./Avg. Commercial |  | 1.25 | 1.13 | 1.26 | 1.13
Cold Storage |  | 1.26 | 1.56 | 1.25 | 1.62
Education |  | 1.3 | 1.25 | 1.31 | 1.25
Grocery |  | 1.11 | 1.14 | 1.09 | 1.14
Health |  | 1.23 | 1.14 | 1.24 | 1.15
Hotel/Motel |  | 1.27 | 1.38 | 1.27 | 1.36
Industrial |  | 1.19 | 1.12 | 1.2 | 1.13
Office |  | 1.08 | 1.25 | 1.07 | 1.26
Restaurant |  | 1.22 | 1.28 | 1.24 | 1.28
Retail |  | 1.39 | 1.14 | 1.36 | 1.15
Warehouse |  | 1.15 | 1.01 | 1.16 | 1.01
Notes:
a. The IE values were derived using a four step process:
1) Tabulation of DEER's IE factors for San Diego (IECC CZ 3B);
2) Tabulation of IE factors from LBNL 1994 study for IECC CZ 3B and IECC CZ 1A;
3) Mapping of DEER and LBNL building types to Hawai‘i Energy's building types listed above;
4) Adjustment of the DEER IE factors for CZ 3B using ratio of LBNL factors for CZ 1A and CZ 3B to determine IE factors for Hawai‘i (CZ 1A). The equation is: IEHawaii = IEDEER, 3B*(IELBNL,1A/IELBNL,3B).
b. Assume no interactive effects for exit signs due to lack of representative data.
Persistence Factor (PF)
Persistence factors may be used to reduce lifetime measure savings in recognition that initial engineering estimates of annual savings may not persist long term due to changed operating hours, changed process operations, and/or the performance degradation of equipment efficiency relative to the baseline efficiency option.
Many of the measure algorithms contain an entry for persistence factor. The default value if none is indicated is 1.00 (100%). A value lower than 1.00 will result in a downward adjustment of the first year savings, lifetime savings, and total resource benefits.

## EFLH & CF
EQUIPMENT OPERATING HOURS AND COINCIDENCE FACTORS
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. Equivalent full load hours and coincidence factors, by building type, were added for commercial building fans and dedicated outdoor air systems.
General Commercial Lighting Hours of Use (HOU) & Coincidence Factor (CF)
The lighting hours of use and coincidence factors were updated for the PY19 TRM. Refer to these AEG analysis files for more information: "AEG HPUC Update of Com-Lighting Measures - Analysis file" and "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays."
Table 1a. General Commercial Lighting: Annual Hours of Use
Building Type |  | Exit Sign |  | Omni-Directional, Directional, and Decorative | High Bay | Linear, U-Tube, Troffer
Misc./Avg. Commercial |  | 8760 |  | 1831 | 3047 | 1963
Cold Storage |  | 8760 |  | 4710 | 4820 | 4700
Education |  | 8760 |  | 1498 | 2176 | 1702
Grocery |  | 8760 |  | 4900 | 5450 | 4770
Health |  | 8760 |  | 5370 | 5870 | 5100
Hotel/Motel |  | 8760 |  | 1284 | 4775 | 1130
Industrial |  | 8760 |  | 2145 | 2860 | 2305
Office |  | 8760 |  | 1780 | 2480 | 1980
Restaurant |  | 8760 |  | 3700 | 3610 | 3500
Retail |  | 8760 |  | 2363 | 3983 | 3690
Warehouse |  | 8760 |  | 1690 | 2245 | 1970
Source: DEER2020 hours of use for San Diego IOU; no occupancy sensor. HOU were originally developed for DEER2016.
Table 1b. General Commercial Lighting: Coincidence Factors
Building Type |  | Exit Sign |  | Omni-Directional, Directional, and Decorative | High Bay | Linear, U-Bend, Troffer
Misc./Avg. Commercial |  | 1 |  | 0.31 | 0.53 | 0.34
Cold Storage |  | 1 |  | 0.2 | 0.2 | 0.2
Education |  | 1 |  | 0.28 | 0.4 | 0.32
Grocery |  | 1 |  | 0.7 | 0.78 | 0.68
Health |  | 1 |  | 0.66 | 0.72 | 0.63
Hotel/Motel |  | 1 |  | 0.26 | 0.96 | 0.23
Industrial |  | 1 |  | 0.53 | 0.58 | 0.59
Office |  | 1 |  | 0.22 | 0.31 | 0.25
Restaurant |  | 1 |  | 0.52 | 0.5 | 0.49
Retail |  | 1 |  | 0.32 | 0.54 | 0.5
Warehouse |  | 1 |  | 0.07 | 0.1 | 0.08
Notes:
a. The CF values were derived using a three step process:
1) AEG analysis of DOE's OpenEI general lighting load shapes simulated with Hawai‘i-specific prototypes, weather data, and peak demand period to determine i) unadjusted CF values for general lighting during Hawai‘i's peak demand period of 5-9 pm on non-holiday weekdays, and ii) unadjusted EFLH values for general lighting (= annual lighting energy use in kWh divided by maximum lighting demand in kW).
2) Mapping of OpenEI's and DEER's building types to Hawai‘i Energy's building types listed above;
3) Adjustment of the OpenEI CF values to specific lighting types (bulbs, highbay, linear lamps) using DEER's annual HOUs for San Diego. The adjustment equation is CFOpenEI*(HOUSD/EFLHOpenEI).
b. San Diego is a good proxy for Hawai‘i for lighting usage. The OpenEI prototypes yield the same energy, demand, EFLH, and CF factors for San Diego, Honolulu, Kahului, and Keahole-Kona weather stations. (Therefore, the same results are applicable to all Hawaiian counties.)
General Commercial Cooling Equivalent Full Load Hours (EFLH) and Coincident Factor (CF)
The general cooling equivalent full load hours and coincidence factors were updated for the PY19 TRM. Refer to these AEG analysis files for more information: "AEG HPUC Update of Commercial Chillers - Analysis File" and "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays."
Table 2. General Commercial Cooling: Equivalent Full Load Hours & Coincidence Factors
Building Type |  | EFLH | CF
Misc./Avg. Commercial |  | 2594 | 0.38
Cold Storage |  | Varies | Varies
Education |  | 2549 | 0.43
Grocery |  | 1531 | 0.27
Health |  | 4891 | 0.55
Hotel/Motel |  | 4910 | 0.6
Industrial |  | Varies | Varies
Office |  | 2754 | 0.48
Restaurant |  | 2451 | 0.4
Retail |  | 1913 | 0.29
Warehouse |  | 1033 | 0.01
Use custom approach for entries noted as "Varies."
Source: AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period.
Commercial Water Heating Equivalent Full Load Hours (EFLH) and Coincident Factor (CF)
The commercial water heating equivalent full load hours and coincidence factors were updated for the PY19 TRM. Refer to these AEG analysis files for more information: "AEG HPUC Update of Com-Solar Water Heater - Analysis file" and "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays."
Table 4. General Commercial Water Heating: Equivalent Full Load Hours & Coincidence Factors
Building Type |  | EFLH | CF
Misc./Avg. Commercial |  | 2322 | 0.29
Cold Storage |  | Varies | Varies
Education |  | 1916 | 0.25
Grocery |  | 4406 | 0.6
Health |  | 2247 | 0.2
Hotel/Motel |  | 3008 | 0.35
Industrial |  | Varies | Varies
Office |  | 2632 | 0.3
Restaurant |  | 3947 | 0.74
Retail |  | Varies | Varies
Warehouse |  | Varies | Varies
Use custom approach for entries noted as "Varies."
Source: AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period.
Commercial Fans Equivalent Full Load Hours (EFLH) and Coincident Factor (CF)
The equivalent full load hours and coincidence factors for commercial building fans were added for the PY26 TRM. Refer to these analysis files for more information: "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays" and "PY26 TRM - DX-DOAS - Analysis File."
Table 5. General Commercial Fans: Equivalent Full Load Hours & Coincidence Factors
Building Type |  | EFLH | CF
Misc./Avg. Commercial |  | 5384 | 0.7
Cold Storage |  | 3436 | 0.01
Education |  | 2639 | 0.46
Grocery |  | 5840 | 1
Health |  | 5849 | 0.67
Hotel/Motel |  | 7837 | 0.94
Industrial |  | Varies | Varies
Office |  | 3675 | 0.63
Restaurant |  | 7300 | 1
Retail |  | 5278 | 0.86
Warehouse |  | 3436 | 0.01
Use custom approach for entries noted as "Varies."
Source: AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period.
Direct Expansion-Dedicated Outdoor Air System (DX-DOAS) Equivalent Full Load Hours (EFLH) and Coincident Factor (CF)
The equivalent full load hours and coincidence factors for commercial building direct expansion-dedicated outdoor air systems (DX-DOAS) were added for the PY26 TRM. Refer to this analysis file for more information: "PY26 TRM - DX-DOAS - Analysis File."
Table 6. DX-DOAS: Equivalent Full Load Hours & Coincidence Factors
Building Type |  | EFLH | CF
Misc./Avg. Commercial |  | 5668 | 0.8
Cold Storage |  | NA | NA
Education |  | 2639 | 0.46
Grocery |  | 5840 | 1
Health |  | 5849 | 0.67
Hotel/Motel |  | 7837 | 0.94
Industrial |  | NA | NA
Office |  | 3675 | 0.63
Restaurant |  | 7300 | 1
Retail |  | 5278 | 0.86
Warehouse |  | NA | NA
Source: AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period. The analysis was conducted using the commercial building fan end-use. ICF did not include the Cold Storage, Industrial, or Warehouse building types on this list because the DX-DOAS measure is unlikely to apply to those building types. Therefore, the EFLH and CF values for the "Misc./Avg. Commercial" building type in this DX-DOAS table differ from those in the General Commercial Fans table above (see Table 5) because they were calculated using the subset of building types applicable to the DX-DOAS measure.

## Custom
Custom Measures
Return to TOC
UPDATE STATUS
Updated in Summer 2025 for the PY25 TRM V1. The update consisted of revising the language for custom chiller projects.
OVERVIEW
In addition to prescriptive energy conservation measures that are defined within this Technical Reference Manual, there are projects that are handled on a case-by-case basis through our custom incentive program. Custom projects may be complex projects with multiple components, first-of-their-kind projects, or special projects that are unique to a particular customer. A few examples of custom incentive projects from past years include:
• | A new packaging machine for a water bottling facility.
• | A condominium submetering installation with submetering on electrical consumption as well as chilled water usage at the individual condo level.
• | A whole-building retro-commissioning project with “pre” and “post” metering.
In PY17, Hawai‘i Energy moved some formerly prescriptive projects to the custom category, mainly for the reason that these projects occur infrequently. These include Residential New Construction and Heat Pump Water Heater-to-Heat Pump Water Heater upgrades. Below is a list and description of a selection of custom measures. Due to the nature of our custom program, this list is not intended to be comprehensive.
CUSTOM PROJECT GUIDANCE DOCUMENT
A Custom Project Guidance Document was created through a collaboration involving Hawai‘i Energy, the EM&V Contractor, the EEM, and the HPUC. It is effective as of July 1, 2022. The purpose of the Custom Project Guidance Document is to define the types of projects applicable for a custom savings estimation path, to describe eligibility requirements and program rules for custom projects, and to provide guidance on custom project documentation and energy savings estimation approaches. The focus is on EM&V-related considerations. This type of guidance is useful to ensure that custom projects are consistently and thoroughly described and analyzed during program implementation, which in turn facilitates an effective assessment of energy and demand savings during the annual EM&V process.
Citation: Hawai'i Energy Custom Project Guidance: EM&V-Related Considerations, Version 1.0, Effective July 1, 2022.
EXAMPLES OF CUSTOM MEASURES
Residential New Construction
Hawai‘i Energy has moved the Residential New Construction incentive from previous TRM versions to a custom incentive due to the complex and unique nature of these projects. Residential homes vary in size, orientation, construction, and equipment and therefore require a customized approach when estimating energy savings. Residential New Construction projects may include a subset of prescriptive measures, such as ENERGY STAR appliances, which may still be rebated on a prescriptive basis.
Chillers
As a guideline, any chiller retrofit that is part of a larger, multi-system plant should be evaluated as a custom project. Projects that are part of a larger project with a variety of efficiency measures being installed simultaneously, or other unique projects, would be a candidate for custom evaluation, at the discretion of Hawai‘i Energy. This requirement was set for the following reasons:
• | Larger chiller projects are usually quite complex, and may involve other system changes, such as controls upgrades, pump modifications, VFD upgrades and more. Calculating savings on a prescriptive or even semi-prescriptive basis of tonnage and nameplate efficiency only would be inadequate in most cases for larger chiller projects.
• | Hawai‘i Energy acknowledges that performing true custom savings calculations is more time, cost, and labor-intensive, due to the additional requirements for pre and post metering. These barriers may actually inhibit the feasibility of a project to move forward, and therefore Hawai‘i Energy would limit the number of custom projects per year.
Ductless Systems
As a guideline, commercial VRF retrofits for systems with capacities greater than 240,000 Btu/h should be evaluated as custom projects. Projects that are part of a larger project with a variety of efficiency measures being installed simultaneously, or other unique projects, would be a candidate for custom evaluation, at the discretion of Hawai‘i Energy. This threshold was chosen based on capacity break points in ASHRAE and IECC code for air-cooled AC and heat pump efficiencies; evaluating a VRF system on a prescriptive or even semi-prescriptive basis would be inadequate for most larger projects at this capacity.
VFDs
As a guideline, Hawai‘i Energy has established an upper threshold of 200 horsepower for prescriptive rebates on variable frequency drives. This value was chosen after a literature review. The NEEP VSD Load shape Project (2014) determined a savings metric for prescriptive energy and demand savings for VSDs on various applications for motors up to 200 hp. In addition, the NREL Chapter 18 VFD Evaluation Protocol (2017) recommended this method for prescriptive evaluation. The NREL Chapter stated that a customized evaluation “is more common for facilities that are applying incentives for a variety of measures in a building.” VFD projects that are part of a larger project with a variety of efficiency measures being installed simultaneously would be a candidate for Custom evaluation, at the discretion of Hawai‘i Energy.
Distribution Transformers
As a guideline, the following distribution transformer projects should be evaluated as custom projects:
• | Replacement of transformers that are 1000 kVA and above.
• | Replacement of transformers installed after 2007 (on a case-by-case basis).
• | Analysis of savings under loaded conditions.
• | Projects where the new transformer will serve a load that is >10% higher than the load served by the pre-existing transformer.
Advanced Residential Intelligent Efficiency Services (ARIES)
ARIES is an opt-in deployment of emerging technology and program services designed to provide significant enhancements over historical approaches with improved:
• | Savings impact, measurement methods, and understanding of savings sources
• | Customer interest, engagement, satisfaction, trust and overall value
• | Cost structure and future curve for long term persistence and cost-effectiveness
The source of savings can be considered as coming from the following 4 categories of home energy impact areas, in rough order of estimated impact and cost/complexity:
• | “Always On” – We estimate the average “baseline” power draw in homes to be ~250 Watts, whereas many homes have far lower continuous draws of 100W or less. Eliminating 50 Watts of always on would amount to 6% household savings. ARIES will prioritize engaging customers to target this opportunity through gamified feedback.
• | “Adjustments & Maintenance” – Changing setting and schedules, or habits associated with devices like electronics and appliances. The savings potential in this category is higher for large electric uses like heat pumps, water and space heaters, etc. Depending upon customer context, could represent additional 5% savings or more. ARIES will assess customer-specific savings potential and act accordingly with informational interventions.
• | “Eliminate” – Many households accumulate energy-using products or equipment over time that they may not need. ARIES will help enhance customers’ visibility and awareness of vestigial device usage and encourage them to consider whether customers have an opportunities to reduce their energy clutter.
• | “Upgrade” – Akin to conventional program activity, ARIES customers might replace existing devices with new ones that have a different energy impact. Out of program equipment changes can be tracked to better understand savings lifetimes, and in-program actions allow for double-counting adjustments.
The nature and high quality of energy information and customer insights developed by ARIES affords a significant opportunity to advance other opportunities that may serve other energy system stakeholders to support public interest.

## C_Appliance_Refrigerator
COMMERCIAL: Residential-Style Refrigerator and Freezer
Return to TOC
UPDATE STATUS
Updated in Winter 2021-2022 for PY22 TRM. This measure essentially duplicates the R_Appliance_Refrigerator measure which was updated in Winter 2019-2020 for PY20 TRM.
MEASURE DETAILS
Description
This measure pertains to the installation of a new residential-style ENERGY STAR v5.0 certified refrigerator/freezer (as specified below) in a commercial building and/or recycling of the pre-existing refrigerator/freezer in the commercial building.
Program Criteria
ENERGY STAR v5.0 certified. This measure is only applicable to residential-style refrigerators/freezers in commercial buildings. It is not applicable to commercial refrigerators/freezers. Refer to the C_Kitchen_Refrigerator and C_Kitchen_Freezer measures for commercial refrigerators/freezers.
Unit of Measure
One refrigerator/freezer.
Baseline Equipment
The base case for the new unit is the current federal requirement (National Appliance Energy Conservation Act, or NAECA, 2011) for a refrigerator/freezer, effective as of September 15, 2014. The base case for a turned-in unit is the pre-existing refrigerator/freezer.
High Efficiency Equipment
The efficient case for the new unit is an ENERGY STAR v5.0 qualified refrigerator/freezer, which has an efficiency criteria of 10 percent less energy use than minimum federal requirements.
Note: ENERGY STAR v5.1 was finalized Aug 5, 2021. The change between v5.0 and v5.1 just expanded the scope to include coolers (e.g., wine coolers and beverage centers). The v5.0 to v5.1 amendment did not affect other currently certified products, like the refrigerators and freezers included in this measure.
ALGORITHMS
The base case (minimum federal requirement) and efficient case (ENERGY STAR) for a new refrigerator/freezer are based on the adjusted volume (AV) in cubic feet of the unit. The adjusted volume is calculated as follows (see Equations 1 and 2):
Refrigerator Adjusted Volume (AV), cu ft
(1)
Freezer Adjusted Volume (AV), cu ft
(2)
Unit Replacement Annual Energy Savings, kWh/yr
(3)
Unit Replacement Peak Demand Reduction, kW
(4)
Unit Replacement Lifetime Energy Savings, kWh
(5)
Unit Replacement with Turn-In Annual Energy Savings, kWh/yr
(6)
Unit Replacement with Turn-In Peak Demand Reduction, kW
(7)
Unit Replacement with Turn-In Lifetime Energy Savings, kWh
(8)
2nd Unit Turn-In Only Annual Energy Savings, kWh/yr
(9)
2nd Unit Turn-In Only Peak Demand Reduction, kW
(10)
2nd Unit Turn-In Only Lifetime Energy Savings, kWh
(11)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description |  |  |  | Value |  |  | Unit |  | Source/Notes
AVR |  |  |  | Adjusted volume of refrigerator1 |  |  |  | Default = 25.4 |  |  | cu ft |  | See Footnote 2 for Default assumption
AVF |  |  |  | Adjusted volume of freezer1 |  |  |  | Default = 26.0 |  |  | cu ft |  | See Footnote 3 for Default assumption
Fresh volume |  |  |  | Fresh volume of new refrigerator |  |  |  | User entry |  |  | cu ft |  | Based on actual unit; used to calculate AV in Equation 1
Freezer volume |  |  |  | Freezer volume of new refrigerator or freezer |  |  |  | User entry |  |  | cu ft |  | Based on actual unit; used to calculate AV in Equations 1 and 2
EBase |  |  |  | Annual energy usage of baseline unit |  |  |  | See Tables 1 and 2 |  |  | kWh |  | Federal requirements as of September 15, 2014
EEE |  |  |  | Annual energy usage of new efficient unit |  |  |  | See Tables 1 and 2 |  |  | kWh |  | ENERGY STAR as of September 15, 2014
ETurn-in |  |  |  | Annual energy usage of turned-in refrigerator |  |  |  | 758 |  |  | kWh |  | ENERGY STAR "Flip Your Fridge Calculator" 4
|  |  |  | Annual energy usage of turned-in freezer |  |  |  | 574 |  |  | kWh |  | ENERGY STAR "Flip Your Fridge Calculator" 4
PF |  |  |  | Persistence factor |  |  |  | 1 |  |  | - |  | See Footnote 5
HRS |  |  |  | Annual operating hours |  |  |  | 8760 |  |  | hrs |  | Conservative assumption when used to estimate peak demand savings
CF |  |  |  | Coincidence factor |  |  |  | 1 |  |  | - |  | Acceptable if used along with 8760 hours
EULReplace,R |  |  |  | Effective useful life of new refrigerator |  |  |  | 14 |  |  | yrs |  | AEG's Fall 2018 Benchmarking 6
EULReplace,F |  |  |  | Effective useful life of new freezer |  |  |  | 17 |  |  | yrs |  | AEG's Fall 2018 Benchmarking
RULTurn-In,R |  |  |  | Remaining useful life of turned-in refrigerator |  |  |  | 8 |  |  | yrs |  | AEG's Fall 2018 Benchmarking
RULTurn-In,F |  |  |  | Remaining useful life of turned-in freezer |  |  |  | 7 |  |  | yrs |  | AEG's Fall 2018 Benchmarking
1 Source of AV equations is ENERGY STAR, Savings Calculator for ENERGY STAR Appliances, available at: https://www.energystar.gov/sites/default/files/asset/document/appliance_calculator.xlsx, accessed December 15, 2018.
2 Based on average of default values for Total Model Volume for refrigerators from ENERGY STAR calculator (20.5 cu ft), and assuming 68.6% of volume is refrigerator (fresh volume), which is default in ENERGY STAR calculator. Recommendation for future update: Determine average AV of units installed through Hawai‘i program.
3 Based on average of default values for Total Model Volume for freezers (non-compact ) from ENERGY STAR calculator (15.0 cu ft). Recommendation for future update: Determine average AV of units installed through Hawai‘i program.
4 Source: ENERGY STAR "Flip Your Fridge" calculator, <https://www.energystar.gov/index.cfm?fuseaction=refrig.calculator>, accessed on January 21, 2020. Average of five refrigerator types (top, bottom, side, French, 4-door); capacity: 19.0-21.4 cu ft; model year: 2001-2010. Average of two freezer types (upright, chest); capacity: < 16.5 cu ft; model year: 2001-2010. Recommend updating with Hawai‘i-specific data on the types/ages of units turned-in through the program in future TRM update.
5 Use value of PF=1 until more data is available on savings persistence of ENERGY STAR units relative to baseline units.
6 See analysis file titled "AEG HPUC EUL Analysis."
Table 1. Base and Efficient Case Refrigerator Standards, Total Volume ≥ 7.75 cu ft and < 39 cu ft, Equation: E = a*AV + b
Product Category | [7 empty] | Ebase, Federal Standard, Maximum kWh/yr 1 | [5 empty] | EEE, ENERGY STAR, Maximum kWh/yr 2
Equation Term: | [7 empty] | a |  |  | b |  |  | a |  | b
Manual Defrost w/ and w/o TDD, All Configurations | [7 empty] | 6.79 |  |  | 193.6 |  |  | 6.11 |  | 174.2
Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [7 empty] | 8.07 |  |  | 233.7 |  |  | 7.26 |  | 210.3
Auto Defrost w/o TDD, Side by Side | [7 empty] | 8.51 |  |  | 297.8 |  |  | 7.66 |  | 268
Auto Defrost w/o TDD, Bottom Freezer | [7 empty] | 8.85 |  |  | 317 |  |  | 7.97 |  | 285.3
Auto Defrost w/ TDD, Bottom Freezer | [7 empty] | 9.25 |  |  | 475.4 |  |  | 8.33 |  | 436.3
Auto Defrost w/ TDD, Top Freezer | [7 empty] | 8.4 |  |  | 385.4 |  |  | 7.56 |  | 355.3
Auto Defrost w/ TDD, Side by Side | [7 empty] | 8.54 |  |  | 432.8 |  |  | 7.69 |  | 397.9
"Average" Refrigerator 3 | [7 empty] | 8.3443 |  |  | 333.6714 |  |  | 7.5114 |  | 303.9
1 Electronic Code of Federal Regulations, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates. (a) Refrigerators/refrigerator-freezers/freezers, current as of December 13, 2018, accessed December 17, 2018.
2 ENERGY STAR Program Requirements for Residential Refrigerators and Freezers. Eligibility Criteria, V5.0, https://www.energystar.gov/ia/partners/product_specs/program_reqs/Refrigerators_and_Freezers_Program_Requirements_V5.0.pdf, accessed December 17, 2018.
3 Recommend updating with weighted average by type using program data or baseline data in future TRM update.
Table 2. Base and Efficient Case Freezer Standards, Total Volume ≥ 7.75 cu ft and < 39 cu ft, Equation: E = a*AV + b
Product Category | [7 empty] | Ebase, Federal Standard, Maximum kWh/yr 1 | [5 empty] | EEE, ENERGY STAR, Maximum kWh/yr 2
Equation Term: | [7 empty] | a |  |  | b |  |  | a |  | b
Upright Freezers, Manual Defrost | [7 empty] | 5.57 |  |  | 193.7 |  |  | 5.01 |  | 174.3
Upright Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 8.62 |  |  | 228.3 |  |  | 7.76 |  | 205.5
Upright Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 8.62 |  |  | 312.3 |  |  | 7.76 |  | 289.5
Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 9.86 |  |  | 260.9 |  |  | 8.87 |  | 234.8
Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 9.86 |  |  | 344.9 |  |  | 8.87 |  | 318.8
Chest Freezers and All Other Freezers, except Compact Freezers | [7 empty] | 7.29 |  |  | 107.8 |  |  | 6.56 |  | 97
Chest Freezers with Auto Defrost | [7 empty] | 10.24 |  |  | 148.1 |  |  | 9.22 |  | 133.3
"Average" Freezer 3 | [7 empty] | 8.58 |  |  | 228 |  |  | 7.7214 |  | 207.6
1 Electronic Code of Federal Regulations, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates. (a) Refrigerators/refrigerator-freezers/freezers, current as of December 13, 2018, accessed December 17, 2018.
2 ENERGY STAR Program Requirements for Residential Refrigerators and Freezers. Eligibility Criteria, V5.0, https://www.energystar.gov/ia/partners/product_specs/program_reqs/Refrigerators_and_Freezers_Program_Requirements_V5.0.pdf, accessed December 17, 2018.
3 Recommend updating with weighted average by type using program data or baseline data in future TRM update.
SAVINGS - DEEMED
Deemed Savings (based on default value for Adjusted Volume, AV): Refrigerator w/o Turn-In
| Refrigerator w/o Turn-In, AV = 25.4 cu ft Product Category | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Manual Defrost w/ and w/o TDD, All Configurations | [7 empty] | 0.004 |  |  |  | 36.67 |  | 513.38
| Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [7 empty] | 0.005 |  |  |  | 43.97 |  | 615.58
| Auto Defrost w/o TDD, Side by Side | [7 empty] | 0.006 |  |  |  | 51.39 |  | 719.46
| Auto Defrost w/o TDD, Bottom Freezer | [7 empty] | 0.006 |  |  |  | 54.05 |  | 756.7
| Auto Defrost w/ TDD, Bottom Freezer | [7 empty] | 0.007 |  |  |  | 62.47 |  | 874.58
| Auto Defrost w/ TDD, Top Freezer | [7 empty] | 0.006 |  |  |  | 51.44 |  | 720.16
| Auto Defrost w/ TDD, Side by Side | [7 empty] | 0.006 |  |  |  | 56.49 |  | 790.86
| "Average" Refrigerator | [7 empty] | 0.006 |  |  |  | 50.93 |  | 713.02
Deemed Savings (based on default value for Adjusted Volume, AV): Freezer w/o Turn-In
| Freezer w/o Turn-In, AV = 26.0 cu ft Product Category | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Upright Freezers, Manual Defrost | [7 empty] | 0.004 |  |  |  | 33.96 |  | 577.32
| Upright Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 0.005 |  |  |  | 45.16 |  | 767.72
| Upright Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 0.005 |  |  |  | 45.16 |  | 767.72
| Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 0.006 |  |  |  | 51.84 |  | 881.28
| Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 0.006 |  |  |  | 51.84 |  | 881.28
| Chest Freezers and All Other Freezers, except Compact Freezers | [7 empty] | 0.003 |  |  |  | 29.78 |  | 506.26
| Chest Freezers with Auto Defrost | [7 empty] | 0.005 |  |  |  | 41.32 |  | 702.44
| "Average" Freezer | [7 empty] | 0.005 |  |  |  | 42.72 |  | 726.24
Deemed Savings (based on default value for Adjusted Volume, AV): Refrigerator w/ Turn-In
NOTE: Lifetime Energy Savings and Total Resource Benefits (TRBs) must be calculated using a combination of two baseline periods: 1) new refrigerator (EUL = 14 yr) and 2) turned-in refrigerator (RUL = 8 yr).
| Refrigerator w/ Turn-In, AV = 25.4 cu ft Product Category | [5 empty] | Peak Demand Savings, kW |  |  |  |  | Annual Energy Savings, kWh/yr |  |  | Lifetime Energy Savings
[7 empty] | 1st BL: New + Turn-in 1 |  |  | 2nd BL: New Only 2 |  | 1st BL: New + Turn-in 1 |  | 2nd BL: New Only 2
| Manual Defrost w/ and w/o TDD, All Configurations | [5 empty] | 0.091 |  |  | 0.004 |  | 794.67 |  | 36.67 | 6577.38
| Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [5 empty] | 0.092 |  |  | 0.005 |  | 801.97 |  | 43.97 | 6679.58
| Auto Defrost w/o TDD, Side by Side | [5 empty] | 0.092 |  |  | 0.006 |  | 809.39 |  | 51.39 | 6783.46
| Auto Defrost w/o TDD, Bottom Freezer | [5 empty] | 0.093 |  |  | 0.006 |  | 812.05 |  | 54.05 | 6820.7
| Auto Defrost w/ TDD, Bottom Freezer | [5 empty] | 0.094 |  |  | 0.007 |  | 820.47 |  | 62.47 | 6938.58
| Auto Defrost w/ TDD, Top Freezer | [5 empty] | 0.092 |  |  | 0.006 |  | 809.44 |  | 51.44 | 6784.16
| Auto Defrost w/ TDD, Side by Side | [5 empty] | 0.093 |  |  | 0.006 |  | 814.49 |  | 56.49 | 6854.86
| "Average" Refrigerator | [5 empty] | 0.092 |  |  | 0.006 |  | 808.93 |  | 50.93 | 6777.02
1 Use for Years 1 through 8 in TRB calculation.
2 Use for Years 9 through 14 in TRB calculation.
Deemed Savings (based on default value for Adjusted Volume, AV): Freezer w/ Turn-In
NOTE: Lifetime Energy Savings and Total Resource Benefits (TRBs) must be calculated using a combination of two baseline periods: 1) new freezer (EUL = 17 yr) and 2) turned-in freezer (RUL = 7 yr).
| Freezer w/ Turn-In, AV = 26.0 cu ft Product Category | [5 empty] | Peak Demand Savings, kW |  |  |  |  | Annual Energy Savings, kWh/yr |  |  | Lifetime Energy Savings
[7 empty] | 1st BL: New + Turn-in 1 |  |  | 2nd BL: New Only 2 |  | 1st BL: New + Turn-in 1 |  | 2nd BL: New Only 2
| Upright Freezers, Manual Defrost | [5 empty] | 0.069 |  |  | 0.004 |  | 607.96 |  | 33.96 | 4595.32
| Upright Freezers, Auto Defrost, w/o Auto Icemaker | [5 empty] | 0.071 |  |  | 0.005 |  | 619.16 |  | 45.16 | 4785.72
| Upright Freezers, Auto Defrost, w/ Auto Icemaker | [5 empty] | 0.071 |  |  | 0.005 |  | 619.16 |  | 45.16 | 4785.72
| Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [5 empty] | 0.071 |  |  | 0.006 |  | 625.84 |  | 51.84 | 4899.28
| Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [5 empty] | 0.071 |  |  | 0.006 |  | 625.84 |  | 51.84 | 4899.28
| Chest Freezers and All Other Freezers, except Compact Freezers | [5 empty] | 0.069 |  |  | 0.003 |  | 603.78 |  | 29.78 | 4524.26
| Chest Freezers with Auto Defrost | [5 empty] | 0.07 |  |  | 0.005 |  | 615.32 |  | 41.32 | 4720.44
| "Average" Freezer | [5 empty] | 0.07 |  |  | 0.005 |  | 616.72 |  | 42.72 | 4744.24
1 Use for Years 1 through 7 in TRB calculation.
2 Use for Years 8 through 17 in TRB calculation.
Deemed Savings: Refrigerator or Freezer Turn-In Only
| Measure Name | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Refrigerator Turn-In Only, AV = 25.4 cu ft Product Category | [7 empty] | 0.087 |  |  |  | 758 |  | 6064
| Freezer Turn-In Only, AV = 26.0 cu ft Product Category | [7 empty] | 0.066 |  |  |  | 574 |  | 4018
SAVINGS - SEMI-PRESCRIPTIVE CALCULATOR
| Refrigerator | [6 empty] | Freezer
| Enter Fresh Volume |  |  |  |  | 22 |  | Enter Frozen Volume | [5 empty] | 12
| Enter Frozen Volume |  |  |  |  | 8
|  | AVR = | 36.1 |  | per Equation 1 |  |  |  | AVF = | 20.8 |  |  | per Equation 2
Semi-Prescriptive Savings (based on user entry): Refrigerator w/o Turn-In
| Refrigerator w/o Turn-In Product Category | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Manual Defrost w/ and w/o TDD, All Configurations | [7 empty] | 0.005 |  |  |  | 43.95 |  | 615.3
| Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [7 empty] | 0.006 |  |  |  | 52.64 |  | 736.96
| Auto Defrost w/o TDD, Side by Side | [7 empty] | 0.007 |  |  |  | 60.48 |  | 846.72
| Auto Defrost w/o TDD, Bottom Freezer | [7 empty] | 0.007 |  |  |  | 63.47 |  | 888.58
| Auto Defrost w/ TDD, Bottom Freezer | [7 empty] | 0.008 |  |  |  | 72.31 |  | 1012.34
| Auto Defrost w/ TDD, Top Freezer | [7 empty] | 0.007 |  |  |  | 60.42 |  | 845.88
| Auto Defrost w/ TDD, Side by Side | [7 empty] | 0.007 |  |  |  | 65.59 |  | 918.26
| "Average" Refrigerator | [7 empty] | 0.007 |  |  |  | 59.84 |  | 837.76
Semi-Prescriptive Savings (based on user entry): Freezer w/o Turn-In
| Freezer w/o Turn-In Product Category | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Upright Freezers, Manual Defrost | [7 empty] | 0.004 |  |  |  | 31.05 |  | 527.85
| Upright Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 0.005 |  |  |  | 40.69 |  | 691.73
| Upright Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 0.005 |  |  |  | 40.69 |  | 691.73
| Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 0.005 |  |  |  | 46.69 |  | 793.73
| Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 0.005 |  |  |  | 46.69 |  | 793.73
| Chest Freezers and All Other Freezers, except Compact Freezers | [7 empty] | 0.003 |  |  |  | 25.98 |  | 441.66
| Chest Freezers with Auto Defrost | [7 empty] | 0.004 |  |  |  | 36.02 |  | 612.34
| "Average" Freezer | [7 empty] | 0.004 |  |  |  | 38.26 |  | 650.42
Semi-Prescriptive Savings (based on user entry): Refrigerator w/ Turn-In
NOTE: Lifetime Energy Savings and Total Resource Benefits (TRBs) must be calculated using a combination of two baseline periods: 1) new refrigerator (EUL = 14 yr) and 2) turned-in refrigerator (RUL = 8 yr).
| Refrigerator w/ Turn-In Product Category | [5 empty] | Peak Demand Savings, kW |  |  |  |  | Annual Energy Savings, kWh/yr |  |  | Lifetime Energy Savings
[7 empty] | 1st BL: New + Turn-in 1 |  |  | 2nd BL: New Only 2 |  | 1st BL: New + Turn-in 1 |  | 2nd BL: New Only 2
| Manual Defrost w/ and w/o TDD, All Configurations | [5 empty] | 0.092 |  |  | 0.005 |  | 801.95 |  | 43.95 | 6679.3
| Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [5 empty] | 0.093 |  |  | 0.006 |  | 810.64 |  | 52.64 | 6800.96
| Auto Defrost w/o TDD, Side by Side | [5 empty] | 0.093 |  |  | 0.007 |  | 818.48 |  | 60.48 | 6910.72
| Auto Defrost w/o TDD, Bottom Freezer | [5 empty] | 0.094 |  |  | 0.007 |  | 821.47 |  | 63.47 | 6952.58
| Auto Defrost w/ TDD, Bottom Freezer | [5 empty] | 0.095 |  |  | 0.008 |  | 830.31 |  | 72.31 | 7076.34
| Auto Defrost w/ TDD, Top Freezer | [5 empty] | 0.093 |  |  | 0.007 |  | 818.42 |  | 60.42 | 6909.88
| Auto Defrost w/ TDD, Side by Side | [5 empty] | 0.094 |  |  | 0.007 |  | 823.59 |  | 65.59 | 6982.26
| "Average" Refrigerator | [5 empty] | 0.093 |  |  | 0.007 |  | 817.84 |  | 59.84 | 6901.76
1 Use for Years 1 through 8 in TRB calculation.
2 Use for Years 9 through 14 in TRB calculation.
Semi-Prescriptive Savings (based on user entry): Freezer w/ Turn-In
NOTE: Lifetime Energy Savings and Total Resource Benefits (TRBs) must be calculated using a combination of two baseline periods: 1) new freezer (EUL = 17 yr) and 2) turned-in freezer (RUL = 7 yr).
| Freezer w/ Turn-In Product Category | [5 empty] | Peak Demand Savings, kW |  |  |  |  | Annual Energy Savings, kWh/yr |  |  | Lifetime Energy Savings
[7 empty] | 1st BL: New + Turn-in 1 |  |  | 2nd BL: New Only 2 |  | 1st BL: New + Turn-in 1 |  | 2nd BL: New Only 2
| Upright Freezers, Manual Defrost | [5 empty] | 0.069 |  |  | 0.004 |  | 605.05 |  | 31.05 | 4545.85
| Upright Freezers, Auto Defrost, w/o Auto Icemaker | [5 empty] | 0.07 |  |  | 0.005 |  | 614.69 |  | 40.69 | 4709.73
| Upright Freezers, Auto Defrost, w/ Auto Icemaker | [5 empty] | 0.07 |  |  | 0.005 |  | 614.69 |  | 40.69 | 4709.73
| Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [5 empty] | 0.071 |  |  | 0.005 |  | 620.69 |  | 46.69 | 4811.73
| Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [5 empty] | 0.071 |  |  | 0.005 |  | 620.69 |  | 46.69 | 4811.73
| Chest Freezers and All Other Freezers, except Compact Freezers | [5 empty] | 0.068 |  |  | 0.003 |  | 599.98 |  | 25.98 | 4459.66
| Chest Freezers with Auto Defrost | [5 empty] | 0.07 |  |  | 0.004 |  | 610.02 |  | 36.02 | 4630.34
| "Average" Freezer | [5 empty] | 0.07 |  |  | 0.004 |  | 612.26 |  | 38.26 | 4668.42
1 Use for Years 1 through 7 in TRB calculation.
2 Use for Years 8 through 17 in TRB calculation.
RESOURCES
• | AEG's Analysis Files titled "PY22 C_Appliance_Refrigerator - Analysis File," "AEG HPUC Dual BL and TRB - Analysis File" and "AEG HPUC Update of Residential Measures - Analysis file."
• | Electronic Code of Federal Regulations, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates. (a) Refrigerators/refrigerator-freezers/freezers, current as of December 13, 2018, accessed December 17, 2018.
• | Energy Information Administration, Residential Energy Consumption Survey, 2015, Table CE3.5: Annual household site end-use consumption in the West--totals and averages, 2015, https://www.eia.gov/consumption/residential/data/2015/c&e/pdf/ce3.5.pdf, accessed December 17, 2018.
• | ENERGY STAR Version 5.1 Consumer Refrigeration Products Final Cover Memo, August 5, 2021, https://www.energystar.gov/products/spec/residential_refrigerators_and_freezers_specification_version_5_0_pd, accessed January 19, 2022.
• | ENERGY STAR, Flip Your Fridge Calculator, https://www.energystar.gov/index.cfm?fuseaction=refrig.calculator, accessed January 21, 2020.
• | ENERGY STAR, Key Product Criteria, https://www.energystar.gov/products/appliances/refrigerators/key_product_criteria.
• | ENERGY STAR Program Requirements for Residential Refrigerators and Freezers. Eligibility Criteria, V5.0, https://www.energystar.gov/ia/partners/product_specs/program_reqs/ Refrigerators_and_Freezers_Program_Requirements_V5.0.pdf, accessed December 17, 2018.
• | ENERGY STAR, Savings Calculator for ENERGY STAR Appliances, available at: https://www.energystar.gov/sites/default/files/asset/document/appliance_calculator.xlsx, accessed December 15, 2018.
〖𝐴𝑉〗_𝑅=𝐹𝑟𝑒𝑠ℎ 𝑉𝑜𝑙𝑢𝑚𝑒+1.76∗𝐹𝑟𝑒𝑒𝑧𝑒𝑟 𝑉𝑜𝑙𝑢𝑚𝑒
〖𝐴𝑉〗_𝐹=1.73∗𝐹𝑟𝑒𝑒𝑧𝑒𝑟 𝑉𝑜𝑙𝑢𝑚𝑒
〖∆𝑘𝑊ℎ〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒=〖(𝐸〗_𝐵𝑎𝑠𝑒−𝐸_𝐸𝐸)∗𝑃𝐹
〖∆𝑘𝑊〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒=〖(〖∆𝑘𝑊ℎ〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒〗∕〖𝐻𝑅𝑆)∗𝐶𝐹〗
〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒+𝑇𝑢𝑟𝑛−𝑖𝑛)=〖(𝐸〗_𝐵𝑎𝑠𝑒−𝐸_𝐸𝐸+𝐸_(𝑇𝑢𝑟𝑛−𝑖𝑛))∗𝑃𝐹
〖∆𝑘𝑊〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒+𝑇𝑢𝑟𝑛−𝑖𝑛)=〖(〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒+𝑇𝑢𝑟𝑛−𝑖𝑛)〗∕〖𝐻𝑅𝑆)∗𝐶𝐹〗
〖∆𝑘𝑊〗_(𝑇𝑢𝑟𝑛−𝑖𝑛 𝑂𝑛𝑙𝑦)=〖(〖∆𝑘𝑊ℎ〗_(𝑇𝑢𝑟𝑛−𝑖𝑛 𝑂𝑛𝑙𝑦)〗∕〖𝐻𝑅𝑆)∗𝐶𝐹〗
〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒, 𝐿𝑖𝑓𝑒)=〖∆𝑘𝑊ℎ〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒∗〖𝐸𝑈𝐿〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒
〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒+𝑇𝑢𝑟𝑛−𝑖𝑛, 𝐿𝑖𝑓𝑒)=〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒, 𝐿𝑖𝑓𝑒)+(𝐸_(𝑇𝑢𝑟𝑛−𝑖𝑛)∗𝑃𝐹∗〖𝑅𝑈𝐿〗_(𝑇𝑢𝑟𝑛−𝑖𝑛))
〖∆𝑘𝑊ℎ〗_(𝑇𝑢𝑟𝑛−𝑖𝑛, 𝐿𝑖𝑓𝑒)=〖∆𝑘𝑊〗_(𝑇𝑢𝑟𝑛−𝑖𝑛 𝑂𝑛𝑙𝑦)∗〖𝑅𝑈𝐿〗_(𝑇𝑢𝑟𝑛−𝑖𝑛)
〖∆𝑘𝑊ℎ〗_(𝑇𝑢𝑟𝑛−𝑖𝑛 𝑂𝑛𝑙𝑦)=𝐸_(𝑇𝑢𝑟𝑛−𝑖𝑛)∗𝑃𝐹

## C_BEnvelope_Cool Roof
COMMERCIAL: Cool Roof
Return to TOC
MEASURE DETAILS
Description
This section covers installation of “cool roof” roofing materials in commercial buildings with mechanical cooling. The cool roof is assumed to have a solar absorptance of 0.3(1) compared to a standard roof with solar absorptance of 0.8(2). Energy and demand saving are realized through reductions in the building cooling loads. The approach utilizes DOE-2.2 simulations on a series of commercial prototypical building models. Energy and demand impacts are normalized per thousand square feet of roof space.
Program Criteria
Building must have a means of mechanical cooling and cool roof must meet solar absorptance criteria.
Unit of Measure
Per 1000 square feet of material
Baseline Equipment
Roof with a solar absorptance of 0.80
High Efficiency Equipment
Roof with a solar absorptance of 0.30
ALGORITHMS
ΔE |  |  | = 250 kWh per 1000-SF
ΔP |  |  | = CF * (0.0001 / SF)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Value | Unit | Notes
ΔE |  | Annual energy reduction per ft2 |  |  | Calculated | kWh | 250 kWh per 1000 SF
ΔP |  | Peak power demand reduction per ft2 |  |  | Calculated | kW | 0.100 kW per 1000 SF
CF |  | Coincidence factor, percent of time equipment load corresponds with utility peak load |  |  | 50 | %
Measure Life |  | Expected duration of energy savings |  |  | 15 | yrs
SAVINGS
Measure Name |  |  |  | Peak Demand Savings | Annual Energy Savings
Cool Roof |  |  |  | 0.05 | 250

## C_BEnvelope_Window Film
COMMERCIAL: Window Film
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM.
MEASURE DETAILS
Description
Window film reduces solar heat gain, reducing load on cooling systems. This is rated in solar heat gain coefficient (SHGC), which is the fraction of solar radiation admitted through fenestrations, ranging from 0 to 1. The lower the SHGC, the less solar heat it transmits and the greater its shading ability.
Program Criteria
| • | Both retrofit and new construction (NC) projects are included in this measure.
| • | Film must have a minimum five-year manufacturer’s warranty and one-year installer’s warranty.
| • | Rebates shall be paid on actual square footage of glass in a conditioned space.
| • | Windows may be clear or factory tinted, single or double pane, but must not have reflective glass.
| • | North-facing windows are not eligible for rebates.
| • | Windows significantly shaded by buildings, trees or awnings are not eligible for rebates. The degree of shading will be assessed by a Hawai‘i Energy Engineer / Energy Advisor. Hawai‘i Energy will provide documentation of the eligibility assessment, such as a satellite image, photograph from an onsite inspection, or signed statement from the customer. Examples of significant shading include the following:
|  | a) | South-facing windows: if trees, awnings, buildings, or other structures cover more than 50% of the window during midday hours.
|  | b) | West-facing windows: if trees, awnings, buildings, or other structures cover more than 50% of the window during afternoon hours.
|  | c) | East-facing windows: if trees, awnings, buildings, or other structures cover more than 50% of the window during morning hours.
| • | Replacement of deteriorated window film is eligible for 50% of the rebate if the customer attests to not previously receiving a rebate for the existing film.
| • | Because of the nature of their design, jalousie windows are not eligible for rebates. (Jalousie windows are also exempted from Hawaii's SHGC code requirements.)
Unit of Measure
Per window film application in a given orientation, where the orientation and window area (ft2) are custom entries.
Baseline Equipment
For retrofit projects, the baseline condition is no window film installed.
For new construction projects, the SHGC shall meet the IECC 2018 code minimum:
0.25 SHGC if projection factor is < 0.2
0.3 SHGC if projection factor is ≥ 0.2 and < 0.5
0.4 SHGC if projection factor = 0.5
where projection factor = horizontal projection of overhang divided by the vertical distance from overhang to bottom of window.
High Efficiency Equipment
For retrofit projects, the installed window film must have SHGC < 0.43 or Shading Coefficient (SC) < 0.5, where SHGC = 0.86*SC.
For new construction projects, window films that are 10% or more efficient than code requirements:
≤ 0.225 SHGC if projection factor is < 0.2
≤ 0.27 SHGC if projection factor is ≥ 0.2 and < 0.5
≤ 0.36 SHGC if projection factor = 0.5
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [6 empty] | Value |  | Unit |  | Source/Notes
o |  |  |  | Orientation of window (i.e., direction the window is facing) | [6 empty] | User input |  | -
Afilm,o |  |  |  | Area of window film applied to windows in orientation [o] | [6 empty] | User input |  | ft2
SHGFo |  |  |  | Peak solar heat gain factor for orientation of interest | [6 empty] | See Table 1 |  | Btu/ hr-ft2-yr |  | Values derived by AEG using the NREL (now NLR) PVWatts calculation tool. Analysis was conducted for Honolulu, HI and for Hawaii's peak demand period of 5-9 pm on non-holiday weekdays. (See file named "PVWatts_Honolulu_All _Orientations".)
SHGo |  |  |  | Solar heat gain for orientation of interest | [6 empty] | See Table 1 |  | Btu/ ft2-yr
SHGCpre,o |  |  |  | Solar heat gain coefficient for existing windows in orientation of interest | [6 empty] | User input |  | - |  | See Note 1 below regarding the specification of SHGC for existing windows.1
SHGCpost,o |  |  |  | Solar heat gain coefficient for windows with film in orientation of interest | [6 empty] | User input |  | - |  | See Note 2 below regarding the specification of SHGC for windows with film.2, 3
Eff |  |  |  | Efficiency of the cooling system. It is the ratio of net cooling capacity in Btu/hr to the total electric power input in Watts under designated operating conditions. The corresponding metric will be EER, SEER2, IEER, or IPLV (expressed in Btu/hr-W), depending on the equipment type. | [6 empty] | User input |  | Btu/ hr-W |  | If the Eff value is unknown, a default value (see Table 3) based on the cooling system type and the building year of construction can be selected by the user.
1000 |  |  |  | Conversion factor (W per kW) | [6 empty] | - |  | W/kW
EUL |  |  |  | Effective useful life of measure | [6 empty] | 10 |  | years |  | See Note 4 below.
1 Table 2 below contains examples of window and interior shading configurations along with their typical SHGC values. When specifying the SHGC of existing windows, the practitioner should also be aware that the SHGC of the same windows with film should be a value relative to the SHGC of the existing windows (see Note 2 below).
2 SHGC of new window film can be obtained from manufacturer specifications and/or an accredited rating organization such as the National Fenestration Rating Council (NFRC). For the purpose of savings calculation, the practitioner must select a SHGC value of the new window film that is relative to the SHGC of the existing window in order to capture the appropriate amount of SHGC reduction due to the window film. It is for this reason that the NFRC provides both the SHGC (no film) and SHGC (with film) values for each of their window film product ratings. An arbitrary SHGC value for the window film that has no relation to the existing window SHGC should not be used for the savings calculation.
3 Older products may provide a shading coefficient (SC) instead of SHGC. Per Section 5.8.2.4 of ASHRAE 90.1-2016, SHGC can be estimated by multiplying SC by 0.86.
4 EUL of 10 years is consistent with the EUL reported for window film in the California Database for Energy Efficiency Resources (DEER) 2020, Texas Technical Reference Manual (version 13), and New Mexico Technical Reference Manual (2025-2026).
Table 1. Solar Heat Gain (SHG) and Peak Solar Heat Gain Factor (SHGF) for Honolulu 5
| Window Orientation |  |  |  | SHG (Btu/ft2-year) |  |  | SHGF (Btu/hr-ft2-year)
| North-East |  |  |  | 260727 |  |  | 4
| East |  |  |  | 353512 |  |  | 4
| South-East |  |  |  | 370064 |  |  | 5
| South |  |  |  | 350779 |  |  | 10
| South-West |  |  |  | 373810 |  |  | 29
| West |  |  |  | 356792 |  |  | 41
| North-West |  |  |  | 261620 |  |  | 32
5 AEG derived SHG and SHGF values for Honolulu with the use of NLR's PVWatts Calculator (available online at: https://pvwatts.nlr.gov/) by (1) specifying a 90-degree tilt angle to simulate the vertical plane of a window and (2) varying the azimuth to simulate each orientation. The final SHG and SHGF values were obtained by averaging the results across 45 degrees of azimuth with the listed orientation at the center (e.g. the values listed for South is the average of the results for South-South-West, South, and South-South-East).
Table 2. Solar Heat Gain Coefficient (SHGC) for Various Window and Shading Configurations 6
| Window and Shading 7 | [8 empty] | SHGCpre
| Single-pane (no interior shade) | [8 empty] | 0.7998
| Single-pane with roller shade | [8 empty] | 0.516
| Single-pane with louvered interior shades | [8 empty] | 0.4816
| Single-pane with draperies (open weave) | [8 empty] | 0.5762
| Single-pane with draperies (closed weave) | [8 empty] | 0.4816
| Double-pane (no interior shade) | [8 empty] | 0.688
| Double-pane with roller shade | [8 empty] | 0.5332
| Double-pane with louvered interior shades | [8 empty] | 0.4988
| Double-pane with draperies (open weave) | [8 empty] | 0.5504
| Double-pane with draperies (closed weave) | [8 empty] | 0.4988
6 The SHGC values in this table are provided for reference only and are not used in the semi-prescriptive calculator for this measure. The window types and SHGC values are the same as those listed in the New Mexico Technical Resource Manual 2025-2026, which in turn are based on shading coefficients (SC) provided in Chapter 15 of the 2009 ASHRAE Fundamentals Handbook. ICF converted the listed SC values to SHGC values (per Section 5.8.2.4 of ASHRAE 90.1-2016, SHGC can be estimated by multiplying SC by 0.86.).
7 The window types listed in this table are all clear-glass windows with no existing treatments or coatings.
Table 3. Efficiency (Btu/hr-W) by Building Vintage and HVAC System Type 8
| Year of Construction | [5 empty] | AC/HP |  | PTAC/PTHP |  |  | Air-Cooled Chiller |  |  |  | Water-Cooled Chiller
| Before 2011 | [5 empty] | 9.9 |  | 9.9 |  |  | 8.5 |  |  |  | 14.3
| 2011-2016 | [5 empty] | 13 |  | 10.6 |  |  | 9.6 |  |  |  | 18.8
| After 2016 | [5 empty] | 13.6 |  | 10.7 |  |  | 14.9 |  |  |  | 26
8 The efficiency values (in units of Btu/hr-W) in the "Before 2011" and "2011-2016" rows are derived from converted COP values from Table 125 in the Texas Technical Reference Manual, version 13, which in turn are based on a review of minimum requirements specified in the International Energy Conservation Code (IECC) for various years. The efficiency values (in units of Btu/hr-W) in the "After 2016" row are based on averages of EER, SEER2, IEER, or IPLV values (as appropriate) across capacity bins and by equipment type from the baseline tables in the Hawai'i Energy PY26 TRM's worksheets named "C_HVAC_AC_HP_WKST" and "C_HVAC_Chiller_WKST". All values in the table also map to ASHRAE 90.1 and minimum federal standards, as applicable. Refer to ICF's analysis file named "PY26 TRM - Commercial Window Film - Analysis File" for more information.
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Note: If a project involves the application of film to windows in multiple orientations, then the total savings for the project is equal to the sum of the savings for each orientation.
SHGC of new window film can be obtained from manufacturer specifications and/or an accredited rating organization such as the National Fenestration Rating Council (NFRC). For the purpose of savings calculation, the practitioner must select a SHGC value of the new window film that is relative to the SHGC of the existing window in order to capture the appropriate amount of SHGC reduction due to the window film. It is for this reason that the NFRC provides both the SHGC (no film) and SHGC (with film) values for each of their window film product ratings. An arbitrary SHGC value for the window film that has no relation to the existing window SHGC should not be used for the savings calculation.
User Inputs
| Is this a new construction project? | [9 empty] | No
| Window orientation: | [9 empty] | South
| SHGC of baseline windows: | [9 empty] | 0.7
| SHGC of windows with film applied: | [9 empty] | 0.4 |  |  | Measure qualifies
| Area of window film applied, in square feet: | [9 empty] | 100
| HVAC system efficiency (units of Btu/hr-W) | [9 empty] | 17 |  |  | <--Leave blank if unknown
If efficiency is unknown, select the items below -
[5 empty] | Building year of construction: | [5 empty] | After 2016
[5 empty] | HVAC system type: | [5 empty] | AC/HP
Measure Name | [5 empty] | Peak Demand Savings |  |  |  |  | Annual Energy Savings |  |  |  |  | Lifetime Energy Savings
Retrofit Window Film | [5 empty] | 0.018 |  |  |  |  | 619.02 |  |  |  |  | 6190.2
Note: Savings shown in blue result from sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Commercial Window Film - Analysis File."
• | AEG's 2021 Analysis Files titled "PY21 TRM NonRes Window Film Analysis File" and "PVWatts_Honolulu_All_Orientations."
• | American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE), Standard 90.1, 2016.
• | National Fenestration Rating Council, Certified Products Directory, https://www.nfrc.org/certified-product-directory/, accessed 2/10/2021.
• | National Laboratory of the Rockies (NLR), PVWatts Calculator, https://pvwatts.nlr.gov/.
• | New Mexico Technical Resource Manual for the Calculation of Energy Efficiency Savings, Prepared for the New Mexico Public Regulation Commission, April 15, 2025, https://www.prc.nm.gov/wp-content/uploads/2025/04/New-Mexico-TRM-2025-Final-04-15-2025.pdf.
• | Savings Estimation Technical Reference Manual 2017, Third Edition, California Municipal Utilities Association.
• | Southern California Edison, Work Paper SCE13HC002: Reflective Window Film, January 28, 2015.
• | Texas Technical Reference Manual, Version 13.0, Volume 3: Nonresidential Measures, November 2025, https://texasefficiency.com/wp-content/uploads/2025/11/trm13v3.pdf.
• | California Database for Energy Efficiency Resources (DEER) 2020.
∆𝑘𝑊=(𝐴_(𝑓𝑖𝑙𝑚,𝑜)×〖𝑆𝐻𝐺𝐹〗_𝑜×(〖𝑆𝐻𝐺𝐶〗_(𝑝𝑟𝑒,𝑜)−〖𝑆𝐻𝐺𝐶〗_(𝑝𝑜𝑠𝑡,𝑜) ))/(𝐸𝑓𝑓 ×1000)
∆𝑘𝑊ℎ=(𝐴_(𝑓𝑖𝑙𝑚,𝑜)×〖𝑆𝐻𝐺〗_𝑜×(〖𝑆𝐻𝐺𝐶〗_(𝑝𝑟𝑒,𝑜)−〖𝑆𝐻𝐺𝐶〗_(𝑝𝑜𝑠𝑡,𝑜) ))/(𝐸𝑓𝑓 ×1000)
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ×𝐸𝑈𝐿

## C_Kitchen_Combination Oven
COMMERCIAL: Combination Oven
Return to TOC
UPDATE STATUS
Updated in Winter 2022-2023 for PY23 TRM.
MEASURE DETAILS
Description
This measure relates to installing a new commercial combination oven meeting ENERGY STAR efficiency standards. Commercial combination ovens are convection ovens with the added capability to inject steam into the oven capacity. They offer three distinct cooking modes: hot air convection, steam heating, and a combination of both modes. The combination oven is also referred to as a combination oven/steamer, combi, or combo. ENERGY STAR commercial combination ovens are about 20-40% more energy efficient than standard models.
Program Criteria
Eligible ovens must be compliant with the current ENERGY STAR requirements: • Full-size electric combination ovens must accommodate two 12.7 x 20.8 x 2.5-inch steam table pans per rack position. • Half-size electric convection ovens must accommodate one 12.7 x 20.8 x 2.5-inch steam table pan per rack position. • Cooking energy efficiency and idle energy rate must meet or exceed those specified in ENERGY STAR Version 3.0.
Unit of Measure
One oven
Baseline Equipment
For this characterization to apply, the baseline equipment is assumed to be a full-size or half-size electric combination oven not meeting the ENERGY STAR key product criteria and with a pan capacity equal to or more than three pans and equal to or less than 40 pans.
High Efficiency Equipment
For this characterization to apply, the efficient equipment is assumed to be a full-size or half-size electric combination convection oven meeting the minimum ENERGY STAR key product criteria and with a pan capacity equal to or more than three pans and equal to or less than 40 pans.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Where:
(2)
(3)
(4)
(5)
(6)
(6)
(7)
(8)
(9)
Peak Demand Reduction, kW
(10)
Lifetime Energy Savings, kWh
(11)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  | Value | Unit | Source/Notes
EBaseline |  |  | Baseline equipment daily energy use |  |  | See Table 1 | Wh | Calculated
EHE |  |  | High efficiency equipment daily energy use |  |  | See Table 1 | Wh | Calculated
Epreheat |  |  | Daily preheat energy use |  |  | See Table 1 | Wh | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
Econvection |  |  | Daily convection energy use |  |  | See Table 1 | Wh | Calculated
Esteam |  |  | Daily steam energy use |  |  | See Table 1 | Wh | Calculated
Eidle,convection |  |  | Daily idle energy use in convection mode |  |  | See Table 1 | Wh | Calculated
Eidle,steam |  |  | Daily idle energy use in steam mode |  |  | See Table 1 | Wh | Calculated
EPMconvection |  |  | Energy needed to cook 1 lb of food |  |  | 73.2 | Wh/lb | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
EPMsteam |  |  | Energy needed to steam 1lb of food |  |  | 30.8 | Wh/lb | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
ƞconvection |  |  | Energy efficiency of convection mode |  |  | See Table 1 | - | ENERGY STAR Version 3.0, Texas TRM
ƞsteam |  |  | Energy efficiency of steam mode |  |  | See Table 1 | - | ENERGY STAR Version 3.0, Texas TRM
%convection |  |  | Percentage of time in convection mode |  |  | 50% | - | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
%steam |  |  | Percentage of time in steam mode |  |  | 50% | - | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
npreheat |  |  | Number of daily preheat cycles |  |  | 1 | - | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
tpreheat |  |  | Duration of preheat |  |  | 15 | mins | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
tidle,convection |  |  | Daily idle time in convection mode |  |  | See Table 1 | hrs | Calculated
tidle,steam |  |  | Daily idle time in steam mode |  |  | See Table 1 | hrs | Calculated
Pidle,convection |  |  | Idle power draw of cooking mode |  |  | See Table 1 | W | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
Pidle,steam |  |  | Idle power draw of steam mode |  |  | See Table 1 | W | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
MASSDAY |  |  | Amount of food cooked daily |  |  | See Table 1 | lb | 2023 California eTRM
CAPconvection |  |  | Production capacity in convection mode |  |  | See Table 1 | lb/hr | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21) & 2023 Texas TRM
CAPsteam |  |  | Production capacity in steam mode |  |  | See Table 1 | lb/hr | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21) & 2023 Texas TRM
P |  |  | Number of sheet pans in oven |  |  | See Table 1 footnotes | - | AEG assumption for each capacity bin
DAYS |  |  | Annual days of operation |  |  | 365 | days | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
DAYHRS |  |  | Daily hours of operation |  |  | 12 | hrs | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
HRS |  |  | Annual operating hours |  |  | 4380 | hrs | 365 days; 12 hrs/day
CF |  |  | Coincidence factor |  |  | 0.9 | - | 2004-2005 DEER Update Study1
EUL |  |  | Expected useful life of measure |  |  | 12 | yrs | PY23 TRM Commercial Kitchen Combination Oven Analysis File, "EUL Benchmarking" sheet
Notes:
1. The commercial kitchen combination oven is assumed to operate within the California DEER peak period of 4-9 pm on weekdays at a constant load throughout the day. Hawaii's peak period is 5-9 pm non-holiday weekdays (year-round), similar to California's peak period of 4-9 pm on weekdays. As such, a CF of 0.90 is appropriate to use for Hawaii. The CF value should be updated with Hawaii-specific load shape analysis in the future.
Table 1. Summary of Savings Calculations
3- 4 Pan Capacity
|  |  |  | Baseline |  |  | High Efficiency
|  |  |  | Convection Mode | Steam Mode |  | Convection Mode |  |  | Steam Mode
Percentage of time in convection/steam mode, %convection, %steam |  |  |  | 50% | 50% |  | 50% |  |  | 50%
Energy efficiency of convection/steam mode, ƞconvection, ƞsteam |  |  |  | 70% | 49% |  | 70% |  |  | 51%
Production capacity in convection/steam mode (lbs/hr), CAPconvection, CAPsteam |  |  |  | 79 | 126 |  | 119 |  |  | 177
Number of daily preheat cycles, npreheat |  |  |  | 1
Duration of preheat (minutes), tpreheat |  |  |  | 15
Preheat energy use (Wh), Epreheat |  |  |  | 3000 |  |  | 1500
Idle power draw of convection/steam mode (W)a, Pidle,convection, Pidle,steam |  |  |  | 1320 | 5260 |  | 750 |  |  | 2400
Energy needed to cook/steam 1 lb of food (Wh/pound), EPMconvection, EPMsteam |  |  |  | 73.2 | 30.8 |  | 73.2 |  |  | 30.8
Amount of food cooked daily (lbs), MASSDAY |  |  |  | 200
Daily convection/steam energy use (Wh), Econvection, Esteam |  |  |  | 10457.1429 | 6285.7143 |  | 10457.1429 |  |  | 6039.2157
Daily idle time in convection/steam mode (hours), tidle,convection, tidle,steam |  |  |  | 10.4842 | 10.9563 |  | 10.9097 |  |  | 11.185
Daily idle energy use (Wh) |  |  |  | 13839.1139 | 57630.3968 |  | 8182.2479 |  |  | 26844.0678
Total daily energy use (Wh) |  |  |  | 91212.3679 |  |  | 53022.6742
5-14 Pan Capacity
|  |  |  | Baseline |  |  | High Efficiency
|  |  |  | Convection Mode | Steam Mode |  | Convection Mode |  |  | Steam Mode
Percentage of time in convection/steam mode, %convection, %steam |  |  |  | 50% | 50% |  | 50% |  |  | 50%
Energy efficiency of convection/steam mode, ƞconvection, ƞsteam |  |  |  | 72% | 49% |  | 78% |  |  | 55%
Production capacity in convection/steam mode (lbs/hr), CAPconvection, CAPsteam |  |  |  | 79 | 126 |  | 119 |  |  | 177
Number of daily preheat cycles, npreheat |  |  |  | 1
Duration of preheat (minutes), tpreheat |  |  |  | 15
Preheat energy use (Wh), Epreheat |  |  |  | 3000 |  |  | 1500
Idle power draw of convection/steam mode (W)b, Pidle,convection, Pidle,steam |  |  |  | 1320 | 5260 |  | 1180 |  |  | 1970
Energy needed to cook/steam 1 lb of food (Wh/pound), EPMconvection, EPMsteam |  |  |  | 73.2 | 30.8 |  | 73.2 |  |  | 30.8
Amount of food cooked daily (lbs), MASSDAY |  |  |  | 200
Daily convection/steam energy use (Wh), Econvection, Esteam |  |  |  | 10166.6667 | 6285.7143 |  | 9384.6154 |  |  | 5600
Daily idle time in convection/steam mode (hours), tidle,convection, tidle,steam |  |  |  | 10.4842 | 10.9563 |  | 10.9097 |  |  | 11.185
Daily idle energy use (Wh), Eidle,convection, Eidle,steam |  |  |  | 13839.1139 | 57630.3968 |  | 12873.4034 |  |  | 22034.5056
Total daily energy use (Wh) |  |  |  | 90921.8917 |  |  | 51392.5244
15-28 Pan Capacity
|  |  |  | Baseline |  |  | High Efficiency
|  |  |  | Convection Mode | Steam Mode |  | Convection Mode |  |  | Steam Mode
Percentage of time in convection/steam mode, %convection, %steam |  |  |  | 50% | 50% |  | 50% |  |  | 50%
Energy efficiency of convection/steam mode, ƞconvection, ƞsteam |  |  |  | 72% | 49% |  | 78% |  |  | 55%
Production capacity in convection/steam mode (lbs/hr), CAPconvection, CAPsteam |  |  |  | 166 | 201 |  | 295 |  |  | 349
Number of daily preheat cycles, npreheat |  |  |  | 1
Duration of preheat (minutes), tpreheat |  |  |  | 15
Preheat energy use (Wh), Epreheat |  |  |  | 3750 |  |  | 2000
Idle power draw of convection/steam mode (W)c, Pidle,convection, Pidle,steam |  |  |  | 2280 | 8710 |  | 2176 |  |  | 3566
Energy needed to cook/steam 1 lb of food (Wh/pound), EPMconvection, EPMsteam |  |  |  | 73.2 | 30.8 |  | 73.2 |  |  | 30.8
Amount of food cooked daily (lbs), MASSDAY |  |  |  | 250
Daily convection/steam energy use (Wh), Econvection, Esteam |  |  |  | 12708.3333 | 7857.1429 |  | 11730.7692 |  |  | 7000
Daily idle time in convection/steam mode (hours), tidle,convection, tidle,steam |  |  |  | 10.997 | 11.1281 |  | 11.3263 |  |  | 11.3918
Daily idle energy use (Wh), Eidle,convection, Eidle,steam |  |  |  | 25073.1325 | 96925.8333 |  | 24645.9661 |  |  | 40623.2794
Total daily energy use (Wh) |  |  |  | 146314.4421 |  |  | 86000.0147
28-40 Pan Capacity
|  |  |  | Baseline |  |  | High Efficiency
|  |  |  | Convection Mode | Steam Mode |  | Convection Mode |  |  | Steam Mode
Percentage of time in convection/steam mode, %convection, %steam |  |  |  | 50% | 50% |  | 50% |  |  | 50%
Energy efficiency of convection/steam mode, ƞconvection, ƞsteam |  |  |  | 72% | 49% |  | 78% |  |  | 55%
Production capacity in convection/steam mode (lbs/hr), CAPconvection, CAPsteam |  |  |  | 166 | 201 |  | 295 |  |  | 349
Number of daily preheat cycles, npreheat |  |  |  | 1
Duration of preheat (minutes), tpreheat |  |  |  | 15
Preheat energy use (Wh), Epreheat |  |  |  | 5630 |  |  | 3000
Idle power draw of convection/steam mode (W)a, Pidle,convection, Pidle,steam |  |  |  | 2280 | 8710 |  | 3172 |  |  | 5162
Energy needed to cook/steam 1 lb of food (Wh/pound), EPMconvection, EPMsteam |  |  |  | 73.2 | 30.8 |  | 73.2 |  |  | 30.8
Amount of food cooked daily (lbs), MASSDAY |  |  |  | 400
Daily convection/steam energy use (Wh), Econvection, Esteam |  |  |  | 20333.3333 | 12571.4286 |  | 18769.2308 |  |  | 11200
Daily idle time in convection/steam mode (hours), tidle,convection, tidle,steam |  |  |  | 10.5452 | 10.755 |  | 11.072 |  |  | 11.1769
Daily idle energy use (Wh), Eidle,convection, Eidle,steam |  |  |  | 24043.012 | 93675.8333 |  | 35120.4915 |  |  | 57695.3338
Total daily energy use (Wh) |  |  |  | 156253.6073 |  |  | 125785.0561
a. The idle power draw for high efficiency case is calculated using an average pan capacity of 4. Convection mode: ((0.05*4)+0.55)*1000W=750W. Steam mode: (0.6*4)*1000W=2400W.
b. The idle power draw for high efficiency case is calculated using an average pan capacity of 10. Convection mode: ((0.083*10)+0.35)*1000W=1180W. Steam mode: ((0.133*10)+0.64)*1000W=1970W
c. The idle power draw for high efficiency case is calculated using an average pan capacity of 22. Convection mode: ((0.083*22)+0.35)*1000W=2176W. Steam mode: ((0.133*22)+0.64)*1000W=2926W
d. The idle power draw for high efficiency case is calculated using an average pan capacity of 22. Convection mode: ((0.083*34)+0.35)*1000W=3172W. Steam mode: ((0.133*34)+0.64)*1000W=5162W
SAVINGS
Oven Capacity |  |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  | Lifetime Energy Savings
3-4 Pans |  |  |  | 2.864 |  | 13939.24 |  |  | 167270.88
9 |  |  |  | 2.965 |  | 14428.22 |  |  | 173138.64
15-28 Pans |  |  |  | 4.524 |  | 22014.77 |  |  | 264177.24
29-40 Pans |  |  |  | 2.285 |  | 11121.02 |  |  | 133452.24
RESOURCES
• | AEG's analysis file titled "PY23 TRM Commercial Kitchen Combination Oven - Analysis File."
• | Code of Federal Regulations at 10 CFR 431.66. URL: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-C/subject-group-ECFR8115bf7451f830f/section-431.66.
• | ENERGY STAR. 2023. "ENERGY STAR® Program Requirements Product Specification for Commercial Ovens - Eligibility Criteria Version 3.0." Effective on January 12, 2023. URL: https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Version%203.0%20Commercial%20Ovens%20Final%20Specification_0.pdf
• | US EPA and US DOE. ENERGY STAR Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products. June 7, 2021. URL: https://www.energystar.gov/sites/default/files/asset/document/CFS_calculator_07-15-2021.xlsx
• | California eTRM. Combination Oven, Commercial. SWFS003-02. November 10, 2022. URL: https://www.caetrm.com/measure/SWFS003/02/
• | Itron, Inc. 2005-2005 Database for Energy Efficiency Resources (DEER) Update Study. Final Report. Prepared for Southern California Edison. December 2005. Table 3-14, p. 3-17.
• | California Technical Forum. 2023. "CPUC Support Tables. Effective Useful Life and Remaining Useful Life." URL: https://www.caetrm.com/cpuc/table/effusefullife/. February 1, 2023.
• | 2023 Illinois Statewide Technical Reference Manual for Energy Efficiency Version 11.0, Volume 2: Commercial and Industrial Measures FINAL. September 22, 2022.
• | Texas Technical Reference Manual Version 10.0, Volume 3: Nonresidential Measures. Program Years 2023. November 2022.
• | New Jersey Board of Public Utilities, New Jersey's Clean Energy ProgramTM Protocols to Measure Resource Savings, FY2021 Addendum. December 2, 2020.
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Program Version 3.3 FINAL. January 31, 2021.
DAYS
∆𝑘𝑊ℎ=〖(𝐸〗_𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 − 𝐸_𝐻𝐸) ∗ DAYS
∆𝑘𝑊= ∆𝑘𝑊ℎ∗𝐶𝐹/𝐻𝑅𝑆
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
𝐸_𝐻𝐸 =( 𝐸_(𝑝𝑟𝑒ℎ𝑒𝑎𝑡, 𝐻𝐸)+ 𝐸_(𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛, 𝐻𝐸 )+ 𝐸_(𝑠𝑡𝑒𝑎𝑚, 𝐻𝐸)+𝐸_(𝑖𝑑𝑙𝑒, 𝐻𝐸 ) )
𝐸_𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 =( 𝐸_(𝑝𝑟𝑒ℎ𝑒𝑎𝑡, 𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒)+ 𝐸_(𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛, 𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 )+ 〖𝐸_(𝑠𝑡𝑒𝑎𝑚, 𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 )+𝐸〗_(𝑖𝑑𝑙𝑒, 𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 ) )
𝐸_𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛 =𝐸𝑃𝑀𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛 ∗𝑀𝐴𝑆𝑆𝐷𝐴𝑌/ ƞ_(𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛 )
𝐸_𝑠𝑡𝑒𝑎𝑚 =𝐸𝑃𝑀𝑠𝑡𝑒𝑎𝑚 ∗𝑀𝐴𝑆𝑆𝐷𝐴𝑌/ ƞ_𝑠𝑡𝑒𝑎𝑚
𝐸_(𝑖𝑑𝑙𝑒,𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛)=𝑃_(𝑖𝑑𝑙𝑒, 𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛) ∗ 𝑡_(𝑖𝑑𝑙𝑒, 𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛 )
𝑡_(𝑖𝑑𝑙𝑒,𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛) = 𝐷𝐴𝑌𝐻𝑅𝑆 −(𝑀𝐴𝑆𝑆𝐷𝐴𝑌/𝐶𝐴𝑃𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛) − (𝑡𝑝𝑟𝑒ℎ𝑒𝑎𝑡/60)
𝑡_(𝑖𝑑𝑙𝑒,𝑠𝑡𝑒𝑎𝑚) = 𝐷𝐴𝑌𝐻𝑅𝑆 −(𝑀𝐴𝑆𝑆𝐷𝐴𝑌/𝐶𝐴𝑃𝑠𝑡𝑒𝑎𝑚) − (𝑡𝑝𝑟𝑒ℎ𝑒𝑎𝑡/60)
𝐸_(𝑖𝑑𝑙𝑒,𝑠𝑡𝑒𝑎𝑚)=𝑃_(𝑖𝑑𝑙𝑒,𝑠𝑡𝑒𝑎𝑚) ∗ 𝑡_(𝑖𝑑𝑙𝑒,𝑠𝑡𝑒𝑎𝑚)
+
𝐸_𝑖𝑑𝑙𝑒=𝐸_(𝑖𝑑𝑙𝑒, 𝑐𝑜𝑛𝑣𝑒𝑐𝑡𝑖𝑜𝑛) + 𝐸_(𝑖𝑑𝑙𝑒,𝑠𝑡𝑒𝑎𝑚)

## C_Kitchen_Convection Oven
COMMERCIAL: Convection Oven
Return to TOC
UPDATE STATUS
Updated in Winter 2022-2023 for PY23 TRM.
MEASURE DETAILS
Description
This measure relates to installing a new commercial convection oven meeting ENERGY STAR efficiency standards. Commercial convection ovens cook food by forcing hot, dry air over the food product surface. The rapidly moving hot air strips away the colder air layer next to the food surface and causes the food to absorb the heat. While this measure does not include convection ovens that can heat the cooking cavity with saturated or superheated steam, it encompasses convection ovens that may have moisture injection capabilities (e.g., baking ovens and moisture-assist ovens). Convection ovens with a hold feature are eligible as long as convection is the only method used to cook the food. ENERGY STAR commercial full-size convection ovens are about 10-30% more energy efficient than standard models.
Program Criteria
Eligible ovens must be compliant with the current ENERGY STAR requirements: • Full-size electric convection ovens must accommodate standard full-size sheets pans measuring 18 x 26 x 1 inch. • Half-size electric convection ovens must accommodate half-size sheets pans measuring 18 x 13 x 1 inch. • Cooking energy efficiency and idle energy rate must meet or exceed those specified in ENERGY STAR Version 3.0.
Unit of Measure
One oven
Baseline Equipment
For this characterization to apply, the baseline equipment is assumed to be a full-size or half-size electric convection oven not meeting the ENERGY STAR key product criteria.
High Efficiency Equipment
For this characterization to apply, the efficient equipment is assumed to be a full-size or half-size convection oven meeting the minimum ENERGY STAR key product criteria.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Where:
(2)
(3)
(4)
(5)
(6)
Peak Demand Reduction, kW
(7)
Lifetime Energy Savings, kWh
(8)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  | Value | Unit | Source/Notes
EBaseline |  |  | Baseline equipment daily energy use |  |  | Table 1 | Wh | Calculated
EHE |  |  | High efficiency equipment daily energy use |  |  | Table 1 | Wh | Calculated
Epreheat |  |  | Daily preheat energy use |  |  | Table 1 | Wh | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
Ecook |  |  | Daily cooking energy use |  |  | Table 1 | Wh | Calculated
Eidle |  |  | Daily idle energy use |  |  | Table 1 | Wh | Calculated
EPM |  |  | Energy needed to cook 1 lb of food |  |  | 73.2 | Wh/lb | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
ƞcook |  |  | Cooking energey efficiency |  |  | Table 1 | - | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21) & ENERGY STAR 5.0
npreheat |  |  | Number of daily preheat cycles |  |  | 1 | - | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Product
tpreheat |  |  | Duration of preheat |  |  | Table 1 | mins | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
tIdle |  |  | Daily idle time |  |  | Table 1 | hrs | Calculated
Pidle |  |  | Idle power draw |  |  | Table 1 | W | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21) & ENERGY STAR 5.0
MASSDAY |  |  | Amount of food cooked daily |  |  | 122 | lbs | 2023 California eTRM
CAP |  |  | Production capacity |  |  | Table 1 | lbs/hr | US EPA Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products (07-15-21)
DAYS |  |  | Annual days of operation |  |  | 270 | days | 2023 California eTRM
DAYHRS |  |  | Daily hours of operation |  |  | 10 | hrs | 2023 California eTRM
HRS |  |  | Annual operating hours |  |  | 2700 | hrs | 270 days; 10 hrs/day
CF |  |  | Coincidence factor |  |  | 0.9 | - | 2004-2005 DEER Update Study1
EUL |  |  | Estimated useful life of measure |  |  | 12 | yrs | PY23 TRM Commercial Kitchen Convection Oven Analysis File, "EUL Benchmarking" sheet
Notes:
1. The commercial kitchen convection oven is assumed to operate within the California DEER peak period of 4-9 pm on weekdays at a constant load throughout the day. Hawaii's peak period is 5-9 pm non-holiday weekdays (year-round), similar to California's peak period of 4-9 pm on weekdays. As such, a CF of 0.90 is appropriate to use for Hawaii. The CF value should be updated with Hawaii-specific load shape analysis in the future.
Table 1. Summary of Savings Calculations
|  |  |  | Full-size Oven ≥5 Pans |  | Full-size Oven <5 Pans |  |  | Half-size Oven
|  |  |  | Baseline | EnergyStar | Baseline | EnergyStar |  | Baseline | EnergyStar
Cooking energy efficiency, ƞcook |  |  |  | 65% | 76% | 65% | 76% |  | 68% | 71%
Production capacity (lbs/hr), CAP |  |  |  | 90 | 90 | 90 | 90 |  | 45 | 50
Number of daily preheat cycles, npreheat |  |  |  | 1 | 1 | 1 | 1 |  | 1 | 1
Duration of preheat (minutes), tpreheat |  |  |  | 9 | 9 | 9 | 9 |  | 9 | 8
Preheat energy (Wh), Epreheat |  |  |  | 1563 | 1389 | 1563 | 1389 |  | 890 | 700
Idle power draw (W), Pidle |  |  |  | 2000 | 1400 | 2000 | 1000 |  | 1030 | 1000
Energy need to cook 1 lb of food (Wh/pound), EPM |  |  |  | 73.2 |  | 73.2 |  |  | 73.2
Cooking daily energy usage (Wh), Ecook |  |  |  | 13739.0769 | 11750.5263 | 13739.0769 | 11750.5263 |  | 13132.9412 | 12578.0282
Daily idling time (hours), tidle |  |  |  | 8.4944 | 8.4944 | 8.4944 | 8.4944 |  | 7.1389 | 7.4267
Idling daily energy usage (Wh), Eidle |  |  |  | 16988.8889 | 11892.2222 | 16988.8889 | 8494.4444 |  | 7353.0556 | 7426.6667
Total daily energy (Wh), E |  |  |  | 32290.9658 | 25031.7485 | 32290.9658 | 21633.9708 |  | 21375.9967 | 20704.6948
SAVINGS
Equipment Size |  |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Full-size Oven ≥5 Pans |  |  |  | 0.653 |  | 1959.99 |  |  | 23519.88
Full-size Oven <5 Pans |  |  |  | 0.959 |  | 2877.39 |  |  | 34528.68
Half-size Oven |  |  |  | 0.06 |  | 181.25 |  |  | 2175
RESOURCES
• | AEG's analysis file titled "PY23 TRM Commercial Kitchen Convection Oven Analysis File."
• | Code of Federal Regulations at 10 CFR 431.66. URL: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-C/subject-group-ECFR8115bf7451f830f/section-431.66.
• | ENERGY STAR. 2023. "ENERGY STAR® Program Requirements Product Specification for Commercial Ovens - Eligibility Criteria Version 3.0." Effective on January 12, 2023. URL: https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Version%203.0%20Commercial%20Ovens%20Final%20Specification_0.pdf
• | US EPA and US DOE. ENERGY STAR Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products. June 7, 2021. URL: https://www.energystar.gov/sites/default/files/asset/document/CFS_calculator_07-15-2021.xlsx
• | California eTRM. Convection Oven, Commercial. SWFS001-02. December 23, 2021. URL: https://www.caetrm.com/measure/SWFS001/02/
• | Southern California Gas Company (SCG). "UpdatePlan_Conv Oven_12292019.xlsx." August 5, 2019. URL: https://www.caetrm.com/media/reference-documents/Update_Plan_Conv_Oven_12292019.xlsx
• | Itron, Inc. 2005-2005 Database for Energy Efficiency Resources (DEER) Update Study. Final Report. Prepared for Southern California Edison. December 2005. Table 3-14, p. 3-17.
• | California Technical Forum. 2023. "CPUC Support Tables. Effective Useful Life and Remaining Useful Life." URL: https://www.caetrm.com/cpuc/table/effusefullife/. February 1, 2023.
• | 2023 Illinois Statewide Technical Reference Manual for Energy Efficiency Version 11.0, Volume 2: Commercial and Industrial Measures FINAL. September 22, 2022.
• | Texas Technical Reference Manual Version 10.0, Volume 3: Nonresidential Measures. Program Years 2023. November 2022.
• | New Jersey Board of Public Utilities, New Jersey's Clean Energy ProgramTM Protocols to Measure Resource Savings, FY2021 Addendum. December 2, 2020.
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Program Version 3.3 FINAL. January 31, 2021.
DAYS
∆𝑘𝑊ℎ=〖(𝐸〗_𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 − 𝐸_𝐻𝐸) ∗ DAYS
∆𝑘𝑊=∆𝑘𝑊ℎ∗𝐶𝐹/𝐻𝑅𝑆
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
𝐸_𝐻𝐸 =( 𝐸_(𝑝𝑟𝑒ℎ𝑒𝑎𝑡, 𝐻𝐸)+ 𝐸_(𝑐𝑜𝑜𝑘, 𝐻𝐸 )+ 𝐸_(𝑖𝑑𝑙𝑒, 𝐻𝐸 ) )
𝐸_𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 =( 𝐸_(𝑝𝑟𝑒ℎ𝑒𝑎𝑡, 𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒)+ 𝐸_(𝑐𝑜𝑜𝑘, 𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 )+ 𝐸_(𝑖𝑑𝑙𝑒, 𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 ))
𝐸_𝑐𝑜𝑜𝑘 =𝐸𝑃𝑀 ∗𝑀𝐴𝑆𝑆𝐷𝐴𝑌/ ƞ_(𝑐𝑜𝑜𝑘 )
𝐸_𝑖𝑑𝑙𝑒 = 𝑃_𝑖𝑑𝑙𝑒 ∗ 𝑡_𝑖𝑑𝑙𝑒
𝑡_𝑖𝑑𝑙𝑒 = 𝐷𝐴𝑌𝐻𝑅𝑆 −(𝑀𝐴𝑆𝑆𝐷𝐴𝑌/𝐶𝐴𝑃) − (𝑡𝑝𝑟𝑒ℎ𝑒𝑎𝑡/60)

## C_Kitchen_DCV
COMMERCIAL: Demand-Controlled Kitchen Ventilation
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. The updates clarified program criteria and added two savings tiers for demand-controlled kitchen ventilation. Tier 1: The system is used with a variable speed drive on the exhaust fan only. Tier 2: The system is used with variable speed drives on both the exhaust fan and makeup air fan motors.
MEASURE DETAILS
Description
Commercial demand-controlled kitchen ventilation (DCKV) is a demand-based energy management system for a commercial kitchen exhaust hood that minimizes fan energy use by reducing the exhaust and makeup air fan speeds during little or no cooking activity. The DCKV system uses a temperature or an optic sensor (or both sensors) and a microprocessor-based controller in conjunction with variable speed drive on the fan motor to automatically modulate fan speed based on cooking activity. (The temperature sensor detects when a cooking surface is in use and the optic sensor detects the amount of effluent in the air.) Compared to traditional kitchen ventilation systems that operate at 100% ON/OFF, DCKV systems reduce energy consumption by matching ventilation rates to real-time cooking demand. There are two tiers of savings for this measure. Tier 1: The system is used with a variable speed drive on the exhaust fan motor only. Tier 2: The system is used with variable speed drives on both the exhaust fan and makeup air fan motors. The savings do not include the coincident cooling savings associated with reduced makeup air.
Program Criteria
To qualify for a Hawai‘i Energy Commercial DCKV Rebate, the following conditions must be met: 1. The DCKV measure requires the installation of a temperature sensor in the hood exhaust collar or within the hood, or an optic sensor within the hood that senses cooking effluent conditions, or both types of sensors. The sensor(s) must allow for automatically varying the rate of exhaust (and makeup air for Tier 2) by adjusting the fan speeds accordingly. 2. For Tier 1, the DCKV system must be used with a variable speed drive on the exhaust fan motor. 3. For Tier 2, the DCKV system must be used with variable speed drives on the exhaust fan and makeup air fan motors. 4. This measure applies as a retrofit on existing exhaust hoods. For new construction or major renovations, this measure is limited to kitchen systems with ≤ 5,000 cfm of total exhaust airflow. The 2018 IECC with Hawaii State Amendments specifies demand-controlled ventilation as one of three mandatory compliance options for new kitchen systems with a total exhaust airflow of greater than 5,000 cfm. (The alternative options in 2018 IECC are (a) not less than 50% of all replacement air shall be transfer air that would otherwise be exhausted, or (b) listed energy recovery devices with a sensible heat recovery effectiveness of not less than 40% on not less than 50% of the total exhaust airflow.)
Unit of Measure
Exhaust fan horsepower
Baseline Equipment
Commercial kitchen exhaust hood fan with manual ON/OFF switch and magnetic rely or motor starter that operates the exhaust fan at 100% or not at all.
High Efficiency Equipment
Commercial kitchen exhaust hood equipped with temperature and/or optic sensor(s) to control exhaust hood ventilation airflow (and makeup air volume for Tier 2) via variable speed drives on the exhaust fan motor (and makeup air fan motor for Tier 2).
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  |  | Value |  | Unit | Source/Notes
∆kWh/HP |  |  | Annual energy savings per controlled motor horsepower |  |  |  | See Table 1 |  | kWh/hp | California Electronic Technical Reference Manual (eTRM). "Exhaust Hood Demand Controlled Ventilation, Commercial. Measure Characterization." [1]
∆kW/HP |  |  | Peak demand reduction per controlled motor horsepower |  |  |  | See Table 1 |  | kW/ hp | California Electronic Technical Reference Manual (eTRM). "Exhaust Hood Demand Controlled Ventilation, Commercial. Measure Characterization." [2]
HP |  |  | Horsepower of exhaust fan |  |  |  | User input |  | hp | Savings for both tiers are normalized to the rated exhaust fan horsepower.
EUL |  |  | Effective useful life of measure |  |  |  | 15 |  | years | PY22 TRM Commercial Kitchen Demand-Controlled Ventilation Analysis File, "EUL Benchmarking" sheet.
1. The energy savings are based on field meter data from 13 case studies from SCE, PG&E, and ASHRAE.
2. The peak demand reduction was derived from field meter data from four case studies using a peak period definition of 4-9 pm. Because this peak period definition is similar to Hawaii's definition (5-9 pm), the peak demand reduction was not adjusted further for Hawaii.
Table 1. Energy and Peak Demand Impacts [1]
Equipment |  |  |  |  | Baseline |  |  | With DCKV |  |  | Savings
[5 empty] | kW/HP | kWh/HP |  | kW/HP | kWh/HP |  | ∆kW/HP |  | ∆kWh/HP
Exhaust Fan (Tier 1) |  |  |  |  | 0.66106 | 3627.7269 |  | 0.24749 | 1606.2459 |  | 0.41357 |  | 2021.4811
Makeup Air Fan |  |  |  |  | 0.28331 | 1554.7401 |  | 0.10607 | 688.3911 |  | 0.17724 |  | 866.349
Exhaust + Makeup Air Fans (Tier 2) |  |  |  |  | 0.94437 | 5182.467 |  | 0.35356 | 2294.6369 |  | 0.59081 |  | 2887.8301
1. Source: California Electronic Technical Reference Manual (eTRM). "Exhaust Hood Demand Controlled Ventilation, Commercial. Measure Characterization." See spreadsheet for detailed analysis: https://www.caetrm.com/media/reference-documents/SWFS012_Fan_Savings_CZ_Analysis_2023-07-25.xlsx. Note that the values from the California eTRM do not vary by climate zone. Therefore, no adjustments have been made to apply the values to Hawaii's climate.
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
User Input
|  | Horsepower of exhaust fan: | [5 empty] | 1
Measure Name |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  |  |  | Lifetime Savings
Demand-Controlled Kitchen Ventilation (Tier 1) |  |  |  | 0.414 |  |  | 2021.48 |  |  |  |  | 30322.2
Demand-Controlled Kitchen Ventilation (Tier 2) |  |  |  | 0.591 |  |  | 2887.83 |  |  |  |  | 43317.45
Note: Savings shown in blue result from sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Kitchen DCV - Analysis File."
• | AEG's 2022 Analysis File named "PY22 TRM Commercial Kitchen Demand-Controlled Ventilation Analysis File."
• | California Technical Forum. California Electronic Technical Reference Manual (eTRM). "Exhaust Hood Demand Controlled Ventilation, Commercial. Measure Characterization". SWFS012-04. URL: https://www.caetrm.com/measure/SWFS012/04/. Published September 29, 2024.
• | Commercial Checklist. 2018 IECC with State Amendments. Hawaii State Energy Office. URL: https://energy.hawaii.gov/wp-content/uploads/2025/05/Checklist-2018-IECC_State_Commercial_2025-05-12.pdf.
• | Hawaii Energy Code 2018. UpCodes. Section C403.7.5 Kitchen Exhaust Systems (Mandatory). URL: https://up.codes/viewer/hawaii/iecc-2018/chapter/CE_4/ce-commercial-energy-efficiency#C403.7.5.
• | Idaho Power Company Technical Reference Manual 3.1. July 28th, 2021. URL: https://docs.idahopower.com/pdfs/EnergyEfficiency/Reports/2020TRM.pdf.
• | New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs, Residential, Multi-Family, and Commercial/Industrial Measures, Version 9. August 30, 2021. URL: https://www3.dps.ny.gov/W/PSCWeb.nsf/96f0fec0b45a3c6485257688006a701a/72c23decff52920a85257f1100671bdd/$FILE/NYS%20TRM%20V9.pdf.
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Program Version 3.2 FINAL. January 7, 2021. URL: https://mn.gov/commerce-stat/pdfs/20210201_trm_cip_vers3.2.pdf.
• | 2022 Illinois Statewide Technical Reference Manual for Energy Efficiency Version 10.0, Volume 2: Commercial and Industrial Measures FINAL. September 24, 2021. URL: https://ilsag.s3.amazonaws.com/IL-TRM_Effective_010122_v10.0_Vol_2_C_and_I_09242021.pdf.
• | New Jersey Board of Public Utilities, New Jersey's Clean Energy ProgramTM Protocols to Measure Resource Savings, FY2021 Addendum. December 2, 2020. URL: https://www.njcleanenergy.com/files/file/Library/FY21/FY21%20Savings%20Protocols.pdf.
∆𝑘𝑊=∆𝑘𝑊/𝐻𝑃 ∗𝐻𝑃
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊ℎ=∆𝑘𝑊ℎ/𝐻𝑃 ∗𝐻𝑃

## C_Kitchen_Electric Griddle
COMMERCIAL: Electric Griddle
Return to TOC
MEASURE DETAILS
Description
Energy-efficient commercial electric griddles reduce energy consumption primarily through the application of advanced controls and improved temperature uniformity.
Program Criteria
This measure applies to ENERGY STAR or equivalent electric commercial griddles in retrofit and new construction applications. This appliance is designed for cooking food in oil or its own juices by direct contact with either a flat, smooth, hot surface or a hot channeled cooking surface where plate temperature is thermostatically controlled.
Unit of Measure
Per linear foot of cooking surface with assumed depth of 2 feet.
Baseline Equipment
Electric griddle that does not meet ENERGY STAR efficiency requirements.
High Efficiency Equipment
Meets ENERGY STAR efficiency requirements. Requirements apply to single and double-sided griddles.
| Performance Parameters |  |  |  | Requirements
| Heavy-Load Cooking Energy Efficiency |  |  |  | >= 70%
| Idle Energy Rate |  |  |  | <= 320 watts per ft2
ALGORITHMS
ΔE.total |  |  | = E.base - E.he
ΔE.base or ΔE.he |  |  | = E.cook + E.idle + E.preheat
E.cook,total |  |  | = (LBS.food * E.food / η.cook) * DAYS
E.idle,total |  |  | = E.idle * [HRS.daily - (LBS.food / CAP) - (MIN.preheat / 60)] * DAYS
E.preheat,total |  |  | = E.preheat * DAYS
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  |  | Value | Unit | Notes
HRS.daily |  | Daily operating hours |  |  |  | 12 | hrs | FSTC
MIN.preheat |  | Time to preheat |  |  |  | 15 | min | FSTC
E.food |  | ASTM defined energy to food |  |  |  | 0.139 | kWh/lb | FSTC
DAYS |  | Days of operation per year |  |  |  | 365 | days | FSTC
η.cook |  | Cooking energy efficiency |  |  |  | Table | % | FSTC, ENERGY STAR
E.idle |  | Idle energy rate |  |  |  | Table | kW/ft | FSTC, ENERGY STAR
CAP |  | Production capacity |  |  |  | Table | lbs/hr | FSTC
E.preheat |  | Daily preheating energy |  |  |  | Table | kWh/ft | FSTC
LBS.food |  | Food cooked per day |  |  |  | Table | lbs/day | FSTC
CF |  | Coincidence factor |  |  |  | 100 | %
PF |  | Persistance factor |  |  |  | 100 | %
Measure Life |  | Expected duration of energy savings |  |  |  | 12 | years | ENERGY STAR
General assumptions used for deriving deemed electric savings are values taken from the Food Service Technology Center (FSTC) work papers. These deemed values assume that the griddles are 3 x 2 feet in size. Parameters in the table are per linear foot, with an assumed depth of 2 feet.
Parameters |  |  |  |  | Baseline Electric Griddle |  |  | Efficient Electric Griddle
Preheat Energy (E_preheat) |  |  |  |  | 1.33 |  |  | 0.67
Idle Energy Rate (E_idle) |  |  |  |  | 0.8 |  |  | 0.64
Cooking Energy Efficiency (η_cook) |  |  |  |  | 65% |  |  | 70%
Production Capacity (CAP) |  |  |  |  | 11.7 |  |  | 16.33
Lbs of cooked per day, per ft (LBS_food) |  |  |  |  | 33.33 |  |  | 33.33
SAVINGS
Base (kWh/year) per linear foot | [5 empty] | Efficient (kWh/year) per linear foot
Cook |  |  |  | 2601.5347 |  | Cook |  |  | 2415.7108
Idle |  |  |  | 2599.1744 |  | Idle |  |  | 2268.0157
Preheat |  |  |  | 485.45 |  | Preheat |  |  | 244.55
Total Energy Usage |  |  |  | 5686.1591 |  | Total Energy Usage |  |  | 4928.2765
Power Demand |  |  |  | 1.2982 |  | Power Demand |  |  | 1.1252
Measure Name |  |  |  | Peak Demand Savings |  | Annual Energy Savings
Electric Griddle |  |  |  | 0.173 |  | 757.88

## C_Kitchen_Electric Steam Cooker
COMMERCIAL: Electric Steam Cooker
Return to TOC
MEASURE DETAILS
Description
The installation of a qualified ENERGY STAR commercial steam cooker. ENERGY STAR steam cookers save energy during cooling and idle times due to improved cooking efficiency and idle energy rates.
Program Criteria
Meet ENERGY STAR efficiency requirements.
Unit of Measure
Per pan
Baseline Equipment
The Baseline Efficiency case is a conventional electric steam cooker with a cooking energy efficiency of 30%, pan production of 23.3 pounds per hour, and an idle energy rate of 1.2 kW.
High Efficiency Equipment
The High Efficiency case is an ENERGY STAR electric steam cooker with a cooking energy efficiency of 50%, pan production capacity of 16.7 pounds per hour, and an idle energy rate of 0.4 kW.
ALGORITHMS
(See below)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  |  | Value | Unit |  | Notes
HRS_daily |  | Daily operating hours |  |  |  | 12 | hrs |  | FSTC
%_steam |  | Percentage of time in steam mode |  |  |  | 40% | - |  | FSTC
E_food |  | ASTM defined energy to food |  |  |  | 30.8 | Wh/lb |  | FSTC
DAYS |  | Annual days of operation |  |  |  | 365 | days |  | FSTC
η_cook |  | Cooking energy efficiency |  |  |  | Table | - |  | FSTC, ENERGY STAR
E_idle |  | Idle energy rate |  |  |  | Table | W |  | FSTC, ENERGY STAR
CAP |  | Production capacity |  |  |  | Table | lbs/hr |  | FSTC
LBS_food |  | Food cooked per day |  |  |  | 100 | lbs/day |  | FSTC
CF |  | Coincidence factor |  |  |  | 1 | -
Measure Life |  | Expected duration of energy savings |  |  |  | 12 | yrs
SAVINGS
| Average daily operation |  |  |  | 12 | hours |  | Entry for pounds cooked exceeds hourly production capacity. Change production capacity below, or change pounds, number of pans or hours on Inputs tab.
| Annual days of operation |  |  |  | 365 | days
| Food cooked per day |  |  |  | 100 | pounds
| Number of pans per unit |  |  |  | 3
[5 empty] | Conventional | ENERGY STAR
| Type |  |  |  | boiler based | boilerless
| Time in constant steam mode |  |  |  | 40% | 40%
| Cooking energy efficiency |  |  |  | 30% | 50%
| Production capacity per pan |  |  |  | 23.3 | 16.7 |  | pounds/hour/pan
| Idle energy rate |  |  |  | 1200 | 400 |  | W
| ASTM energy to food |  |  |  | 30.8 |  |  | Wh/pound
| Equipment lifetime |  |  |  | 12 |  |  | years
[5 empty] | Conventional | ENERGY STAR
| Annual operation |  |  |  | 4380 |  |  | hours
| Daily pre-heat energy |  |  |  | 1500 | 1500 |  | Wh
| Daily cooking energy |  |  |  | 10266.6667 | 6160 |  | Wh
| Daily idle time |  |  |  | 10.5694 | 10.004 |  | hour
| Daily idle energy |  |  |  | 37950.0104 | 14750.5261 |  | Wh
| Total daily energy |  |  |  | 49716.6771 | 22410.5261 |  | Wh
[5 empty] | Conventional | ENERGY STAR |  | Savings (3-pan)
| Annual Energy Use per Cooker |  |  |  | 18146.5871 | 8179.842 |  | 9966.7451
Measure Name |  |  |  | Peak Demand Savings |  | Annual Energy Savings
Electric Steam Cooker |  |  |  | 0.759 |  | 3322.25
References
| Source: |  | https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator.xlsx
| Equipment specifications: |  | - ENERGY STAR specification
- Food Service Technology Center (FSTC) research on available models, 2009
| Operating Hours: |  | - FSTC research on average use, 2009
| Equipment life: |  | - FSTC research on available models, 2009
Notes on Modifications from Original ENERGY STAR Calculator
Cooking energy efficiency for baseline steam cookers is the average efficiency for steam generator and boiler-based cookers. Idle energy rate for baseline steam cookers is the average rate for steam generator and boiler-based cookers.

## C_Kitchen_Fryer
COMMERCIAL: Fryer
Return to TOC
MEASURE DETAILS
Description
This measure applies to ENERGY STAR or its equivalent electric commercial open-deep fat fryers in retrofit and new construction applications. Commercial fryers consist of a reservoir of cooking oil that allows food to be fully submerged without touching the bottom of the vessel. Electric fryers use a heating element immersed in the cooking oil. High efficiency standard and large vat fryers offer shorter cook times and higher production rates through the use of heat exchanger design. Standby losses are reduced in more efficient models through the use of fry pot insulation.
Program Criteria
Meet ENERGY STAR energy efficiency requirements. ENERGY STAR requirements apply to a standard fryer and a large vat fryer. A standard fryer measures 14 to 18 inches wide with a vat capacity from 25 to 60 pounds. A large vat fryer measures 18 inches to 24 inches wide with a vat capacity greater than 50 pounds.
| Performance Parameters | [5 empty] | Standard Fryer |  |  | Large Vat Fryer
| Heavy-Load Cooking Energy Efficiency | [5 empty] | >= 80% |  |  | >= 80%
| Idle Energy Rate | [5 empty] | <= 1.0 kW |  |  | <= 1.1 kW
Unit of Measure
One fryer
Baseline Equipment
See table below.
High Efficiency Equipment
See table below.
ALGORITHMS
ΔE.total |  |  |  | = E.base - E.he
ΔE.base or ΔE.he |  |  |  | = E.cook + E.idle + E.preheat
E.cook,total |  |  |  | = LBS.food * (E.food / η.cook) * DAYS
E.idle,total |  |  |  | = E.idle * [HRS.daily - (LBS.food / CAP) - (MIN.preheat / 60)] * DAYS
E.preheat,total |  |  |  | = E.preheat * DAYS
DEFINITIONS & ASSUMPTIONS
Variable |  | Description | [5 empty] | Value |  |  | Unit |  | Notes
HRS.daily |  | Daily operating hours | [5 empty] | 12 |  |  | hrs |  | FSTC
MIN.preheat |  | Time to preheat | [5 empty] | 15 |  |  | min |  | FSTC
E.food |  | ASTM defined energy to food | [5 empty] | 0.167 |  |  | kWh/lb |  | FSTC
DAYS |  | Annual days of operation | [5 empty] | 365 |  |  | days |  | FSTC
η.cook |  | Cooking energy efficiency | [5 empty] | Table |  |  | % |  | FSTC, ENERGY STAR
E.idle |  | Idle energy rate | [5 empty] | Table |  |  | kW |  | FSTC, ENERGY STAR
CAP |  | Production capacity | [5 empty] | Table |  |  | lbs/hr |  | FSTC
E.preheat |  | Preheating energy | [5 empty] | Table |  |  | kWh/day |  | FSTC
LBS.food |  | Food cooked per day | [5 empty] | Table |  |  | lbs/day |  | FSTC
CF |  | Coincidence factor | [5 empty] | 100 |  |  | %
PF |  | Persistance factor | [5 empty] | 100 |  |  | %
Measure Life |  | Expected duration of energy savings | [5 empty] | 12 |  |  | yrs
General assumptions used for deriving deemed electric savings are values taken from the Food Service Technology Center (FSTC) work papers.
Parameters | [6 empty] | Baseline Electric Fryer |  |  |  |  | Efficient Electric Fryer
[7 empty] | Standard |  | Large Vat |  |  | Standard |  |  | Large Vat
Preheat Energy (E_preheat) | [6 empty] | 2.3 |  | 2.5 |  |  | 1.7 |  |  | 2.1
Idle Energy Rate (E_idle) | [6 empty] | 1.05 |  | 1.35 |  |  | 1 |  |  | 1.1
Cooking Energy Efficiency (η_cook) | [6 empty] | 75% |  | 70% |  |  | 80% |  |  | 80%
Production Capacity per ft (CAP) | [6 empty] | 65 |  | 100 |  |  | 70 |  |  | 110
Lbs of food cooked per day, per ft (LBS_food) | [6 empty] | 150 |  | 150 |  |  | 150 |  |  | 150
SAVINGS
Baseline Fryer |  |  | Standard |  |  | Large Vat |  |  | Efficient Fryer |  |  |  |  | Standard |  | Large Vat
Cook |  |  | 12191 |  |  | 13061.7857 |  |  | Cook |  |  |  |  | 11429.0625 |  | 11429.0625
Idle |  |  | 3618.7644 |  |  | 5050.6875 |  |  | Idle |  |  |  |  | 3506.6071 |  | 4170.125
Preheat |  |  | 839.5 |  |  | 912.5 |  |  | Preheat |  |  |  |  | 620.5 |  | 766.5
Total Base Energy |  |  | 16649.2644 |  |  | 19024.9732 |  |  | Total Base Energy |  |  |  |  | 15556.1696 |  | 16365.6875
Power Demand |  |  | 3.8012 |  |  | 4.3436 |  |  | Power Demand |  |  |  |  | 3.5516 |  | 3.7365
Measure Name |  |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings
Standard Electric Fryer |  |  |  |  | 0.25 |  |  | 1093.09
Large Vat Electric Fryer |  |  |  |  | 0.607 |  |  | 2659.29

## C_Kitchen_HF Holding Cabinet
COMMERCIAL: Hot Food Holding Cabinet
Return to TOC
MEASURE DETAILS
Description
Commercial insulated hot food holding cabinet models that meet program requirements incorporate better insulation, reducing heat loss, and may also offer additional energy saving devices such as magnetic door electric gaskets, auto-door closures, or dutch doors. The insulation of the cabinet also offers better temperature uniformity within the cabinet from top to bottom. This means that qualified hot food holding cabinets are more efficient at maintaining food temperature while using less energy.
Program Criteria
• Full-size holding cabinets are defined as any holding cabinet with an internal measured volume of greater than or equal to 15 cubic feet (≥15 ft.3). This measure does not include cook-and-hold equipment. All measures must be electric hot food holding cabinets that are fully insulated and have doors. Qualifying cabinets must not exceed the maximum idle energy rate of 20 Watts per cubic foot in accordance with the ASTM Standard test method. • Half-size holding cabinets are defined as any holding cabinet with an internal measured volume of less than 15 cubic feet (<15 ft.3). This measure does not include cook-and-hold or retherm equipment. All measures must be electric hot food holding cabinets that are fully insulated and have doors. Qualifying cabinets must not exceed the maximum idle energy rate of 20 Watts per cubic foot in accordance with the ASTM Standard test method.
Unit of Measure
Per cabinet
Baseline Equipment
The baseline equipment is assumed to be a standard hot food holding cabinet with an idle energy rate of 40 watts per cubic foot.
High Efficiency Equipment
The efficient equipment is assumed to be an ENERGY STAR qualified hot food holding cabinet with an idle energy rate of 20 watts per cubic foot.
ALGORITHMS
ΔkWh |  |  |  | = HRS.daily * DAYS * (kW.bs - kW.he)
ΔkW |  |  |  | = (kW.bs - kW.he) * CF
DEFINITIONS & ASSUMPTIONS
Variable |  | Description | [5 empty] | Value |  | Unit | Notes
kW.bs |  | Baseline equipment demand | [5 empty] | See below |  | kW
kW.he |  | High efficiency equipment demand | [5 empty] | See below |  | kW
HRS_daily |  | Daily hours of operation | [5 empty] | 15 |  | hrs
DAYS |  | Annual days of operation | [5 empty] | 365 |  | days
CF |  | Coincidence factor | [5 empty] | 100 |  | %
Measure Life |  | Expected duration of energy savings | [5 empty] | 12 |  | yrs
SAVINGS
Energy usage calculations are based on 15 hours a day, 365 days per year operation at a typical temperature setting of 150°F. The different sizes for the holding cabinets (half size and full size) have proportional operating energy rates. Operating energy rate for the full size holding cabinets was obtained in accordance with the ASTM Standard. The energy savings calculations listed in the following tables use Title 20 (California) as the baseline for potential energy savings requiring all hot food holding cabinets sold in California to meet a normalized idle energy rate of 40 Watts/ft³.
Performance |  |  |  |  | Full-Size |  |  |  | Half-Size
[5 empty] | Baseline |  | High Efficiency |  | Baseline |  |  | High Efficiency
Power Demand |  |  |  |  | 1 |  | 0.28 |  | 0.38 |  |  | 0.05
Annual Energy Use |  |  |  |  | 5475 |  | 1533 |  | 2080.5 |  |  | 273.75
Power Demand Reduction |  |  |  |  | 0.72 |  |  |  | 0.33
Annual Energy Reduction |  |  |  |  | 3942 |  |  |  | 1806.75
The demand reduction estimation is based on measured data for standard efficiency insulated holding cabinets and for high-efficiency insulated holding cabinets. The measured data are derived from tests conducted under ASTM Standard Test Method for the Performance of Hot Food Holding Cabinets.
Cabinet Size |  |  | Cabinet Volume |  |  | Normalized Idle Energy Rate |  |  |  | Total Idle Energy Rate
Full-Size |  |  | 25 |  |  | 11.3 |  |  |  | 0.28
Half-Size |  |  | 10 |  |  | 5.7 |  |  |  | 0.05
Measure Name |  |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings
Full-Size Cabinet |  |  |  |  | 0.72 |  |  | 3942
Half-Size Cabinet |  |  |  |  | 0.33 |  |  | 1806.75

## C_Kitchen_Ice Machine
COMMERCIAL: Ice Machine
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the PY25 TRM.
MEASURE DETAILS
Description
This measure relates to installing a new air cooled, automatic commercial ice machine meeting ENERGY STAR efficiency standards. Automatic commercial ice machines are factory-made assemblies consisting of a condensing unit and an ice making section operating as an integrated unit for making and harvesting ice. They can be of the batch type with alternating freezing and harvesting periods or the continuous type with continual freezing and harvesting of ice simultaneously. The measure applies to energy efficient air-cooled ice machines, both batch and continuous types. Commercial automatic ice machines are categorized into three equipment types: ice maker heads (IMH), remote condensing units (TCUs), and self contained units (SCUs). ENERGY STAR batch type and continuous type ice machines are about 10% and 16% more energy efficient than standard models.
Program Criteria
This incentive applies to purchasing new or replacement with high efficiency air-cooled batch and continuous type ice machines of the following design types: ice making heads (IMHs), remote condensing units (RCUs), and self-contained units (SCUs). The high efficiency ice machines must meet or exceed the ENERGY STAR product criteria. Water cooled ice machines, ice machines with ice and water dispensing systems, and air cooled RCUs designed only for connection to remote track compressors are ineligible. Any commercial building type is eligible.
Unit of Measure
One ice machine
Baseline Equipment
For this characterization to apply, the baseline equipment is assumed to be a commercial ice machine meeting the federal standards published in 10 CFR 431.136, with an ice harvest rate capacity between 50 and 4000 pounds per 24 hour period. See Tables 1 and 2 below.
High Efficiency Equipment
For this characterization to apply, the high efficiency equipment is assumed to be a commercial ice machine meeting or exceeding the ENERGY STAR Version 3.0 key product criteria, with an ice harvest rate capacity between 50 and 4000 pounds per 24 hour period. See Tables 1 and 2 below.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  |  |  | Value | Unit |  | Source/Notes
EBaseline,100lb |  | Baseline equipment energy usage per 100 lbs of ice |  |  |  |  | Table 3 | kWh |  | Calculated
EHE,100lb |  | High efficiency equipment energy usage per 100 lbs of ice |  |  |  |  | Table 3 | kWh |  | Calculated
DC |  | Duty cycle of ice machine |  |  |  |  | 75% |  |  | ENERGY STAR CFS Calculator
H |  | Ice harvest rate |  |  |  |  | Tables 1, 2 & 3 | lbs/24 hrs
DAYS |  | Annual days of operation |  |  |  |  | 365 | days
HRS |  | Annual operating hours |  |  |  |  | 6570 | hrs |  | 365 days * 0.75 *24 hrs
CF |  | Coincidence factor |  |  |  |  | 90% |  |  | 2004-2005 DEER Update Study1
EUL |  | Effective useful life of measure |  |  |  |  | 10 | yrs |  | PY23 TRM Commercial Kitchen Ice Machine Analysis File, "EUL Benchmarking" sheet
Notes:
1. The commercial kitchen ice machine measure is assumed to operate within the California DEER peak period of 4-9 pm on weekdays at a constant load throughout the day. Hawaii's peak period is 5-9 pm non-holiday weekdays (year-round), similar to California's peak period of 4-9 pm on weekdays. As such, a CF of 0.90 is appropriate to use for Hawaii. The CF value should be updated with Hawaii-specific load shape analysis in the future.
Table 1. ENERGY STAR Requirements and Federal Minimum Standards for Air Cooled Batch Type Ice Machines
Equipment Type |  |  |  | Ice Harvest Rate (H) (lbs ice/24 hrs) |  | Daily Energy Use Rate (kWh/100 lbs) |  | Potable Water Use (gal/100 lbs ice) |  |  | Federal Minimum Standard Energy Use Rate (kWh/100 lbs)
Ice Maker Heads (IMH) |  |  |  | H < 300 |  | ≤ 9.20 - 0.01134*H |  | ≤ 20.0 |  |  | 10 - 0.01233*H
|  |  |  | 300 ≤ H < 800 |  | ≤ 6.49 - 0.0023*H |  |  |  |  | 7.05 - 0.0025*H
|  |  |  | 800 ≤ H < 1500 |  | ≤ 5.11 - 0.00058*H |  |  |  |  | 5.55 - 0.00063*H
|  |  |  | 1500 ≤ H < 4000 |  | ≤ 4.24 |  |  |  |  | 4.61
Remote Condensing Unit (RCU) but not Remote Compressor |  |  |  | H < 988 |  | ≤ 7.17 - 0.00308*H |  | ≤ 20 |  |  | 7.97 - 0.00342*H
|  |  |  | 988 ≤ H < 4000 |  | ≤ 4.13 |  |  |  |  | 4.59
Self-Contained Units (SCU) |  |  |  | < 110 |  | ≤ 12.57 - 0.0399*H |  | ≤ 25 |  |  | 14.79 - 0.0469*H
|  |  |  | 110 ≤ H < 200 |  | ≤ 10.56 - 0.0215*H |  |  |  |  | 12.42 - 0.02533*H
|  |  |  | 200 ≤ H < 4000 |  | ≤ 6.25 |  |  |  |  | 7.35
Table 2. ENERGY STAR Requirements and Federal Minimum Standards for Air Cooled Continuous Type Ice Machines
Equipment Type |  |  |  | Ice Harvest Rate (H) (lbs ice/24 hrs) |  | Daily Energy Use Rate (kWh/100 lbs) |  | Potable Water Use (gal/100 lbs ice) |  |  | Federal Minimum Standard Energy Use Rate (kWh/100 lbs)
Ice Maker Heads (IMH) |  |  |  | H < 310 |  | ≤ 7.90 - 0.005409*H |  | ≤ 15.0 |  |  | 9.19 - 0.00629*H
|  |  |  | 310 ≤ H < 820 |  | ≤ 7.08 - 0.002752*H |  |  |  |  | 8.23 - 0.0032*H
|  |  |  | 820 ≤ H < 4000 |  | ≤ 4.82 |  |  |  |  | 5.61
Remote Condensing Unit (RCU) but not Remote Compressor |  |  |  | H < 800 |  | ≤ 7.76 - 0.00464*H |  | ≤ 15.0 |  |  | 9.7 - 0.0058*H
|  |  |  | 800 ≤ H < 4000 |  | ≤ 4.05 |  |  |  |  | 5.06
Self-Contained Units (SCU) |  |  |  | H < 200 |  | ≤ 12.37 - 0.0261*H |  | ≤ 15.0 |  |  | 14.22 - 0.03*H
|  |  |  | 200 ≤ H < 700 |  | ≤ 8.24 - 0.005429*H |  |  |  |  | 9.47 - 0.00624*H
|  |  |  | 700 ≤ H < 4000 |  | ≤ 4.44 |  |  |  |  | 5.1
SAVINGS
Table 3. Summary of Savings Calculations
Air-Cooled Ice Machine, Batch Operation
Measure Name |  |  | H (lbs ice/ 24 hrs) | Energy Use per 100 lbs (kWh/100 lbs) |  |  | Daily Energy Use (kWh) |  |  |  | Annual Energy Use (kWh)
|  |  |  | Baseline | High Eff |  | Baseline |  | High Eff |  | Baseline | High Eff
IMH Batch, H < 300 |  |  | 150 | 8.15 | 7.5 |  | 9.1687 |  | 8.4375 |  | 3346.5937 | 3079.6875
IMH Batch, 300 ≤ H < 800 |  |  | 550 | 5.68 | 5.225 |  | 23.43 |  | 21.5531 |  | 8551.95 | 7866.8906
IMH Batch, 800 ≤ H < 1500 |  |  | 1150 | 4.83 | 4.443 |  | 41.6587 |  | 38.3209 |  | 15205.4437 | 13987.1194
IMH Batch, 1500 ≤ H < 4000 |  |  | 2750 | 4.61 | 4.24 |  | 95.0813 |  | 87.45 |  | 34704.6563 | 31919.25
RCU Batch, H < 988 |  |  | 494 | 6.28 | 5.6485 |  | 23.2674 |  | 20.9276 |  | 8492.601 | 7638.5807
RCU Batch, 988 ≤ H < 4000 |  |  | 2494 | 4.59 | 4.13 |  | 85.8559 |  | 77.2516 |  | 31337.4217 | 28196.8522
SCU Batch, H < 110 |  |  | 55 | 12.21 | 10.3755 |  | 5.0366 |  | 4.2799 |  | 1838.3681 | 1562.1612
SCU Batch, 110 ≤ H < 200 |  |  | 155 | 8.49 | 7.2275 |  | 9.8696 |  | 8.402 |  | 3602.4131 | 3066.7186
SCU Batch, 200 ≤ H < 4000 |  |  | 2100 | 7.35 | 6.25 |  | 115.7625 |  | 98.4375 |  | 42253.3125 | 35929.6875
Air-Cooled Ice Machine, Continuous Operation
Measure Name |  |  | H (lbs ice/ 24 hrs) | Energy Use per 100 lbs (kWh/100 lbs) |  |  | Daily Energy Use (kWh) |  |  |  | Annual Energy Use (kWh)
|  |  |  | Baseline | High Eff |  | Baseline |  | High Eff |  | Baseline | High Eff
IMH Continuous, H < 310 |  |  | 155 | 8.22 | 7.06 |  | 9.5558 |  | 8.2073 |  | 3487.8488 | 2995.6463
IMH Continuous, 310 ≤ H < 820 |  |  | 565 | 6.42 | 5.53 |  | 27.2048 |  | 23.4334 |  | 9929.7337 | 8553.1819
IMH Continuous, 820 ≤ H < 4000 |  |  | 2410 | 5.61 | 4.82 |  | 101.4008 |  | 87.1215 |  | 37011.2738 | 31799.3475
RCU Continuous, H < 800 |  |  | 400 | 7.38 | 5.9 |  | 22.14 |  | 17.7 |  | 8081.1 | 6460.5
RCU Continuous, 800 ≤ H < 4000 |  |  | 2400 | 5.06 | 4.05 |  | 91.08 |  | 72.9 |  | 33244.2 | 26608.5
SCU Continuous, H < 200 |  |  | 100 | 11.22 | 9.76 |  | 8.415 |  | 7.32 |  | 3071.475 | 2671.8
SCU Continuous, 200 ≤ H < 700 |  |  | 450 | 6.66 | 5.8 |  | 22.4775 |  | 19.575 |  | 8204.2875 | 7144.875
SCU Continuous, 700 ≤ H < 4000 |  |  | 2350 | 5.1 | 4.44 |  | 89.8875 |  | 78.255 |  | 32808.9375 | 28563.075
Measure Name |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  |  | Lifetime Energy Savings
IMH Batch, H < 300 |  |  |  | 0.037 |  |  | 266.91 |  |  |  | 2669.1
IMH Batch, 300 ≤ H < 800 |  |  |  | 0.094 |  |  | 685.06 |  |  |  | 6850.6
IMH Batch, 800 ≤ H < 1500 |  |  |  | 0.167 |  |  | 1218.32 |  |  |  | 12183.2
IMH Batch, 1500 ≤ H < 4000 |  |  |  | 0.382 |  |  | 2785.41 |  |  |  | 27854.1
RCU Batch, H < 988 |  |  |  | 0.117 |  |  | 854.02 |  |  |  | 8540.2
RCU Batch, 988 ≤ H < 4000 |  |  |  | 0.43 |  |  | 3140.57 |  |  |  | 31405.7
SCU Batch, H < 110 |  |  |  | 0.038 |  |  | 276.21 |  |  |  | 2762.1
SCU Batch, 110 ≤ H < 200 |  |  |  | 0.073 |  |  | 535.69 |  |  |  | 5356.9
SCU Batch, 200 ≤ H < 4000 |  |  |  | 0.866 |  |  | 6323.62 |  |  |  | 63236.2
IMH Continuous, H < 310 |  |  |  | 0.067 |  |  | 492.2 |  |  |  | 4922
IMH Continuous, 310 ≤ H < 820 |  |  |  | 0.189 |  |  | 1376.55 |  |  |  | 13765.5
IMH Continuous, 820 ≤ H < 4000 |  |  |  | 0.714 |  |  | 5211.93 |  |  |  | 52119.3
RCU Continuous, H < 800 |  |  |  | 0.222 |  |  | 1620.6 |  |  |  | 16206
RCU Continuous, 800 ≤ H < 4000 |  |  |  | 0.909 |  |  | 6635.7 |  |  |  | 66357
SCU Continuous, H < 200 |  |  |  | 0.055 |  |  | 399.68 |  |  |  | 3996.8
SCU Continuous, 200 ≤ H < 700 |  |  |  | 0.145 |  |  | 1059.41 |  |  |  | 10594.1
SCU Continuous, 700 ≤ H < 4000 |  |  |  | 0.582 |  |  | 4245.86 |  |  |  | 42458.6
RESOURCES
• | ICF's 2025 Analysis File named "PY25 TRM - Commercial Kitchen Ice Machine - Analysis File."
• | AEG's analysis file titled "PY23 TRM Commercial Kitchen Ice Machine Analysis File."
• | Code of Federal Regulations at 10 CFR 431.66. URL: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-H?toc=1.
• | ENERGY STAR. 2023. "ENERGY STAR® Program Requirements Product Specification for Commercial Ice Machines - Eligibility Criteria Version 3.0." Effective on January 28, 2018. URL: https://www.energystar.gov/sites/default/files/Final%20V3.0%20ACIM%20Specification%205-17-17_1_0.pdf
• | US EPA and US DOE. ENERGY STAR Savings Calculator for ENERGY STAR Commercial Food Service (CFS) Products. June 7, 2021. URL: https://www.energystar.gov/sites/default/files/asset/document/CFS_calculator_07-15-2021.xlsx
• | California eTRM. Ice Machine, Commercial. SWFS006-02. January 19, 2023. URL: https://www.caetrm.com/measure/SWFS006/02/
• | Itron, Inc. 2005-2005 Database for Energy Efficiency Resources (DEER) Update Study. Final Report. Prepared for Southern California Edison. December 2005. Table 3-14, p. 3-17.
• | California Technical Forum. 2023. "CPUC Support Tables. Effective Useful Life and Remaining Useful Life." URL: https://www.caetrm.com/cpuc/table/effusefullife/. February 1, 2023.
• | 2023 Illinois Statewide Technical Reference Manual for Energy Efficiency Version 11.0, Volume 2: Commercial and Industrial Measures FINAL. September 22, 2022.
• | Texas Technical Reference Manual Version 10.0, Volume 3: Nonresidential Measures. Program Years 2023. November 2022.
• | New Jersey Board of Public Utilities, New Jersey's Clean Energy ProgramTM Protocols to Measure Resource Savings, FY2020. July 20, 2019, page 145.
• | New Jersey Board of Public Utilities, New Jersey's Clean Energy ProgramTM Protocols to Measure Resource Savings, FY2021 Addendum. December 2, 2020.
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Program Version 3.3 FINAL. January 31, 2021.
∆𝑘𝑊= ∆𝑘𝑊ℎ∗𝐶𝐹/𝐻𝑅𝑆
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊ℎ=(〖(𝐸〗_(𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒,100𝑙𝑏) − 𝐸_(𝐻𝐸,100𝑙𝑏)))/100∗𝐷𝐶 ∗𝐻∗𝐷𝐴𝑌𝑆

## C_Kitchen_LF Spray Nozzle
COMMERCIAL: Low-Flow Spray Nozzle
Return to TOC
UPDATE STATUS
Updated in Winter 2022-2023 for the PY23 TRM.
MEASURE DETAILS
Description
All pre-rinse valves use a spray of water to remove food waste from dishes prior to cleaning the dishes in a dishwasher. They reduce water consumption, water heating cost, and wastewater (sewer) charges. Pre-rinse spray valves include a nozzle, squeeze lever, and dish guard bumper. Energy savings depend on the facility type and the facility’s method of water heating (electric resistance or heat pump). The spray valves usually have a clip to lock the handle in the “on” position. Pre-rinse valves are inexpensive and easily interchangeable with different manufacturers’ assemblies.
Program Criteria
The facility must use electric water heating for this measure to be eligible. The flowrate of the new low-flow pre-rinse spray valve must be at least 10% less than required by the Federal Standards that have been in effect since Jan. 28, 2019. Table 1 shows the Federal Standards. Class 1, 2, and 3 products are eligible for rebates.
Table 1. Federal Standards for Commercial Pre-rinse Spray Valves. Effective as of Jan. 28, 2019.1
| Product Class (spray force in ounce-force, ozf) |  |  |  |  | Flowrate (gallons per minute, gpm)
| Product Class 1 (≤5.0 ozf) |  |  |  |  | 1
| Product Class 2 (>5.0 ozf and ≤8.0 ozf) |  |  |  |  | 1.2
| Product Class 3 (>8.0 ozf) |  |  |  |  | 1.28
Note:
1. Federal Energy Conservation Standard, Code of Federal Regulations, Title 10, Chapter 22, Subchapter D, Part 431, Subpart O, Section §431.266. Available here: <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-O#431.266>, accessed Jan. 31, 2023.
Unit of Measure
One spray valve.
Baseline Equipment
The baseline equipment is assumed to be a pre-rinse spray valve with a flowrate of 1.2 gpm, consistent with the Federal Standard for Class 2 products with a spray force of >5.0 ozf and ≤8.0 ozf (see Table 1 above). However, Class 1 and Class 3 products are also eligible for rebates.
High Efficiency Equipment
The efficient equipment is assumed to be a pre-rinse spray valve with a flowrate of 1.07 gpm. This is a commonly available flowrate for Class 2 products and represents savings of 10.8% relative to the baseline.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Value |  | Unit | Source/Notes
GPMBase |  | Flowrate of the baseline pre-rinse spray valve |  |  | 1.2 |  | gpm | Based on Federal Standards as of Jan. 28, 2019. This value is the maximum flowrate for Class 2 products with a spray force of >5.0 ozf and ≤8.0 ozf. (See Table 1 above.)
GPMEE |  | Flowrate of the low-flow pre-rinse spray valve |  |  | 1.07 |  | gpm | This is a commonly available flowrate for Class 2 products and represents savings of 10.8% relative to the baseline.
Minday |  | Daily operating minutes of the pre-rinse spray valve |  |  | 120 |  | min/day | Consistent with benchmarking.1
Dayyear |  | Annual days of operation |  |  | See Table 2 |  | day/year | Consistent with Hawaii Baseline Study data and benchmarking.1,2
ρ |  | Density of water |  |  | 8.3 |  | lbm/gal | -
cp |  | Specific heat capacity of water |  |  | 1 |  | Btu/lbm°F | -
Tmix |  | Hot/cold mixed water temperature |  |  | 114.1 |  | °F | California eTRM.3
Tsupply |  | Supply water temperature |  |  | 75 |  | °F | Hawai'i Energy.4
UEF |  | Water heater uniform energy factor |  |  | See Table 2 |  | - | Derived from mean water heater tank capacities from Hawaii Baseline Study and minimum Federal standards for water heater UEFs.1,2,5
Constant |  | Factor to convert BTU to kWh |  |  | 3412 |  | Btu/kWh | -
CF |  | Peak demand coincidence factor from load shape analysis |  |  | 0.74 |  | - | AEG's 2018 Hawaii-specific analysis of U.S. DOE OpenEI Load shapes for Commercial Water Heating; peak period defined as non-holiday weekdays from 5-9 pm. Building type: Restaurant.6
EFLH |  | Equivalent full load hours of water heater operation from load shape analysis |  |  | 3947 |  | hrs | AEG's 2018 Hawaii-specific analysis of U.S. DOE OpenEI Load shapes for Commercial Water Heating. Building type: Restaurant.6
EULEE |  | Effective useful life of measure |  |  | 5 |  | yrs | See Note 7.
Notes:
1. See AEG's 2023 Analysis File named "PY23 TRM - Commercial Low-Flow Spray Nozzle."
2. Evergreen Economics, Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, Feb. 26, 2014, Appendices, Table E.2.1 and Table E.2.2.
3. California eTRM, Low-Flow Pre-Rinse Spray Valve, Food Service, SWFS013-02, effective Jan. 1, 2023, available here: <https://www.caetrm.com/measure/SWFS013/02/>. The California eTRM cites field data from: Tso, B and J. Koeller. 2005. Pre- Rinse Spray Valves Programs: How are they Really Doing? Bellevue (WA): SBW Consulting.
4. Hawai‘i Energy Solar Water Heating Program Handbook, Table 2, for Hawaii and Honolulu counties. (Maui county average temperature is 71 °F).
5. Electronic Code of Federal Regulations: Title 10: Energy, Part 430 - Energy Conservation Program for Consumer Products. Subpart C - Energy and Water Conservation Standards. Section 6d. <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>.
6. Refer to AEG's analysis file named "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays."
7. Energy Efficiency and Renewable Energy Office, 2021-08-18 Energy Conservation Program: Energy Conservation Standards for Commercial Prerinse Spray Valves; Notification of proposed determination and request for comment, Aug 17, 2021, Table IV.10—Summary of Inputs and Methods for the LCC and PBP Analysis, available here: <https://www.regulations.gov/document/EERE-2019-BT-STD-0034-0012>, accessed Feb. 1, 2023.
Table 2. Values for Key Parameters1
Building Type |  |  | Dayyear | Federal Standard Electric Resistance Water Heater UEF |  |  | Federal Standard Heat Pump Water Heater UEF
Restaurants/Institutions |  |  | 365 | 0.93 |  |  | 2.18
Dormitories |  |  | 274 | 0.93 |  |  | 2.11
K-12 Schools |  |  | 200 | 0.93 |  |  | 2.11
Note:
1. For derivation of the values in Table 2, see AEG's 2023 Analysis File named "PY23 TRM - Commercial Low-Flow Spray Nozzle," sheet named "Hawaii Data."
SAVINGS
Measure Name |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Electric Resistance, Restaurants/ Institutions |  |  | 0.109 |  | 582.34 |  |  | 2911.7
Electric Resistance, Dormitories |  |  | 0.082 |  | 437.16 |  |  | 2185.8
Electric Resistance, K-12 Schools |  |  | 0.06 |  | 319.09 |  |  | 1595.45
Heat Pump, Restaurants/ Institutions |  |  | 0.047 |  | 248.43 |  |  | 1242.15
Heat Pump, Dormitories |  |  | 0.036 |  | 192.68 |  |  | 963.4
Heat Pump, K-12 Schools |  |  | 0.026 |  | 140.64 |  |  | 703.2
RESOURCES
• | AEG's 2023 Analysis File named "PY23 TRM - Commercial Low-Flow Spray Nozzle."
• | AEG's analysis file named "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays."
• | California eTRM, Low-Flow Pre-Rinse Spray Valve, Food Service, SWFS013-02, effective Jan. 1, 2023, available here: <https://www.caetrm.com/measure/SWFS013/02/>.
• | Electronic Code of Federal Regulations: Title 10: Energy, Part 430 - Energy Conservation Program for Consumer Products. Subpart C - Energy and Water Conservation Standards. Section 6d. <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>.
• | Energy Efficiency and Renewable Energy Office, 2021-08-18 Energy Conservation Program: Energy Conservation Standards for Commercial Prerinse Spray Valves; Notification of proposed determination and request for comment, Aug 17, 2021, Table IV.10—Summary of Inputs and Methods for the LCC and PBP Analysis, available here: <https://www.regulations.gov/document/EERE-2019-BT-STD-0034-0012>, accessed Feb. 1, 2023.
• | Evergreen Economics, Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, Feb. 26, 2014, Appendices, Table E.2.1 and Table E.2.2.
• | Federal Energy Conservation Standard, Code of Federal Regulations, Title 10, Chapter 22, Subchapter D, Part 431, Subpart O, Section §431.266. Available here: <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-O#431.266>, accessed Jan. 31, 2023.
• | Hawai‘i Energy Solar Water Heating Program Handbook
• | Maryland/Mid-Atlantic Technical Reference Manual, Version 10, Prepared by Shelter Analytics, Facilitated and Managed by Northeast Energy Efficiency Partnerships, March 2020.
• | New York State Joint Utilities, New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs – Residential, Multi-Family, and Commercial/Industrial Measures, Version 10, Effective Date - Jan. 1, 2023.
• | Public Utility Commission of Texas, Texas Technical Reference Manual, Version 10.0, Volume 2: Residential Measures, Program Year 2023.
• | Tso, B and J. Koeller. 2005. Pre- Rinse Spray Valves Programs: How are they Really Doing? Bellevue (WA): SBW Consulting.
• | 2023 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 11.0, Volume 2: Commercial and Industrial Measures, FINAL, September 22, 2022. Effective: January 1, 2023.
∆𝑘𝑊ℎ=((〖𝐺𝑃𝑀〗_𝐵𝑎𝑠𝑒−〖𝐺𝑃𝑀〗_𝐸𝐸 )∗〖𝑀𝑖𝑛〗_𝑑𝑎𝑦∗〖𝐷𝑎𝑦〗_𝑦𝑒𝑎𝑟∗𝜌∗𝑐_𝑝∗(𝑇_𝑚𝑖𝑥−𝑇_𝑠𝑢𝑝𝑝𝑙𝑦 ))/(𝑈𝐸𝐹∗(3412 𝐵𝑡𝑢/𝑘𝑊ℎ) )
∆𝑘𝑊=∆𝑘𝑊ℎ/𝐸𝐹𝐿𝐻∗𝐶𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## C_Kitchen_Freezer
COMMERCIAL: Freezer
Return to TOC
UPDATE STATUS
Updated in Winter 2022-2023 for PY23 TRM.
MEASURE DETAILS
Description
This measure relates to the installation of a new self-contained, reach-in commercial freezer with a door meeting ENERGY STAR efficiency standards. ENERGY STAR labeled commercial freezers are more energy efficient because they are designed with components such as ECM evaporator and condenser fan motors, hot gas anti-sweat heaters, or high-efficiency compressors, which will significantly reduce energy consumption. Commercial freezers are typically larger, more versatile, and robust than residential freezers. This measure is applicable to commercial freezers, only. It is not applicable to residential freezers operating in commercial buildings.
Program Criteria
This measure could relate to the replacing of an existing unit at the end of its useful life, or the installation of a new system in a new or existing building.
Unit of Measure
One freezer
Baseline Equipment
For this characterization to apply, the baseline equipment is assumed to be a solid or glass door freezer, closing either vertically or horizontally, meeting the minimum federal manufacturing standards. The volume for the baseline is assumed to be the average of the range. For example, if the range is 0 to 15, the average volume is 7.5.
High Efficiency Equipment
For this characterization to apply, the efficient equipment is assumed to be a solid or glass door freezer meeting the minimum ENERGY STAR efficiency level standards.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  |  |  | Value |  | Unit | Notes
EBaseline |  | Baseline equipment daily energy usage |  |  |  |  | See Table 1 |  | kWh/day | Code of Federal Regulations at 10 CFR 431.66
EHE |  | High efficiency equipment daily energy usage |  |  |  |  | See Table 1 |  | kWh/day | ENERGY STAR Version 5.0
DAYS |  | Annual days of operation |  |  |  |  | 365 |  | days
HRS |  | Annual operating hours |  |  |  |  | 8760 |  | hrs
CF |  | Coincidence factor |  |  |  |  | 1 |  | -
EUL |  | Estimated useful life of measure |  |  |  |  | 12 |  | yrs | PY23 TRM Commercial Kitchen Freezer Analysis File, "EUL Benchmarking" sheet
SAVINGS
Table 1. Summary of Savings Calculations
Volume |  | Typical Volume | Volumetric Factor (kWh/ft3) |  |  | Fixed Energy (kWh) |  | Adjusted Energy (kWh/day) |  |  |  | Energy Savings (kWh/yr) | Demand Savings (kW)
|  |  | Base |  | Efficient | Base | Efficient | Base |  | Efficient
Vertical Closed
Solid Door
0 < V < 15 |  | 7.5 | 0.22 |  | 0.21 | 1.38 | 0.9 | 3.03 |  | 2.475 |  | 202.575 | 0.023125
15 ≤ V < 30 |  | 22.5 | 0.22 |  | 0.12 | 1.38 | 2.248 | 6.33 |  | 4.948 |  | 504.43 | 0.057583
30 ≤ V < 50 |  | 40 | 0.22 |  | 0.2578 | 1.38 | -1.8864 | 10.18 |  | 8.4256 |  | 640.356 | 0.0731
50 ≤ V |  | 60 | 0.22 |  | 0.14 | 1.38 | 4.4 | 14.58 |  | 12.8 |  | 649.7 | 0.074167
Glass Door
0 < V < 15 |  | 7.5 | 0.29 |  | 0.232 | 2.95 | 2.36 | 5.125 |  | 4.1 |  | 374.125 | 0.042708
15 ≤ V < 30 |  | 22.5 | 0.29 |  | 0.232 | 2.95 | 2.36 | 9.475 |  | 7.58 |  | 691.675 | 0.078958
30 ≤ V < 50 |  | 40 | 0.29 |  | 0.232 | 2.95 | 2.36 | 14.55 |  | 11.64 |  | 1062.15 | 0.12125
50 ≤ V |  | 60 | 0.29 |  | 0.232 | 2.95 | 2.36 | 20.35 |  | 16.28 |  | 1485.55 | 0.16958
Horizontal Closed
Solid Door
0 < V < 15 |  | 7.5 | 0.06 |  | 0.057 | 1.12 | 0.55 | 1.57 |  | 0.9775 |  | 216.2625 | 0.024688
15 ≤ V < 30 |  | 22.5 | 0.06 |  | 0.057 | 1.12 | 0.55 | 2.47 |  | 1.8325 |  | 232.6875 | 0.026562
30 ≤ V < 50 |  | 40 | 0.06 |  | 0.057 | 1.12 | 0.55 | 3.52 |  | 2.83 |  | 251.85 | 0.02875
50 ≤ V |  | 60 | 0.06 |  | 0.057 | 1.12 | 0.55 | 4.72 |  | 3.97 |  | 273.75 | 0.03125
Glass Door
0 < V < 15 |  | 7.5 | 0.08 |  | 0.057 | 1.23 | 0.55 | 1.83 |  | 0.9775 |  | 311.1625 | 0.035521
15 ≤ V < 30 |  | 22.5 | 0.08 |  | 0.057 | 1.23 | 0.55 | 3.03 |  | 1.8325 |  | 437.0875 | 0.049896
30 ≤ V < 50 |  | 40 | 0.08 |  | 0.057 | 1.23 | 0.55 | 4.43 |  | 2.83 |  | 584 | 0.066667
50 ≤ V |  | 60 | 0.08 |  | 0.057 | 1.23 | 0.55 | 6.03 |  | 3.97 |  | 751.9 | 0.085833
Measure Name |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  |  | Lifetime Energy Savings
Vertical Solid-Door, 0 < V < 15 |  | 15 < V < 30 |  | 0.023 |  |  | 202.58 |  |  |  | 2430.96
Vertical Solid-Door, 15 ≤ V < 30 |  | 15 < V < 30 |  | 0.058 |  |  | 504.43 |  |  |  | 6053.16
Vertical Solid-Door, 30 ≤ V < 50 |  | 30 < V < 50 |  | 0.073 |  |  | 640.36 |  |  |  | 7684.32
Vertical Solid-Door, 50 ≤ V |  | 50 < V |  | 0.074 |  |  | 649.7 |  |  |  | 7796.4
Vertical Glass-Door, 0 < V < 15 |  | 0 < V 15 |  | 0.043 |  |  | 374.13 |  |  |  | 4489.56
Vertical Glass-Door, 15 ≤ V < 30 |  | 15 < V < 30 |  | 0.079 |  |  | 691.68 |  |  |  | 8300.16
Vertical Glass-Door, 30 ≤ V < 50 |  | 30 < V < 50 |  | 0.121 |  |  | 1062.15 |  |  |  | 12745.8
Vertical Glass-Door, 50 ≤ V |  | 50 < V |  | 0.17 |  |  | 1485.55 |  |  |  | 17826.6
Horizontal Solid-Door, 0 < V < 15 |  | 0 < V 15 |  | 0.025 |  |  | 216.26 |  |  |  | 2595.12
Horizontal Solid-Door, 15 ≤ V < 30 |  | 15 < V < 30 |  | 0.027 |  |  | 232.69 |  |  |  | 2792.28
Horizontal Solid-Door, 30 ≤ V < 50 |  | 30 < V < 50 |  | 0.029 |  |  | 251.85 |  |  |  | 3022.2
Horizontal Solid-Door, 50 ≤ V |  | 50 < V |  | 0.031 |  |  | 273.75 |  |  |  | 3285
Horizontal Glass-Door, 0 < V < 15 |  | 0 < V 15 |  | 0.036 |  |  | 311.16 |  |  |  | 3733.92
Horizontal Glass-Door, 15 ≤ V < 30 |  | 15 < V < 30 |  | 0.05 |  |  | 437.09 |  |  |  | 5245.08
Horizontal Glass-Door, 30 ≤ V < 50 |  | 30 < V < 50 |  | 0.067 |  |  | 584 |  |  |  | 7008
Horizontal Glass-Door, 50 ≤ V |  | 50 < V |  | 0.086 |  |  | 751.9 |  |  |  | 9022.8
RESOURCES
• | AEG's analysis file titled "PY23 TRM Commercial Kitchen Freezer Analysis File."
• | Code of Federal Regulations at 10 CFR 431.66. URL: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-C/subject-group-ECFR8115bf7451f830f/section-431.66.
• | ENERGY STAR. 2022. "ENERGY STAR® Program Requirements Product Specification for Commercial Refrigerators and Freezers - Eligibility Criteria Version 5.0." Effective on December 22, 2022. URL: https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Version%205.0%20%28Rev.%20November%20-%202022%29%20Commercial%20Refrigerators%20and%20Freezers%20Specification_0.pdf.
• | California Technical Forum. 2023. "CPUC Support Tables. Effective Useful Life and Remaining Useful Life." URL: https://www.caetrm.com/cpuc/table/effusefullife/. Accessed on January 31, 2023.
• | 2023 Illinois Statewide Technical Reference Manual for Energy Efficiency Version 11.0, Volume 2: Commercial and Industrial Measures FINAL. September 22, 2022.
• | Idaho Power Company Technical Reference Manual 3.2. November 24th, 2021.
• | New Jersey Board of Public Utilities, New Jersey's Clean Energy ProgramTM Protocols to Measure Resource Savings, FY2021 Addendum. December 2, 2020.
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Program Version 3.3 FINAL. January 31, 2021.
DAYS
∆𝑘𝑊ℎ=〖(𝐸〗_𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 − 𝐸_𝐻𝐸) ∗ DAYS
∆𝑘𝑊=∆𝑘𝑊ℎ∗𝐶𝐹/𝐻𝑅𝑆
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿

## C_Kitchen_Refrigerator
COMMERCIAL: Refrigerator
Return to TOC
UPDATE STATUS
Updated in Winter 2022-2023 for PY23 TRM.
MEASURE DETAILS
Description
This measure relates to the installation of a new self-contained, reach-in commercial refrigerator with a door meeting ENERGY STAR efficiency standards. ENERGY STAR labeled commercial refrigerators are more energy efficient because they are designed with components such as ECM evaporator and condenser fan motors, hot gas anti-sweat heaters, or high-efficiency compressors, which will significantly reduce energy consumption. Commercial refrigerators are typically larger, more versatile, and robust than residential refrigerators. This measure is applicable to commercial refrigerators, only. It is not applicable to residential refrigerators operating in commercial buildings.
Program Criteria
This measure could relate to the replacing of an existing unit at the end of its useful life, or the installation of a new system in a new or existing building.
Unit of Measure
One refrigerator
Baseline Equipment
For this characterization to apply, the baseline equipment is assumed to be a solid or glass door refrigerator, closing either vertically or horizontally, meeting the minimum federal manufacturing standards. The volume for the baseline is assumed to be the average of the range. For example, if the range is 0 to 15, the average volume is 7.5.
High Efficiency Equipment
For this characterization to apply, the efficient equipment is assumed to be a solid or glass door refrigerator meeting the minimum ENERGY STAR efficiency level standards.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  |  |  | Value |  | Unit | Source/Notes
EBaseline |  | Baseline equipment daily energy usage |  |  |  |  | See Table 1 |  | kWh/day | Code of Federal Regulations at 10 CFR 431.66
EHE |  | High efficiency equipment daily energy usage |  |  |  |  | See Table 1 |  | kWh/day | ENERGY STAR Version 5.0
DAYS |  | Annual days of operation |  |  |  |  | 365 |  | days
HRS |  | Annual operating hours |  |  |  |  | 8760 |  | hrs
CF |  | Coincidence factor |  |  |  |  | 1 |  | -
EUL |  | Effective useful life of measure |  |  |  |  | 12 |  | yrs | PY23 TRM Commercial Kitchen Refrigerator Analysis File, "EUL Benchmarking" sheet
SAVINGS
Table 1. Summary of Savings Calculations
Volume |  | Typical Volume | Volumetric Factor (kWh/ft3) |  |  | Fixed Energy (kWh) |  | Adjusted Energy (kWh/day) |  |  |  | Energy Savings (kWh/yr) | Demand Savings (kW)
|  |  | Base |  | Efficient | Base | Efficient | Base |  | Efficient
Vertical Closed
Solid Door
0 < V < 15 |  | 7.5 | 0.05 |  | 0.0267 | 1.36 | 0.8 | 1.735 |  | 1.0003 |  | 268.1838 | 0.030615
15 ≤ V < 30 |  | 22.5 | 0.05 |  | 0.05 | 1.36 | 0.45 | 2.485 |  | 1.575 |  | 332.15 | 0.037917
30 ≤ V < 50 |  | 40 | 0.05 |  | 0.05 | 1.36 | 0.45 | 3.36 |  | 2.45 |  | 332.15 | 0.037917
50 ≤ V |  | 60 | 0.05 |  | 0.025 | 1.36 | 1.6991 | 4.36 |  | 3.1991 |  | 423.7285 | 0.048371
Glass Door
0 < V < 15 |  | 7.5 | 0.1 |  | 0.095 | 0.86 | 0.445 | 1.61 |  | 1.1575 |  | 165.1625 | 0.018854
15 ≤ V < 30 |  | 22.5 | 0.1 |  | 0.05 | 0.86 | 1.12 | 3.11 |  | 2.245 |  | 315.725 | 0.036042
30 ≤ V < 50 |  | 40 | 0.1 |  | 0.076 | 0.86 | 0.34 | 4.86 |  | 3.38 |  | 540.2 | 0.061667
50 ≤ V |  | 60 | 0.1 |  | 0.105 | 0.86 | -1.111 | 6.86 |  | 5.189 |  | 609.915 | 0.069625
Horizontal Closed
Solid Door
0 < V < 15 |  | 7.5 | 0.05 |  | 0.05 | 0.91 | 0.28 | 1.285 |  | 0.655 |  | 229.95 | 0.02625
15 ≤ V < 30 |  | 22.5 | 0.05 |  | 0.05 | 0.91 | 0.28 | 2.035 |  | 1.405 |  | 229.95 | 0.02625
30 ≤ V < 50 |  | 40 | 0.05 |  | 0.05 | 0.91 | 0.28 | 2.91 |  | 2.28 |  | 229.95 | 0.02625
50 ≤ V |  | 60 | 0.05 |  | 0.05 | 0.91 | 0.28 | 3.91 |  | 3.28 |  | 229.95 | 0.02625
Glass Door
0 < V < 15 |  | 7.5 | 0.06 |  | 0.05 | 0.37 | 0.28 | 0.82 |  | 0.655 |  | 60.225 | 0.006875
15 ≤ V < 30 |  | 22.5 | 0.06 |  | 0.05 | 0.37 | 0.28 | 1.72 |  | 1.405 |  | 114.975 | 0.013125
30 ≤ V < 50 |  | 40 | 0.06 |  | 0.05 | 0.37 | 0.28 | 2.77 |  | 2.28 |  | 178.85 | 0.020417
50 ≤ V |  | 60 | 0.06 |  | 0.05 | 0.37 | 0.28 | 3.97 |  | 3.28 |  | 251.85 | 0.02875
Measure Name |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  |  | Lifetime Energy Savings
Vertical Solid-Door, 0 < V < 15 |  | 15 < V < 30 |  | 0.031 |  |  | 268.18 |  |  |  | 3218.16
Vertical Solid-Door, 15 ≤ V < 30 |  | 15 < V < 30 |  | 0.038 |  |  | 332.15 |  |  |  | 3985.8
Vertical Solid-Door, 30 ≤ V < 50 |  | 30 < V < 50 |  | 0.038 |  |  | 332.15 |  |  |  | 3985.8
Vertical Solid-Door, 50 ≤ V |  | 50 < V |  | 0.048 |  |  | 423.73 |  |  |  | 5084.76
Vertical Glass-Door, 0 < V < 15 |  | 0 < V 15 |  | 0.019 |  |  | 165.16 |  |  |  | 1981.92
Vertical Glass-Door, 15 ≤ V < 30 |  | 15 < V < 30 |  | 0.036 |  |  | 315.73 |  |  |  | 3788.76
Vertical Glass-Door, 30 ≤ V < 50 |  | 30 < V < 50 |  | 0.062 |  |  | 540.2 |  |  |  | 6482.4
Vertical Glass-Door, 50 ≤ V |  | 50 < V |  | 0.07 |  |  | 609.92 |  |  |  | 7319.04
Horizontal Solid-Door, 0 < V ≤ 15 |  | 0 < V 15 |  | 0.026 |  |  | 229.95 |  |  |  | 2759.4
Horizontal Solid-Door, 15 ≤ V < 30 |  | 15 < V < 30 |  | 0.026 |  |  | 229.95 |  |  |  | 2759.4
Horizontal Solid-Door, 30 ≤ V < 50 |  | 30 < V < 50 |  | 0.026 |  |  | 229.95 |  |  |  | 2759.4
Horizontal Solid-Door, 50 ≤ V |  | 50 < V |  | 0.026 |  |  | 229.95 |  |  |  | 2759.4
Horizontal Glass-Door, 0 < V ≤ 15 |  | 0 < V 15 |  | 0.007 |  |  | 60.23 |  |  |  | 722.76
Horizontal Glass-Door, 15 ≤ V < 30 |  | 15 < V < 30 |  | 0.013 |  |  | 114.98 |  |  |  | 1379.76
Horizontal Glass-Door, 30 ≤ V < 50 |  | 30 < V < 50 |  | 0.02 |  |  | 178.85 |  |  |  | 2146.2
Horizontal Glass-Door, 50 ≤ V |  | 50 < V |  | 0.029 |  |  | 251.85 |  |  |  | 3022.2
RESOURCES
• | AEG's analysis file titled: "PY23 TRM Commercial Kitchen Refrigerator Analysis File."
• | Code of Federal Regulations at 10 CFR 431.66. URL: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-C/subject-group-ECFR8115bf7451f830f/section-431.66.
• | ENERGY STAR. 2022. "ENERGY STAR® Program Requirements Product Specification for Commercial Refrigerators and Freezers - Eligibility Criteria Version 5.0." Effective on December 22, 2022. URL: https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Version%205.0%20%28Rev.%20November%20-%202022%29%20Commercial%20Refrigerators%20and%20Freezers%20Specification_0.pdf.
• | California Technical Forum. 2023. "CPUC Support Tables. Effective Useful Life and Remaining Useful Life." URL: https://www.caetrm.com/cpuc/table/effusefullife/. Accessed on January 31, 2023.
• | 2023 Illinois Statewide Technical Reference Manual for Energy Efficiency Version 11.0, Volume 2: Commercial and Industrial Measures FINAL. September 22, 2022.
• | Idaho Power Company Technical Reference Manual 3.2. November 24th, 2021.
• | New Jersey Board of Public Utilities, New Jersey's Clean Energy ProgramTM Protocols to Measure Resource Savings, FY2021 Addendum. December 2, 2020.
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Program Version 3.3 FINAL. January 31, 2021.
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
DAYS
∆𝑘𝑊ℎ=〖(𝐸〗_𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 − 𝐸_𝐻𝐸) ∗ DAYS
∆𝑘𝑊=∆𝑘𝑊ℎ∗𝐶𝐹/𝐻𝑅𝑆

## C_Kitchen_Dishwasher
COMMERCIAL: Dishwasher
Return to TOC
UPDATE STATUS
Added in Winter 2021-2022 for PY22 TRM.
MEASURE DETAILS
Description
This measure relates to installing a new commercial dishwasher that meets the ENERGY STAR efficiency standards. ENERGY STAR dishwashers use waste air heat recovery, drain heat recovery, rinse water re-use, double-walled insulated construction, high-efficiency anti-clogging nozzles, continuous filtering, and efficient booster heating. This measure applies to five commercial dishwasher types: under-counter, stationary single tank door, single tank conveyor, multi-tank conveyor, and pot, pan, utensil dishwashers. It does not apply to flight machines that are custom-built continuous conveyor machines designed for large institutions. The measure does not apply to residential dishwashers operating in commercial buildings.
Program Criteria
This measure can involve replacing an existing dishwasher at the end of its useful life or installing a new dishwasher in a new or existing building. The project documentation must capture the type of fuel used for water heating and booster heating (e.g., electricity, natural gas, propane, solar) to determine energy-saving estimates. An exception to this requirement is when program delivery is through the midstream approach and the customer's water heating type is unknown.
Unit of Measure
One dishwasher
Baseline Equipment
The baseline equipment is a commercial dishwasher that is not ENERGY STAR certified.
High Efficiency Equipment
The efficient equipment must be a commercial dishwasher that meets the minimum ENERGY STAR Version 3.0 efficiency standards.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Where:
(2)
(3)
(4)
(5)
(6)
(7)
(8)
(9)
Peak Demand Reduction, kW
(10)
Lifetime Energy Savings, kWh
(11)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  |  | Description | [10 empty] | Value |  |  |  | Unit |  |  | Source/Notes
Ebase |  |  |  |  | Baseline dishwasher annual energy use | [10 empty] | See Tables 6-9 |  |  |  | kWh/yr |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
EEnergyStar |  |  |  |  | ENERGY STAR equipment annual energy use | [10 empty] | See Tables 6-9 |  |  |  | kWh/yr |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
Ewaterheater base |  |  |  |  | Water heater annual energy use due to baseline dishwasher | [10 empty] | Calculated |  |  |  | kWh/yr |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
Ewaterheater EnergyStar |  |  |  |  | Water heater annual energy use due to ENERGY STAR dishwasher | [10 empty] | Calculated |  |  |  | kWh/yr |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
Eboosterheater base |  |  |  |  | Booster heater annual energy use due to baseline dishwasher | [10 empty] | Calculated |  |  |  | kWh/yr |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
Eboosterheater EnergyStar |  |  |  |  | Booster heater equipment annual energy use due to ENERGY STAR dishwasher | [10 empty] | Calculated |  |  |  | kWh/yr |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
Eidledraw base |  |  |  |  | Baseline dishwasher idle draw annual energy use | [10 empty] | Calculated |  |  |  | kWh/yr |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
Eidledraw EnergyStar |  |  |  |  | ENERGY STAR dishwasher idle draw annual energy use | [10 empty] | Calculated |  |  |  | kWh/yr |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
WaterUsebase |  |  |  |  | Water use per rack of baseline dishwasher | [10 empty] | Table 1 |  |  |  | gallons/ rack |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
WaterUseEnergyStar |  |  |  |  | Water use per rack of ENERGY STAR dishwasher | [10 empty] | Table 1 |  |  |  | gallons/ rack |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
RPD |  |  |  |  | Racks washed per day | [10 empty] | Table 2 |  |  |  | racks/ day |  |  | California Technical Forum. 2022. California Electronic Technical Reference Material (eTRM) and Engineering Judgement.
DAYS |  |  |  |  | Annual days of dishwasher operation | [10 empty] | 365 |  |  |  | days |  |  | California Technical Forum. 2022. California Electronic Technical Reference Material (eTRM).
ΔTwaterheater |  |  |  |  | Inlet water temperature increase for water heater | [10 empty] | 65 |  |  |  | °F |  |  | Increase of inlet water temperature from the average groundwater temperature, which is 75°F in Hawaii, to 140°F. Consistent with other water heater measures in the HI TRM.
ΔTboosterheater |  |  |  |  | Inlet water temperature increase for booster heater | [10 empty] | 40 |  |  |  | °F |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
CP |  |  |  |  | Specific heat of water | [10 empty] | 1 |  |  |  | Btu/lb/°F |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
ρ |  |  |  |  | Density of water | [10 empty] | 8.2 |  |  |  | lb/gallon |  |  | Average of density of water at 75°F (8.3 bs/gallon), 140°F (8.2 lb/gal) and 180°F (8.1 lb/gallon)
DAILY HRS |  |  |  |  | Average daily operating hours of dishwasher | [10 empty] | 12 |  |  |  | hours |  |  | California Technical Forum. 2022. California Electronic Technical Reference Material (eTRM) and Engineering Judgement.
Effwaterheater |  |  |  |  | Efficiency of the water heater | [10 empty] | electric: 98 gas: 80 |  |  |  | % |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
Effboosterheater |  |  |  |  | Efficiency of the booster heater | [10 empty] | electric: 98 gas: 80 |  |  |  | % |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
Conversion factor |  |  |  |  | kWh to Btu conversion factor | [10 empty] | 3412 |  |  |  | kWh/Btu
IdleDrawbase |  |  |  |  | Idle power draw of baseline dishwasher | [10 empty] | Table 3 |  |  |  | kW |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
IdleDrawEnergyStar |  |  |  |  | Idle power draw of ENERGY STAR dishwasher | [10 empty] | Table 3 |  |  |  | kW |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
WashTimebase |  |  |  |  | Typical wash time of baseline dishwasher | [10 empty] | Table 4 |  |  |  | minutes |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
WashTimeEnergyStar |  |  |  |  | Typical wash time of ENERGY STAR dishwasher | [10 empty] | Table 4 |  |  |  | minutes |  |  | ENERGY STAR Commercial Kitchen Equipment Savings Calculator
ANNUAL HRS |  |  |  |  | Annual operating hours of dishwasher | [10 empty] | 4380 |  |  |  | hours |  |  | DAILY HRS * DAYS = (12*365)
CF |  |  |  |  | Coincidence factor | [10 empty] | 0.74 | [6 empty] | PY22 TRM "Equipment Operating Hours and Coincidence Factors" sheet. CF is 0.74 for restaurant water heating which can be used as a proxy for commercial kitchen dishwasher end-use load.
EUL |  |  |  |  | Effective useful life of measure | [10 empty] | See Table 5 |  |  |  | years |  |  | PY22 TRM Commercial Kitchen Dishwasher Analysis File, "EUL Benchmarking" sheet.
Table 1. Water Use Per Rack, by Dishwasher Type
Dishwasher Type | [16 empty] | Baseline Gallons/Rack |  |  |  |  | ENERGY STAR Gallons/Rack
Low Temperature |  |  |  |  | Under Counter | [11 empty] | 1.73 |  |  |  |  | 1.19
[5 empty] | Stationary Single Tank Door | [11 empty] | 2.1 |  |  |  |  | 1.18
[5 empty] | Single Tank Conveyor | [11 empty] | 1.31 |  |  |  |  | 0.79
[5 empty] | Multi Tank Conveyor | [11 empty] | 1.04 |  |  |  |  | 0.54
High Temperature |  |  |  |  | Under Counter | [11 empty] | 1.09 |  |  |  |  | 0.86
[5 empty] | Stationary Single Tank Door | [11 empty] | 1.29 |  |  |  |  | 0.89
[5 empty] | Single Tank Conveyor | [11 empty] | 0.87 |  |  |  |  | 0.7
[5 empty] | Multi Tank Conveyor | [11 empty] | 0.97 |  |  |  |  | 0.54
[5 empty] | Pot, Pan, Utensil | [11 empty] | 0.7 |  |  |  |  | 0.58
Table 2. Racks per Day, by Dishwasher Type
Dishwasher Type | [16 empty] | Racks Per Day
Low Temperature |  |  |  |  | Under Counter | [11 empty] | 50
[5 empty] | Stationary Single Tank Door | [11 empty] | 141
[5 empty] | Single Tank Conveyor | [11 empty] | 267
[5 empty] | Multi Tank Conveyor | [11 empty] | 400
High Temperature |  |  |  |  | Under Counter | [11 empty] | 50
[5 empty] | Stationary Single Tank Door | [11 empty] | 141
[5 empty] | Single Tank Conveyor | [11 empty] | 267
[5 empty] | Multi Tank Conveyor | [11 empty] | 400
[5 empty] | Pot, Pan, Utensil | [11 empty] | 187
Table 3. Idle Power Draw, by Dishwasher Type
Dishwasher Type | [16 empty] | Baseline kW |  |  |  |  | ENERGY STAR kW
Low Temperature |  |  |  |  | Under Counter | [11 empty] | 0.5 |  |  |  |  | 0.25
[5 empty] | Stationary Single Tank Door | [11 empty] | 0.6 |  |  |  |  | 0.3
[5 empty] | Single Tank Conveyor | [11 empty] | 1.6 |  |  |  |  | 0.85
[5 empty] | Multi Tank Conveyor | [11 empty] | 2 |  |  |  |  | 1
High Temperature |  |  |  |  | Under Counter | [11 empty] | 0.76 |  |  |  |  | 0.3
[5 empty] | Stationary Single Tank Door | [11 empty] | 0.87 |  |  |  |  | 0.55
[5 empty] | Single Tank Conveyor | [11 empty] | 1.93 |  |  |  |  | 1.2
[5 empty] | Multi Tank Conveyor | [11 empty] | 2.59 |  |  |  |  | 1.85
[5 empty] | Pot, Pan, Utensil | [11 empty] | 1.2 |  |  |  |  | 0.9
Table 4. Typical Wash Time, by Dishwasher Type
Dishwasher Type | [16 empty] | Baseline minutes |  |  |  |  | ENERGY STAR minutes
Low Temperature |  |  |  |  | Under Counter | [11 empty] | 2 |  |  |  |  | 2
[5 empty] | Stationary Single Tank Door | [11 empty] | 1.5 |  |  |  |  | 1.5
[5 empty] | Single Tank Conveyor | [11 empty] | 0.3 |  |  |  |  | 0.3
[5 empty] | Multi Tank Conveyor | [11 empty] | 0.3 |  |  |  |  | 0.3
High Temperature |  |  |  |  | Under Counter | [11 empty] | 2 |  |  |  |  | 2
[5 empty] | Stationary Single Tank Door | [11 empty] | 1 |  |  |  |  | 1
[5 empty] | Single Tank Conveyor | [11 empty] | 0.3 |  |  |  |  | 0.3
[5 empty] | Multi Tank Conveyor | [11 empty] | 0.2 |  |  |  |  | 0.2
[5 empty] | Pot, Pan, Utensil | [11 empty] | 3 |  |  |  |  | 3
Table 5. Effective Useful Life, by Dishwasher Type
Dishwasher Type | [16 empty] | EUL
Low Temperature |  |  |  |  | Under Counter | [11 empty] | 10
[5 empty] | Stationary Single Tank Door | [11 empty] | 15
[5 empty] | Single Tank Conveyor | [11 empty] | 20
[5 empty] | Multi Tank Conveyor | [11 empty] | 20
High Temperature |  |  |  |  | Under Counter | [11 empty] | 10
[5 empty] | Stationary Single Tank Door | [11 empty] | 15
[5 empty] | Single Tank Conveyor | [11 empty] | 20
[5 empty] | Multi Tank Conveyor | [11 empty] | 20
[5 empty] | Pot, Pan, Utensil | [11 empty] | 10
Table 6. Summary Savings for Commercial Dishwasher, Electric Water Heating and Electric Booster Water Heating
Dishwasher Type | [16 empty] | Ebase (kWh/yr) |  |  |  | EEnergyStar (kWh/yr) |  |  |  | Energy Savings (kWh/yr) |  |  |  | Demand Savings (kW)
Low Temperature1 |  |  |  |  | Under Counter | [11 empty] | 6917 |  |  |  | 4404 |  |  |  | 2513 |  |  |  | 0.42457
[5 empty] | Stationary Single Tank Door | [11 empty] | 19079 |  |  |  | 10605 |  |  |  | 8474 |  |  |  | 1.4317
[5 empty] | Single Tank Conveyor | [11 empty] | 26548 |  |  |  | 15563 |  |  |  | 10985 |  |  |  | 1.8559
[5 empty] | Multi Tank Conveyor | [11 empty] | 31496 |  |  |  | 16214 |  |  |  | 15282 |  |  |  | 2.5819
High Temperature |  |  |  |  | Under Counter | [11 empty] | 7987 |  |  |  | 5172 |  |  |  | 2815 |  |  |  | 0.47559
[5 empty] | Stationary Single Tank Door | [11 empty] | 20154 |  |  |  | 13728 |  |  |  | 6426 |  |  |  | 1.0857
[5 empty] | Single Tank Conveyor | [11 empty] | 29312 |  |  |  | 22211 |  |  |  | 7101 |  |  |  | 1.1997
[5 empty] | Multi Tank Conveyor | [11 empty] | 46539 |  |  |  | 27498 |  |  |  | 19041 |  |  |  | 3.217
[5 empty] | Pot, Pan, Utensil | [11 empty] | 13445 |  |  |  | 11049 |  |  |  | 2396 |  |  |  | 0.4048
1. Low temperature dishwashers do not require booster heaters.
Table 7. Summary Savings for Commercial Dishwasher, Electric Water Heating and Natural Gas Booster Water Heating
Dishwasher Type | [16 empty] | Ebase (kWh/yr) |  |  |  | EEnergyStar (kWh/yr) |  |  |  | Energy Savings (kWh/yr) |  |  |  | Demand Savings (kW)
Low Temperature1 |  |  |  |  | Under Counter | [11 empty] | 6917 |  |  |  | 4404 |  |  |  | 2513 |  |  |  | 0.42457
[5 empty] | Stationary Single Tank Door | [11 empty] | 19079 |  |  |  | 10605 |  |  |  | 8474 |  |  |  | 1.4317
[5 empty] | Single Tank Conveyor | [11 empty] | 26548 |  |  |  | 15563 |  |  |  | 10985 |  |  |  | 1.8559
[5 empty] | Multi Tank Conveyor | [11 empty] | 31496 |  |  |  | 16214 |  |  |  | 15282 |  |  |  | 2.5819
High Temperature |  |  |  |  | Under Counter | [11 empty] | 6036 |  |  |  | 3633 |  |  |  | 2403 |  |  |  | 0.40599
[5 empty] | Stationary Single Tank Door | [11 empty] | 13644 |  |  |  | 9236 |  |  |  | 4408 |  |  |  | 0.74473
[5 empty] | Single Tank Conveyor | [11 empty] | 21008 |  |  |  | 15529 |  |  |  | 5479 |  |  |  | 0.92568
[5 empty] | Multi Tank Conveyor | [11 empty] | 32652 |  |  |  | 19766 |  |  |  | 12886 |  |  |  | 2.1771
[5 empty] | Pot, Pan, Utensil | [11 empty] | 8768 |  |  |  | 7173 |  |  |  | 1595 |  |  |  | 0.26947
1. Low temperature dishwashers do not require booster heaters.
Table 8. Summary Savings for Commercial Dishwasher, Natural Gas Water Heating and Electric Booster Water Heating
Dishwasher Type | [16 empty] | Ebase (kWh/yr) |  |  |  | EEnergyStar (kWh/yr) |  |  |  | Energy Savings (kWh/yr) |  |  |  | Demand Savings (kW)
Low Temperature1 |  |  |  |  | Under Counter | [11 empty] | 1886 |  |  |  | 943 |  |  |  | 943 |  |  |  | 0.15932
[5 empty] | Stationary Single Tank Door | [11 empty] | 1856 |  |  |  | 928 |  |  |  | 928 |  |  |  | 0.15679
[5 empty] | Single Tank Conveyor | [11 empty] | 6229 |  |  |  | 3309 |  |  |  | 2920 |  |  |  | 0.49333
[5 empty] | Multi Tank Conveyor | [11 empty] | 7300 |  |  |  | 3650 |  |  |  | 3650 |  |  |  | 0.61667
High Temperature |  |  |  |  | Under Counter | [11 empty] | 4817 |  |  |  | 2671 |  |  |  | 2146 |  |  |  | 0.36257
[5 empty] | Stationary Single Tank Door | [11 empty] | 9575 |  |  |  | 6429 |  |  |  | 3146 |  |  |  | 0.53152
[5 empty] | Single Tank Conveyor | [11 empty] | 15818 |  |  |  | 11353 |  |  |  | 4465 |  |  |  | 0.75436
[5 empty] | Multi Tank Conveyor | [11 empty] | 23972 |  |  |  | 14934 |  |  |  | 9038 |  |  |  | 1.527
[5 empty] | Pot, Pan, Utensil | [11 empty] | 5845 |  |  |  | 4751 |  |  |  | 1094 |  |  |  | 0.18483
1. Low temperature dishwashers do not require booster heaters.
Table 9. Summary Savings for Commercial Dishwasher, Natural Gas Water Heating and Natural Gas Booster Water Heating
Dishwasher Type | [16 empty] | Ebase (kWh/yr) |  |  |  | EEnergyStar (kWh/yr) |  |  |  | Energy Savings (kWh/yr) |  |  |  | Demand Savings (kW)
Low Temperature1 |  |  |  |  | Under Counter | [11 empty] | 1886 |  |  |  | 943 |  |  |  | 943 |  |  |  | 0.15932
[5 empty] | Stationary Single Tank Door | [11 empty] | 1856 |  |  |  | 928 |  |  |  | 928 |  |  |  | 0.15679
[5 empty] | Single Tank Conveyor | [11 empty] | 6229 |  |  |  | 3309 |  |  |  | 2920 |  |  |  | 0.49333
[5 empty] | Multi Tank Conveyor | [11 empty] | 7300 |  |  |  | 3650 |  |  |  | 3650 |  |  |  | 0.61667
High Temperature |  |  |  |  | Under Counter | [11 empty] | 2866 |  |  |  | 1132 |  |  |  | 1734 |  |  |  | 0.29296
[5 empty] | Stationary Single Tank Door | [11 empty] | 3064 |  |  |  | 1937 |  |  |  | 1127 |  |  |  | 0.19041
[5 empty] | Single Tank Conveyor | [11 empty] | 7514 |  |  |  | 4672 |  |  |  | 2842 |  |  |  | 0.48016
[5 empty] | Multi Tank Conveyor | [11 empty] | 10084 |  |  |  | 7203 |  |  |  | 2881 |  |  |  | 0.48674
[5 empty] | Pot, Pan, Utensil | [11 empty] | 1168 |  |  |  | 876 |  |  |  | 292 |  |  |  | 0.049333
1. Low temperature dishwashers do not require booster heaters.
Table 10. Water Heating Fuel in Restaurants In Hawaii
Fuel Used for Water Heating | [19 empty] | Share
Electric, including Solar Thermal with Electric Backup | [19 empty] | 71%
Natural Gas, Synthetic Gas, or Propane | [19 empty] | 29%
Total | [19 empty] | 100%
Note: These shares are used to calculate blended savings values for use when the water heating fuel type is unknown. The blended savings calculation approach assumes that these share apply both to primary water heating fuel type and to booster heating fuel type.
Data Source: These market shares were used by AEG to develop the restaurant market profiles for the 2020 Hawaii Statewide Market Potential Study. They were derived from water heating data for restaurants obtained during the 2019 Hawaii Statewide Baseline Energy Use Study.
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
User Inputs
|  | Dishwasher Temperature: | [12 empty] | Low Temperature
|  | Dishwasher Type: Note: Pot, Pan and Utensil dishwasher is always High Temperature dishwasher. | [12 empty] | Under Counter
|  | Primary Water Heating Type: Note: If kitchen uses propane for water heating, please select natural gas water heating. | [12 empty] | Unknown Water Heating
|  | Booster Water Heating Type: Note: Must select booster heating for high temperature dishwasher. If kitchen uses propane for booster water heating, please select natural gas booster heating. If primary water heating type is unknown, please select unknown booster heating as well. | [12 empty] | Unknown Booster Heating
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Savings
Low Temperature Under Counter, Unknown Water Heating | [7 empty] | 0.348 | [7 empty] | 2057.7 | [7 empty] | 20577
Note: Savings shown in blue result from sample entry above. They are for illustrative purposes only.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Low Temperature Under Counter, Electric Water Heating |  |  |  | 15 < V < 30 |  |  |  | 0.425 | [7 empty] | 2513 | [7 empty] | 25130
Low Temperature Stationary Single Tank Door, Electric Water Heating |  |  |  | 15 < V < 30 |  |  |  | 1.432 | [7 empty] | 8474 | [7 empty] | 127110
Low Temperature Single Tank Conveyor, Electric Water Heating |  |  |  | 15 < V < 30 |  |  |  | 1.856 | [7 empty] | 10985 | [7 empty] | 219700
Low Temperature Multi Tank Conveyor, Electric Water Heating |  |  |  | 15 < V < 30 |  |  |  | 2.582 | [7 empty] | 15282 | [7 empty] | 305640
Low Temperature Under Counter, Natural Gas Water Heating |  |  |  | 15 < V < 30 |  |  |  | 0.159 | [7 empty] | 943 | [7 empty] | 9430
Low Temperature Stationary Single Tank Door, Natural Gas Water Heating |  |  |  | 15 < V < 30 |  |  |  | 0.157 | [7 empty] | 928 | [7 empty] | 13920
Low Temperature Single Tank Conveyor, Natural Gas Water Heating |  |  |  | 15 < V < 30 |  |  |  | 0.493 | [7 empty] | 2920 | [7 empty] | 58400
Low Temperature Multi Tank Conveyor, Natural Gas Water Heating |  |  |  | 15 < V < 30 |  |  |  | 0.617 | [7 empty] | 3650 | [7 empty] | 73000
Low Temperature Under Counter, Unknown Water Heating |  |  |  | 15 < V < 30 |  |  |  | 0.348 | [7 empty] | 2057.7 | [7 empty] | 20577
Low Temperature Stationary Single Tank Door, Unknown Water Heating |  |  |  | 15 < V < 30 |  |  |  | 1.062 | [7 empty] | 6285.66 | [7 empty] | 94284.9
Low Temperature Single Tank Conveyor, Unknown Water Heating |  |  |  | 15 < V < 30 |  |  |  | 1.461 | [7 empty] | 8646.15 | [7 empty] | 172923
Low Temperature Multi Tank Conveyor, Unknown Water Heating |  |  |  | 15 < V < 30 |  |  |  | 2.012 | [7 empty] | 11908.72 | [7 empty] | 238174.4
High Temperature Under Counter, Electric Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.476 | [7 empty] | 2815 | [7 empty] | 28150
High Temperature Stationary Single Tank Door, Electric Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 1.086 | [7 empty] | 6426 | [7 empty] | 96390
High Temperature Single Tank Conveyor, Electric Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 1.2 | [7 empty] | 7101 | [7 empty] | 142020
High Temperature Multi Tank Conveyor, Electric Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 3.217 | [7 empty] | 19041 | [7 empty] | 380820
High Temperature Pot Pan and Utensil, Electric Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.405 | [7 empty] | 2396 | [7 empty] | 23960
High Temperature Under Counter, Electric Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.406 | [7 empty] | 2403 | [7 empty] | 24030
High Temperature Stationary Single Tank Door, Electric Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.745 | [7 empty] | 4408 | [7 empty] | 66120
High Temperature Single Tank Conveyor, Electric Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.926 | [7 empty] | 5479 | [7 empty] | 109580
High Temperature Multi Tank Conveyor, Electric Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 2.177 | [7 empty] | 12886 | [7 empty] | 257720
High Temperature Pot Pan and Utensil, Electric Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.269 | [7 empty] | 1595 | [7 empty] | 15950
High Temperature Under Counter, Natural Gas Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.363 | [7 empty] | 2146 | [7 empty] | 21460
High Temperature Stationary Single Tank Door, Natural Gas Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.532 | [7 empty] | 3146 | [7 empty] | 47190
High Temperature Single Tank Conveyor, Natural Gas Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.754 | [7 empty] | 4465 | [7 empty] | 89300
High Temperature Multi Tank Conveyor, Natural Gas Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 1.527 | [7 empty] | 9038 | [7 empty] | 180760
High Temperature Pot Pan and Utensil, Natural Gas Water Heating and Electric Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.185 | [7 empty] | 1094 | [7 empty] | 10940
High Temperature Under Counter, Natural Gas Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.293 | [7 empty] | 1734 | [7 empty] | 17340
High Temperature Stationary Single Tank Door, Natural Gas Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.19 | [7 empty] | 1127 | [7 empty] | 16905
High Temperature Single Tank Conveyor, Natural Gas Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.48 | [7 empty] | 2842 | [7 empty] | 56840
High Temperature Multi Tank Conveyor, Natural Gas Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.487 | [7 empty] | 2881 | [7 empty] | 57620
High Temperature Pot Pan and Utensil, Natural Gas Water Heating and Natural Gas Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.049 | [7 empty] | 292 | [7 empty] | 2920
High Temperature Under Counter, Unknown Water Heating and Unknown Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.423 | [7 empty] | 2501.51 | [7 empty] | 25015.1
High Temperature Stationary Single Tank Door, Unknown Water Heating and Unknown Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.826 | [7 empty] | 4889.5 | [7 empty] | 73342.5
High Temperature Single Tank Conveyor, Unknown Water Heating and Unknown Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.991 | [7 empty] | 5866.1 | [7 empty] | 117322
High Temperature Multi Tank Conveyor, Unknown Water Heating and Unknown Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 2.425 | [7 empty] | 14355.01 | [7 empty] | 287100.2
High Temperature Pot Pan and Utensil, Unknown Water Heating and Unknown Booster Heating |  |  |  | 15 < V < 30 |  |  |  | 0.302 | [7 empty] | 1786.05 | [7 empty] | 17860.5
Deemed Savings Tables - Blended Water Heater Type (see Table 10 for Shares)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Low Temperature Under Counter, Blended |  |  |  | 15 < V < 30 |  |  |  | 0.348 | [7 empty] | 2057.7 | [7 empty] | 20577
Low Temperature Stationary Single Tank Door, Blended |  |  |  | 15 < V < 30 |  |  |  | 1.062 | [7 empty] | 6285.66 | [7 empty] | 94284.9
Low Temperature Single Tank Conveyor, Blended |  |  |  | 15 < V < 30 |  |  |  | 1.461 | [7 empty] | 8646.15 | [7 empty] | 172923
Low Temperature Multi Tank Conveyor, Blended |  |  |  | 15 < V < 30 |  |  |  | 2.012 | [7 empty] | 11908.72 | [7 empty] | 238174.4
High Temperature Under Counter, Blended |  |  |  | 15 < V < 30 |  |  |  | 0.423 | [7 empty] | 2501.51 | [7 empty] | 25015.1
High Temperature Stationary Single Tank Door, Blended |  |  |  | 15 < V < 30 |  |  |  | 0.826 | [7 empty] | 4889.5 | [7 empty] | 73342.5
High Temperature Single Tank Conveyor, Blended |  |  |  | 15 < V < 30 |  |  |  | 0.991 | [7 empty] | 5866.1 | [7 empty] | 117322
High Temperature Multi Tank Conveyor, Blended |  |  |  | 15 < V < 30 |  |  |  | 2.425 | [7 empty] | 14355.01 | [7 empty] | 287100.2
High Temperature Pot Pan and Utensil, Blended |  |  |  | 15 < V < 30 |  |  |  | 0.302 | [7 empty] | 1786.05 | [7 empty] | 17860.5
RESOURCES
• | AEG's analysis file titled: "PY22 TRM Commercial Kitchen Dishwasher Analysis File."
• | ENERGY STAR. 2021. "ENERGY STAR® Program Requirements Product Specification for Commercial Dishwashers - Eligibility Criteria Version 3.0." Effective on June 27, 2021. URL: https://www.energystar.gov/sites/default/files/Commercial%20Dishwashers%20Final%20Version%203.0%20Specification.pdf.
• | ENERGY STAR. 2021. "ENERGY STAR Commercial Kitchen Equipment Savings Calculator" , URL: https://cmadmin.energystar.gov/sites/default/files/asset/document/CFS_calculator_03-02-2021.xlsx.
• | 2022 Illinois Statewide Technical Reference Manual for Energy Efficiency Version 10.0, Volume 2: Commercial and Industrial Measures FINAL. September 24, 2021.
• | New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs, Residential, Multi-Family, and Commercial/Industrial Measures, Version 9. August 30, 2021. URL: https://www3.dps.ny.gov/W/PSCWeb.nsf/96f0fec0b45a3c6485257688006a701a/72c23decff52920a85257f1100671bdd/$FILE/NYS%20TRM%20V9.pdf.
• | California Technical Forum. 2022. California Electronic Technical Reference Material (eTRM). "Door-Type Dishwasher, Commercial. Characterization." Effective on November 7, 2021. URL: https://www.caetrm.com/measure/SWFS002/02/.
• | California Technical Forum. 2022. California Electronic Technical Reference Material (eTRM). "Undercounter Dishwasher, Commercial. Characterization." Effective on November 7, 2021. URL: https://www.caetrm.com/measure/SWFS018/03/.
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Program Version 3.2 FINAL. January 7, 2021. URL: https://mn.gov/commerce-stat/pdfs/20210201_trm_cip_vers3.2.pdf.
• | Applied Energy Group. 2019 Hawaii Statewide Baseline Study Energy Use Study. Prepared for the Hawaii Public Utilities Commission. April 27, 2020. Analysis of raw survey data related to water heating in restaurants.
• | Applied Energy Group. State of Hawaii Market Potential Study. Prepared for the Hawaii Public Utilities Commission. July 27, 2020. Shares of water heating fuel type used in market profiles for restaurants.
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊ℎ=𝐸𝑏𝑎𝑠𝑒−𝐸𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟
∆𝑘𝑊=∆𝑘𝑊ℎ∗𝐶𝐹/𝐻𝑅𝑆
𝐸𝑏𝑎𝑠𝑒=𝐸𝑤𝑎𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 𝑏𝑎𝑠𝑒+𝐸𝑏𝑜𝑜𝑠𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 𝑏𝑎𝑠𝑒+𝐸𝑖𝑑𝑙𝑒 𝑏𝑎𝑠𝑒
𝐸𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟=𝐸𝑤𝑎𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟+𝐸𝑏𝑜𝑜𝑠𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟+𝐸𝑖𝑑𝑙𝑒 𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟
base
𝐸𝑤𝑎𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 𝑏𝑎𝑠𝑒=(𝑊𝑎𝑡𝑒𝑟𝑈𝑠𝑒base ∗𝑅𝑃𝐷∗𝐷𝐴𝑌𝑆)∗((∆𝑇𝑖𝑤𝑎𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 ∗ 𝐶𝑝 ∗ ρ )/𝐸𝑓𝑓𝑤𝑎𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 " " )∗(1/3412 " " )
EnergyStar
𝐸𝑤𝑎𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟=
(𝑊𝑎𝑡𝑒𝑟𝑈𝑠𝑒EnergyStar ∗𝑅𝑃𝐷∗𝐷𝐴𝑌𝑆)∗((∆𝑇𝑤𝑎𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 ∗ 𝐶𝑝 ∗ ρ )/𝐸𝑓𝑓𝑤𝑎𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟)∗(1/3412 " " )
base
𝐸𝑏𝑜𝑜𝑠𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 𝑏𝑎𝑠𝑒=(𝑊𝑎𝑡𝑒𝑟𝑈𝑠𝑒base ∗𝑅𝑃𝐷∗𝐷𝐴𝑌𝑆)∗((∆𝑇𝑏𝑜𝑜𝑠𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 ∗ 𝐶𝑝 ∗ ρ )/𝐸𝑓𝑓𝑏𝑜𝑜𝑠𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟)∗(1/3412 " " )
base
𝐸𝑏𝑜𝑜𝑠𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟=
(𝑊𝑎𝑡𝑒𝑟𝑈𝑠𝑒base ∗ 𝑅𝑃𝐷∗𝐷𝐴𝑌𝑆)∗ ((∆𝑇𝑏𝑜𝑜𝑠𝑡𝑒𝑟ℎ𝑒𝑎𝑡𝑒𝑟 ∗ 𝐶𝑝 ∗ ρ )/(𝐸𝑓𝑓𝑏𝑜𝑜𝑠𝑡𝑒𝑟 ℎ𝑒𝑎𝑡𝑒𝑟) " " )∗(1/3412 " " )
𝐸𝑖𝑑𝑙𝑒 𝑏𝑎𝑠𝑒=𝐼𝑑𝑙𝑒𝐷𝑟𝑎𝑤𝑏𝑎𝑠𝑒∗[𝐷𝐴𝐼𝐿𝑌 𝐻𝑅𝑆∗𝐷𝐴𝑌𝑆 − 𝑅𝑃𝐷∗𝐷𝐴𝑌𝑆 ∗(𝑊𝑎𝑠ℎ𝑇𝑖𝑚𝑒𝑏𝑎𝑠𝑒/60)]
𝐸𝑖𝑑𝑙𝑒 𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟=
𝐼𝑑𝑙𝑒𝐷𝑟𝑎𝑤𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟∗[𝐷𝐴𝐼𝐿𝑌 𝐻𝑅𝑆∗𝐷𝐴𝑌𝑆−𝑅𝑃𝐷∗𝐷𝐴𝑌𝑆∗(𝑊𝑎𝑠ℎ𝑇𝑖𝑚𝑒𝐸𝑛𝑒𝑟𝑔𝑦𝑆𝑡𝑎𝑟/60)]

## C_ESG_Design Assistance
COMMERCIAL: Design Assistance
Return to TOC
MEASURE DETAILS
Description
Design Assistance is available to building owners and their design teams to encourage the implementation of energy efficient building systems. Considering energy efficiency during the initial phases of planning and design greatly increase the feasibility of implementation. Incentives for energy efficiency are project-specific and offered as upfront assistance for additional costs incurred during the design phase. The long-term benefits include energy use reduction for the state of Hawai‘i and a reduction in operating costs, equipment lifecycle improvement for building owners, and improved comfort for building users.
Program Criteria
• Application with written pre-approval from Hawai‘i Energy • Project in planning or initial design phase • Total resource benefit ratio greater than or equal to 1
Unit of Measure
n/a
Baseline Equipment
The baseline efficiency case assumes compliance with the efficiency requirements as mandated by the Hawai‘i State Energy Code or industry accepted standard practice.
High Efficiency Equipment
The high efficiency scenario is specific to each project and may include one or more energy efficiency measures. Energy and demand savings calculations are based on comparing a base case analysis and enhanced cased analysis on equipment efficiencies and operating characteristics and are determined on a case-by-case basis. The energy efficiency measures must be proven cost-effective, pass total resource benefit, and have a payback greater than or equal to 1.
ALGORITHMS
Gross energy and demand savings estimates for design assistance are calculated using engineering analysis and project-specific details. Custom analyses typically include a weather dependent load bin analysis, whole building energy model simulation, or other engineering analysis and include estimates of savings, costs, and an evaluation of the project’s cost-effectiveness.
SAVINGS
A base case and enhanced case model must be produced with a clear comparison. All assumptions, data, and formulas used in energy efficiency calculations must be clearly documented. Standard engineering principles must be applied, and all references cited. Energy saving calculations shall also reflect the interactive effects of other simultaneous technologies to prevent the overstatement of actual savings. Proposed base and enhanced cases must be performed by a qualified person or firm. In some cases, a professional engineer may be required to provide verification of the analysis.

## C_ESG_Energy Study
COMMERCIAL: Energy Study
Return to TOC
MEASURE DETAILS
Description
The Energy Study is an indirect impact product that offers Hawai‘i businesses with analysis services to identify energy saving opportunities. The goal of the energy study is to provide a method for commercial and industrial customers to learn how their business uses energy today and to identify measures that will help them save energy and reduce operating costs in the future. The focus is on a customer’s core energy efficiency opportunities.
Program Criteria
• Program approval is required prior to the start of work on the energy study. • The program reserves the right to review all materials that result from a program-supported study including, but not limited to, final reports, consultant recommendations, and metered data. • The study must be performed by a qualified person or firm. A brief summary of the consultant’s qualifications should be submitted with the application. In some cases, a professional engineer may be required to provide verification of the analysis. • At any time, customers may contact program staff to discuss a project, get assistance in preparing an application, or with any program-related questions.
Unit of Measure
n/a
Baseline Equipment
n/a
High Efficiency Equipment
n/a
ALGORITHMS
Gross energy and demand savings estimates for energy studies are calculated using engineering analysis and project-specific details. Energy study analyses typically include estimates of savings, costs, and an evaluation of the cost-effectiveness of potential projects/upgrades.
SAVINGS
All assumptions, data and formulas used in energy efficiency calculations must be clearly documented. Standard engineering principles must be applied, and all references cited. Energy saving calculations shall also reflect the interactive effects of other simultaneous technologies to prevent the overstatement of the actual savings.
The Energy Study shall include the following information and be presented in the following format:
1) Executive Summary
a) Energy Conservation Measures (ECMs) Proposed
b) Summary of Baseline and Enhanced Case Assumptions
c) Actionable Recommendations in “loading order.”
2) Technical Information and Analysis
a) Energy Consumption Analysis
i) Two years of billing data (weatherized and compared to some pertinent operating metric)
b) Description of the project
c) Proposed Energy Conservation Measures (ECM)
i) Descriptive Name
ii) Schematic System Drawing
iii) Current Peak Demand (kW), Energy Usage (kWh), Effective Full Load Run Hours
iv) Proposed Peak Demand (kW), Energy Usage (kWh), Effective Full Load Run Hours
v) % Change for above
vi) Estimated Installation Cost
vii) Project timeline
viii) Measure Life
ix) Simple Payback
d) Base case information
i) Short term/spot baseline thermal, fluid, and electrical measurements for major equipment to be changed with ECMs
ii) Permanent metering data (This metering will qualify for additional cost assistance)
iii) Sizing/Performance Reviews (Pump Curves, Cooling Bin Data etc.)
e) Enhanced case information
i) How will performance be measured in the future.
ii) Description of where energy savings occurs (lower run time, more efficient operations etc.)
f) Estimated energy and demand savings associated with your proposed project
i) Applicable figures and tables
ii) Simple payback period and/or life cycle costs
g) Estimated costs including design, materials, and installation
3) Appendix
a) Raw and Analyzed Data (Cooling Models, Field Data, Pictures, Metering Data etc.)
b) Building Plans (Mechanical, Electrical Schedules, Layouts etc.)

## C_HVAC_Chiller
COMMERCIAL: Chiller
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM to refer to the current Hawaii State Energy Code and to clarify how the code maps to ASHRAE 90.1.
MEASURE DETAILS
Description
The following is a semi-prescriptive method for calculating chiller savings for one-for-one replacements of standalone chillers.
Any chiller project that is part of a larger, multi-system plant should be evaluated as a custom project.1 In addition, a custom approach should be used for early retirement chiller projects and chillers installed in industrial or cold storage applications.
Program Criteria
To be eligible, chiller efficiency must exceed 2018 IECC code (consistent with ASHRAE 90.1-2016 through ASHRAE 90.1-2022), Path A or Path B, by 10% or more.2
Unit of Measure
Savings are calculated per chiller.
Baseline Equipment
The baseline equipment meets the current Hawaii State Energy Code. As of 2024, the code is 2018 IECC with Hawaii State and County amendments. This code is consistent with the current national ASHRAE 90.1 standard that manufacturers adhere to.3
High Efficiency Equipment
High efficiency equipment must exceed ASHRAE efficiencies by 10% or more. An additional tier (20% above ASHRAE) has also been included for this measure. Actual nameplate data for rated efficiency will be compared against ASHRAE standard efficiency.
Note: In PY25 (as in PY22 through PY24), only the part-load efficiency (IPLV) must exceed ASHRAE minimum efficiency requirements by 10% for Tier 1 (or 20% for Tier 2), while the full-load (peak efficiency) must at least meet ASHRAE minimum efficiencies. This is a temporary special exception to increase the number of qualifying chiller projects. The exception will be re-evaluated by PY28.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  |  | Value | Unit | Source/Notes
TONS |  | Chiller rated cooling capacity, in tons | Chiller nominal cooling capacity, in tons |  |  | User input | tons | Capacity thresholds for evaluation as custom project were removed for PY25
PEBL |  | Peak efficiency of baseline chiller at full load |  |  |  | See Chiller Worksheet | kW/ton | Equal to the minimum efficiency requirements of the ASHRAE 90.1-2022 standard
PEEE |  | Peak efficiency of installed high efficiency chiller at full load |  |  |  | User input | kW/ton | Must exceed the minimum efficiency requirements of the ASHRAE 90.1-2022 standard. (Refer to the High Efficiency Equipment description above for more information.)
IPLVBL |  | Part-load efficiency of baseline chiller expressed as Integrated Part Load Value (IPLV), |  |  |  | See Chiller Worksheet | kW/ton | Equal to the minimum efficiency requirements of the ASHRAE 90.1-2022 standard
IPLVEE |  | Part-load efficiency of installed high efficiency chiller |  |  |  | User input | kW/ton | At least 10% better than the ASHRAE 90.1-2022 standard
CF |  | Coincidence factor for commercial cooling with chiller |  |  |  | See Table 1 | - | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period
EFLH |  | Equivalent full load hours for commercial cooling with chiller |  |  |  | See Table 1 | hrs | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes and weather data
EUL |  | Effective useful life of measure |  |  |  | 22 | yrs | Median of various sources from AEG's Fall 2018 Benchmarking
SAVINGS
See accompanying Chiller Worksheet: |  |  |  |  | (C_HVAC_Chiller_WKST)
The following equivalent full load hours and coincidence factors are recommended per building type based on EnergyPlus simulations of DOE prototypes with Honolulu weather (OpenEI datasets).4 Retrofits in cold storage and industrial facilities should be evaluated as custom measures unless the equipment is used for HVAC and not process cooling loads.
Table 1: Equivalent Full Load Hours and Coincidence Factors for Commercial Cooling in Hawai‘i
| Building Type |  |  | EFLH |  |  | CF
| Avg. Commercial |  |  | 2594 |  |  | 0.38
| Cold Storage |  |  | Varies |  |  | Varies
| Education |  |  | 2549 |  |  | 0.43
| Grocery |  |  | 1531 |  |  | 0.27
| Health |  |  | 4891 |  |  | 0.55
| Hotel/Motel |  |  | 4910 |  |  | 0.6
| Industrial |  |  | Varies |  |  | Varies
| Office |  |  | 2754 |  |  | 0.48
| Restaurant |  |  | 2451 |  |  | 0.4
| Retail |  |  | 1913 |  |  | 0.29
| Warehouse |  |  | 1033 |  |  | 0.01
Use custom approach for entries noted as "Varies."
FOOTNOTES
1 | The Uniform Methods Project. Chapter 14: Chiller Evaluation Protocol. September 2017. Available electronically at: <https://docs.nrel.gov/docs/fy17osti/68570.pdf>.
2 | 2018 IECC with Honolulu Amendments, Additional Efficiency Requirements, Commercial Checklist. Available at: <https://energy.hawaii.gov/wp-content/uploads/2023/12/Checklist-2018-IECC_Honolulu_Commercial_2023-12-04.pdf>. Requires efficient HVAC equipment to be 10% better than the minimum efficiency.
3 | All equipment is expected to meet minimum ASHRAE standards. ASHRAE requires a subscription to see the standard in full; AEG used staff subscriptions to ASHRAE to obtain the latest 90.1-2022 standard. AEG confirmed that the minimum standards for chillers per ASHRAE 90.1-2022 are the same as in ASHRAE 90.1-2019 and ASHRAE 90.1-2016. The minimum efficiency levels are also summarized in various publicly available sources.
4 | National Renewable Energy Laboratory. (2014). Commercial and Residential Hourly Load Profiles for all TMY3 Locations in the United States [data set]. Retrieved from <https://dx.doi.org/10.25984/1788456>.
ADDITIONAL RESOURCES
• | ICF's PY26 analysis file named "PY26 TRM - Res Cool Wall and Chiller IECC Edits - Analysis File".
• | ICF's PY25 analysis file named "PY25 TRM - Chiller - Analysis file."
• | AEG's PY22 analysis file named "PY22 C_HVAC_Chiller - Analysis File", AEG's PY20 analysis file named "AEG HPUC - HVAC Measures - Analysis File_Jan 2021," and AEG's PY19 analysis files named "AEG HPUC Update - Commercial Chillers - Analysis File" and "AEG HPUC Mid-Year PY19 TRM Updates_Analysis File."
• | ANSI/ASHRAE/IES Standard 90.1-2022. Available at: <https://www.ashrae.org/technical-resources/bookstore/standard-90-1>.
• | National Renewable Energy Laboratory. (2014). Commercial and Residential Hourly Load Profiles for all TMY3 Locations in the United States [data set]. Retrieved from <https://dx.doi.org/10.25984/1788456>.
• | Ery Djunaedy, Kevin van den Wymelenberg, Brad Acker, Harshana Thimmana, Oversizing of HVAC system: Signatures and penalties, Energy and Buildings, Volume 43, Issues 2–3, 2011, Pages 468-475, ISSN 0378-7788, <https://doi.org/10.1016/j.enbuild.2010.10.011>. Used to determine correct HVAC oversizing adjustment for EFLH and CF analysis.
• | Southern California Edison. Air-Cooled Constant Speed Screw Chiller. Workpaper SCE17HC030, Revision 1. November 16, 2017. Available at: <http://www.deeresources.net/workpapers>.
• | Southern California Edison. Water Cooled Chiller. Workpaper SCE17HC043, Revision 0. November 14, 2017. Available at: <http://www.deeresources.net/workpapers>.
• | 2018 IECC with Honolulu Amendments, Additional Efficiency Requirements, Commercial Checklist. Available at: <https://energy.hawaii.gov/wp-content/uploads/2023/12/Checklist-2018-IECC_Honolulu_Commercial_2023-12-04.pdf>.
• | The Uniform Methods Project. Chapter 14: Chiller Evaluation Protocol. September 2017. Available electronically at: <https://docs.nrel.gov/docs/fy17osti/68570.pdf>.
∆𝑘𝑊=𝑇𝑂𝑁𝑆∗(〖𝑃𝐸〗_𝐵𝐿−〖𝑃𝐸〗_𝐸𝐸 )∗𝐶𝐹
∆𝑘𝑊ℎ=𝑇𝑂𝑁𝑆∗(〖𝐼𝑃𝐿𝑉〗_𝐵𝐿−〖𝐼𝑃𝐿𝑉〗_𝐸𝐸 )∗𝐸𝐹𝐿𝐻
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿

## C_HVAC_Chiller_WKST
COMMERCIAL: Chiller Savings Calculator
Return to TOC
| Step 1: Enter chiller information |  |  | Step 2: Determine if it qualifies |  |  | Step 3: Calculate savings
|  |  |  | Higher than ASHRAE: | 10% Higher? | 20% Higher?
| Enter chiller type: | Air-cooled |  | Path A: | pass | pass | CF: | 0.38
| Enter rated chiller tonnage: | 290 |  | Path B: | fail | fail | EFLH: | 2594 |  | Chiller Types | Range | Column Match | Row Match
| Enter building type: | Avg. Commercial |  |  |  |  | Use: | Path A |  | PD | F34:J37 | 3 |  | A | B
| Enter your FL_ee here: | 1 |  | ASHRAE 90.1 Baseline | Path A | Path B | kW savings: | 20.731 |  | Centrifugal | F40:J43 | 2 | FL | 1 | 3
| Enter your IPLV_ee here: | 0.7 |  | FL_base | 1.1881 | 1.2371 | kWh/yr savings: | 118212.29 |  | Air-cooled | I46:J49 | 2 | IP | 2 | 4
Is the chiller part of a larger, multi-system plant? |  |  |  | IPLV_base | 0.85714 | 0.74534 | Lifetime kWh: | 2600670.38
|  | No |  | FL_delta | 0.18812 | 0.23711 | Meets | Tier 2 (ASHRAE + 20%) |  | Path A | Tier 1 (ASHRAE + 10%)
|  |  |  | IPLV_delta: | 0.15714 | 0.045342 |  |  |  | Path B | Tier 2 (ASHRAE + 20%)
ASHRAE 90.1-2022 + 10% (Efficient Case Minimum) | Positive Displacement (Reciprocating, Rotary Screw, Scroll) | Units: kW/ton |  | < 75 Tons | >= 75 tons & < 150 tons | >= 150 tons & < 300 tons | >= 300 tons & < 600 tons | >= 600 tons | path a/path b values + 10%
|  | Path A | FL | 0.675 | 0.648 | 0.594 | 0.549 | 0.504 | 1
|  |  | IPLV | 0.54 | 0.504 | 0.486 | 0.468 | 0.45 | 2
|  | Path B | FL | 0.702 | 0.675 | 0.612 | 0.5625 | 0.5265 | 4
|  |  | IPLV | 0.45 | 0.441 | 0.396 | 0.369 | 0.342 | 5
| Centrifugal | Units: kW/ton |  | < 150 Tons | >= 150 tons & < 300 tons | >= 300 tons & < 400 tons | >= 400 tons & < 600 tons | >= 600 tons
|  | Path A | FL | 0.549 | 0.549 | 0.504 | 0.504 | 0.504 | 6 |  | Pass/Fail Test
|  |  | IPLV | 0.495 | 0.495 | 0.468 | 0.45 | 0.45 | 7 |  |  | FL | IPLV | FL+IPLV
|  | Path B | FL | 0.6255 | 0.5715 | 0.5355 | 0.5265 | 0.5265 | 10 |  | Path A+10% | 22 | 22 | 44
|  |  | IPLV | 0.396 | 0.36 | 0.351 | 0.342 | 0.342 | 11 |  | Path B+10% | 34 | 0 | 34
| Air-cooled with condenser | Units: EER (Btu/W) |  | < 150 Tons | >= 150 Tons | Units: kW/ton | < 150 Tons | >= 150 Ton
|  | Path A | FL | 11.11 | 11.11 | Path A | 1.0801 | 1.0801 | 22
|  |  | IPLV | 15.07 | 15.4 |  | 0.79628 | 0.77922 | 22
|  | Path B | FL | 10.67 | 10.67 | Path B | 1.1246 | 1.1246 | 34
|  |  | IPLV | 17.38 | 17.71 |  | 0.69045 | 0.67758 | 36
ASHRAE 90.1-2022 (Baseline) | Positive Displacement (Reciprocating, Rotary Screw, Scroll) | Units: kW/ton |  | < 75 Tons | >= 75 tons & < 150 tons | >= 150 tons & < 300 tons | >= 300 tons & < 600 tons | >= 600 tons
|  | Path A | FL | 0.75 | 0.72 | 0.66 | 0.61 | 0.56
|  |  | IPLV | 0.6 | 0.56 | 0.54 | 0.52 | 0.5
|  | Path B | FL | 0.78 | 0.75 | 0.68 | 0.625 | 0.585
|  |  | IPLV | 0.5 | 0.49 | 0.44 | 0.41 | 0.38
| Centrifugal | Units: kW/ton |  | < 150 Tons | >= 150 tons & < 300 tons | >= 300 tons & < 400 tons | >= 400 tons & < 600 tons | >= 600 tons
|  | Path A | FL | 0.61 | 0.61 | 0.56 | 0.56 | 0.56
|  |  | IPLV | 0.55 | 0.55 | 0.52 | 0.5 | 0.5
|  | Path B | FL | 0.695 | 0.635 | 0.595 | 0.585 | 0.585
|  |  | IPLV | 0.44 | 0.4 | 0.39 | 0.38 | 0.38
| Air-cooled with condenser | Units: EER (Btu/W) |  | < 150 Tons | >= 150 Tons | Units: kW/ton | < 150 Tons | >= 150 Ton
|  | Path A | FL | 10.1 | 10.1 | Path A | 1.1881 | 1.1881
|  |  | IPLV | 13.7 | 14 |  | 0.87591 | 0.85714
|  | Path B | FL | 9.7 | 9.7 | Path B | 1.2371 | 1.2371
|  |  | IPLV | 15.8 | 16.1 |  | 0.75949 | 0.74534
ASHRAE 90.1-2022 (Efficient Case Tier 2) | Positive Displacement (Reciprocating, Rotary Screw, Scroll) | Units: kW/ton |  | < 75 Tons | >= 75 tons & < 150 tons | >= 150 tons & < 300 tons | >= 300 tons & < 600 tons | >= 600 tons | path a/path b values + 10%
|  | Path A | FL | 0.6 | 0.576 | 0.528 | 0.488 | 0.448 | 1
|  |  | IPLV | 0.48 | 0.448 | 0.432 | 0.416 | 0.4 | 2
|  | Path B | FL | 0.624 | 0.6 | 0.544 | 0.5 | 0.468 | 4
|  |  | IPLV | 0.4 | 0.392 | 0.352 | 0.328 | 0.304 | 5
| Centrifugal | Units: kW/ton |  | < 150 Tons | >= 150 tons & < 300 tons | >= 300 tons & < 400 tons | >= 400 tons & < 600 tons | >= 600 tons
|  | Path A | FL | 0.488 | 0.488 | 0.448 | 0.448 | 0.448 | 6 |  | Pass/Fail Test
|  |  | IPLV | 0.44 | 0.44 | 0.416 | 0.4 | 0.4 | 7 |  |  | FL | IPLV | FL+IPLV
|  | Path B | FL | 0.556 | 0.508 | 0.476 | 0.468 | 0.468 | 10 |  | Path A+10% | 22 | 22 | 44
|  |  | IPLV | 0.352 | 0.32 | 0.312 | 0.304 | 0.304 | 11 |  | Path B+10% | 34 | 0 | 34
| Air-cooled with condenser | Units: EER (Btu/W) |  | < 150 Tons | >= 150 Tons | Units: kW/ton | < 150 Tons | >= 150 Ton
|  | Path A | FL | 12.12 | 12.12 | Path A | 0.9901 | 0.9901 | 22
|  |  | IPLV | 16.44 | 16.8 |  | 0.72993 | 0.71429 | 22
|  | Path B | FL | 11.64 | 11.64 | Path B | 1.0309 | 1.0309 | 34
|  |  | IPLV | 18.96 | 19.32 |  | 0.63291 | 0.62112 | 36
Note on F4: Full-load requirement was reevaluated for PY25, and this was not reinstated given manufacturers still have difficulty surpassing the 10% above minimum requirement in Hawaii. See hidden cells P23, P24, P65, and P66 for updates to formulas should the full-load requirement be reinstated in the future.
Note on C8: Please enter your full-load efficiency rating here, in kW/ton
Note on J8: delta * tonnage * CF
Note on C9: Please enter your IPLV (part load) efficiency rating here, in kW/ton
Note on J9: delta * tonnage * EFLH
Note on P23: If full load efficiency requirement is reinstated, change back to following eq'n: =IF($D$5="PD", IF(AND($D$6>=600,$D$8<=J$15),$M15, IF(AND($D$6>=300,$D$6<600,$D$8<=$I15),$M15, IF(AND($D$6>=150,$D$6<300,$D$8<=$H15),$M15, IF(AND($D$6>=75,$D$6<150,$D$8<=$G15),$M15, IF(AND($D$6<75,$D$8<=F15),$M15,0))))), IF($D$5="centrifugal", IF(AND($D$6>=600,$D$8<=J21),M21, IF(AND($D$6>=400,$D$6<600,$D$8<=I21),M21, IF(AND($D$6>=300,$D$6<400,$D$8<=H21),M21, IF(AND($D$6>=150,$D$6<300,$D$8<=G21),M21, IF(AND($D$6<150,$D$8<=F21),M21,0))))), IF($D$5="air-cooled", IF(AND($D$6>=150,$D$8<=J27),M27, IF(AND($D$6<150,$D$8<=I27),M27,0)))))
Note on P24: If full load efficiency requirement is reinstated, change back to following eq'n: =IF($D$5="PD", IF(AND($D$6>=600,$D$8<=$J17),$M17, IF(AND($D$6>=300,$D$6<600,$D$8<=$I17),$M17, IF(AND($D$6>=150,$D$6<300,$D$8<=$H17),$M17, IF(AND($D$6>=75,$D$6<150,$D$8<=$G17),$M17, IF(AND($D$6<75,$D$8<=F17),$M17,0))))), IF($D$5="centrifugal", IF(AND($D$6>=600,$D$8<=J23),M23, IF(AND($D$6>=400,$D$6<600,$D$8<=I23),M23, IF(AND($D$6>=300,$D$6<400,$D$8<=H23),M23, IF(AND($D$6>=150,$D$6<300,$D$8<=G23),M23, IF(AND($D$6<150,$D$8<=F23),M23,0))))), IF($D$5="air-cooled", IF(AND($D$6>=150,$D$8<=J29),M29, IF(AND($D$6<150,$D$8<=I29),M29,0)))))
Note on P65: If full load efficiency requirement is reinstated, change back to following eq'n: =IF($D$5="PD", IF(AND($D$6>=600,$D$8<=J$57),$M57, IF(AND($D$6>=300,$D$6<600,$D$8<=$I57),$M57, IF(AND($D$6>=150,$D$6<300,$D$8<=$H57),$M57, IF(AND($D$6>=75,$D$6<150,$D$8<=$G57),$M57, IF(AND($D$6<75,$D$8<=F57),$M57,0))))), IF($D$5="centrifugal", IF(AND($D$6>=600,$D$8<=J63),M63, IF(AND($D$6>=400,$D$6<600,$D$8<=I63),M63, IF(AND($D$6>=300,$D$6<400,$D$8<=H63),M63, IF(AND($D$6>=150,$D$6<300,$D$8<=G63),M63, IF(AND($D$6<150,$D$8<=F63),M63,0))))), IF($D$5="air-cooled", IF(AND($D$6>=150,$D$8<=J69),M69, IF(AND($D$6<150,$D$8<=I69),M69,0)))))
Note on P66: If full load efficiency requirement is reinstated, change back to following eq'n: =IF($D$5="PD", IF(AND($D$6>=600,$D$8<=$J59),$M59, IF(AND($D$6>=300,$D$6<600,$D$8<=$I59),$M59, IF(AND($D$6>=150,$D$6<300,$D$8<=$H59),$M59, IF(AND($D$6>=75,$D$6<150,$D$8<=$G59),$M59, IF(AND($D$6<75,$D$8<=F59),$M59,0))))), IF($D$5="centrifugal", IF(AND($D$6>=600,$D$8<=J65),M65, IF(AND($D$6>=400,$D$6<600,$D$8<=I65),M65, IF(AND($D$6>=300,$D$6<400,$D$8<=H65),M65, IF(AND($D$6>=150,$D$6<300,$D$8<=G65),M65, IF(AND($D$6<150,$D$8<=F65),M65,0))))), IF($D$5="air-cooled", IF(AND($D$6>=150,$D$8<=J71),M71, IF(AND($D$6<150,$D$8<=I71),M71,0)))))

## C_HVAC_AC & Heat Pump
COMMERCIAL: AC & Heat Pump
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the PY25 TRM. Reevaluate the full load efficiency requirement for split-system and single-package air-cooled AC and air-source heat pump systems by PY28.
MEASURE DETAILS
Description
Like-for-like replacement of air conditioner (AC) and heat pump (HP) systems with higher efficiency models. Technologies include the following:
| • | Single-phase split-system and single-package air-cooled AC and air-source HP with capacities < 65,000 Btu/h (residential-scale)
| • | Three-phase split-system and single-package air-cooled AC and air-source HP with capacities < 65,000 Btu/h (commercial-scale)
| • | Unitary split-system and single-package air-cooled AC and air-source HP with capacities ≥ 65,000 and < 240,000 Btu/h
| • | Water-source HP (water-to-air, water loop) with capacities < 135,000 Btu/h
| • | Packaged terminal air conditioner (PTAC), standard and non-standard
| • | Packaged terminal heat pump (PTHP), standard and non-standard
| • | Single-package vertical AC and HP with capacities < 135,000 Btu/h
Program Criteria
Residential-scale single-phase split-system and single-package air-cooled AC and air-source HP systems with capacities < 65,000 Btu/h must meet or exceed 15.2 SEER2.
All other eligible equipment shall have a minimum rated efficiency that is at least 10% higher than the energy code-compliant standard for equivalently-sized equipment.
The following AC and HP projects should be evaluated using a custom approach:
| • | Split/single package AC and air-source HP systems with capacities ≥ 240,000 Btu/h in total
| • | Vertical AC and HP systems with capacities ≥ 240,000 Btu/h in total
| • | Water-source HP systems with capacities ≥ 135,000 Btu/h in total
| • | Early retirement (ER) projects
| • | If not like-for-like replacement
| • | Installations in industrial or cold storage applications
Unit of Measure
Measure impacts are calculated per system.
Baseline Equipment
The baseline equipment meets the current federal and state requirements and ASHRAE 90.1-2019 standards as of January 1, 2025. Split-system and single-package air-cooled AC and air-source HP systems with capacities < 65,000 Btu/h have minimum SEER2 requirements. Split-system and single-package air-cooled AC and air-source HP systems with capacities ≥ 65,000 Btu/h have minimum IEER requirements. Water-source HP, PTAC, PTAC, vertical AC, and vertical HP systems have minimum EER requirements.
Split-system and single-package air-cooled AC and air-source HP systems do not have state, federal, or ASHRAE minimum EER2 (or EER) requirements. An "industry standard practice" baseline was used to calculate the peak demand savings. It involved setting the baseline values equal to the most common EER2 (or EER) value for the given SEER2 (or IEER) minimum requirement, as determined through analysis of AHRI data.
Water-source HP, PTAC, PTAC, vertical AC, and vertical HP systems do not have state, federal, or ASHRAE minimum SEER (or IEER) requirements. The baseline SEER (or IEER) values were set equal to the baseline EER requirements in the calculation worksheet to calculate energy savings.
The baseline assumes the customer would install the minimum efficiency alternative in a like-for-like replacement.
The semi-prescriptive savings approach presented here assumes replace-on-burnout (ROB). A custom dual baseline approach is required for early retirement (ER) projects: use the pre-existing equipment for the 1st ER baseline; use ASHRAE 90.1-2019 and current state requirements for the 2nd ER baseline. Documentation that shows the pre-existing equipment was operating and had a meaningful remaining useful life before replacement is required to be eligible for a custom ER savings approach.
High Efficiency Equipment
Residential-scale high efficiency equipment must meet or exceed 15.2 SEER2. All other eligible high efficiency equipment must exceed ASHRAE minimum efficiencies by 10% or more, as applicable for the given system type. An additional tier (20% above ASHRAE) has also been included for this measure. Actual nameplate data for rated efficiency will be compared against the ASHRAE standard efficiency.
There are no program requirements for full-load efficiency (EER2 or EER) for split-system and single-package air-cooled AC and air-source HP systems.
Water-source heat pump, PTAC, PTAC, vertical AC, and vertical HP systems do not have state, federal, or ASHRAE minimum SEER (or IEER) requirements. Therefore, the high efficiency SEER (or IEER) values have been set equal to the high efficiency EER requirements in the calculation worksheet.
ALGORITHMS
Peak Demand Reduction, kW
(1)
[EER2 used in place of EER for split/single-package AC and HP units <65,000 Btu/h]
Annual Energy Savings, kWh/yr
(2)
[SEER2 used in place of IEER for split/single-package AC and HP units <65,000 Btu/h]
[SEER used in place of IEER for all other units <65,000 Btu/h]
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | Value |  | Unit | Source/Notes
Capacity |  |  |  | Rated capacity, in Btu/h, of installed unit | Based on installed unit |  | Btu/h | As installed
EERBL or EER2BL |  |  |  | Energy Efficiency Ratio of baseline unit. Used to represent full-load operation. | See Table 1 in C_HVAC_AC_HP_WKST |  | Btu/Wh | Equal to the state, federal, and ASHRAE 90.1-2019 minimum efficiency requirements, as applicable to the given system type. (Refer to the Baseline Equipment description above for more information.)
EEREE or EER2EE |  |  |  | Energy Efficiency Ratio of installed high efficiency unit. Used to represent full-load operation. | User input |  | Btu/Wh | As installed. At least 10% better than the baseline efficiency, as applicable to the given system type. (Refer to the High Efficiency Equipment description above for more information.)
IEERBL, SEER2BL or SEERBL |  |  |  | Integrated or Seasonal Energy Efficiency Ratio of baseline unit. Used to represent part-load operation. SEER2 or SEER is used for units <65,000 Btu/h. | See Table 1 in C_HVAC_AC_HP_WKST |  | Btu/Wh | Equal to the state, federal, and ASHRAE 90.1-2019 minimum efficiency requirements, as applicable to the given system type. (Refer to the Baseline Equipment description above for more information.)
IEEREE, SEER2EE or SEEREE |  |  |  | Integrated or Seasonal Energy Efficiency Ratio of installed high efficiency unit. Used to represent part-load operation. SEER2 or SEER is used for units <65,000 Btu/h. | User input |  | Btu/Wh | As installed. At least 10% better than the baseline efficiency, as applicable to the given system type. (Refer to the High Efficiency Equipment description above for more information.)
EFLH |  |  |  | Equivalent full load cooling hours | See Table 4 in C_HVAC_AC_HP_WKST |  | hrs | AEG's analysis of DOE's OpenEI load shapes using Hawaii-specific prototypes and weather data
CF |  |  |  | Coincidence factor | See Table 4 in C_HVAC_AC_HP_WKST |  | - | AEG's analysis of DOE's OpenEI load shapes using Hawaii-specific prototypes, weather data, and peak demand period
EUL |  |  |  | Effective useful life of measure | 15 |  | years | AEG's Fall 2018 Benchmarking
SAVINGS
| For calculations specific to the unit in question, please see the accompanying AC and HP calculation worksheet: |  |  |  |  | (C_HVAC_AC_HP_WKST)
RESOURCES
• | ICF's PY25 Analysis File named "PY25 TRM - Commercial HVAC - Analysis file."
• | AEG's PY23 Analysis File named "PY23 TRM - Commercial AC and HP - Analysis File."
• | AEG's PY22 Analysis File named "PY22 C_HVAC_AC & Heat Pump - Analysis file."
• | AEG's PY20 Analysis Files named "AEG HPUC C_HVAC_VRF AC & HP - Analysis File" and "AEG HPUC - HVAC Measures - Analysis File_Jan 2021."
• | Air-Conditioning, Heating, & Refrigeration Institute (AHRI), Directory of Certified Products, accessed Sep. 2022, Nov. 2022, and Apr. 2025, available here: <https://ahridirectory.org/>.
• | ANSI/ASHRAE/IES Standard 90.1-2019, Energy Standard for Buildings Except Low-Rise Residential Buildings, (I-P Edition), 2019, available here: <https://www.ashrae.org/technical-resources/bookstore/standard-90-1>.
• | Code of Federal Regulations, 10 CFR 430.32, Subpart C, Energy and Water Conservation Standards and their Effective Dates, Paragraph (c): Central Air Conditioners and Heat Pumps, available here: <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>.
• | Code of Federal Regulations, 10 CFR 431.97, Subpart F, Energy Efficiency Standards and their Compliance Dates, Paragraphs (b), (c), and (d), available here: <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-F/subject-group-ECFR2640f6ad978e4e6/section-431.97>.
• | National Renewable Energy Laboratory. (2014). Commercial and Residential Hourly Load Profiles for all TMY3 Locations in the United States [data set]. Retrieved from <https://dx.doi.org/10.25984/1788456>.
• | Ery Djunaedy, Kevin van den Wymelenberg, Brad Acker, Harshana Thimmana, Oversizing of HVAC system: Signatures and penalties, Energy and Buildings, Volume 43, Issues 2–3, 2011, Pages 468-475, ISSN 0378-7788, <https://doi.org/10.1016/j.enbuild.2010.10.011>. Used to determine correct HVAC oversizing adjustment for EFLH and CF analysis.
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅〗_𝐵𝐿−〗 1∕〖〖𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐶𝐹
∆𝑘𝑊ℎ=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐼𝐸𝐸𝑅〗_𝐵𝐿−〗 1∕〖〖𝐼𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻

## C_HVAC_AC_HP_WKST
Commercial: Air Conditioning & Heat Pump Savings Worksheet
Return to TOC | [9 empty] | Lookup/Data Validation Tables
Revise or remove notes in Cells G6 and G7
| Step 1: Enter AC or HP nameplate data* |  |  |  | Step 2: Determine if it qualifies |  |  | Step 3: Calculate savings |  | Single-Phase Split System AC
[6 empty] | Full Load | Part Load |  |  | Single-Phase Single Package AC
| Enter AC or HP Type: | Single-Phase Single Package AC |  |  | Tier 1 | NA | Pass | CF: | 0.48 | Three-Phase Split System AC
| Enter Rated AC or HP Capacity (Btu/h): | 64000 |  |  | Tier 2 | NA | Fail | EFLH: | 2754 | Three-Phase Single Package AC
| Enter Building Type: | Office | [5 empty] | kW savings: | 0 | Split System & Single Package AC
| Enter Full Load Efficiency: | 10.6 | EER or EER2 |  | Capacity Bin: | < 65,000 Btu/h |  | kWh/yr savings: | 1557.64 | Single-Phase Split System HP
| Enter Part-Load Efficiency: | 15.2 | SEER or SEER2 |  | Corresponding Baseline Efficiency (Full Load): | 10.6 | EER or EER2 | Lifetime kWh: | 23364.6 | Single-Phase Single Package HP
| Notes: 1) If an efficiency value is unknown, check AHRI Directory (www.ahridirectory.org); 2) Use EER2 and SEER2 for Split System and Single Package Systems < 65,000 Btu/h. |  |  |  | Corresponding Baseline Efficiency (Part-Load): | 13.4 | SEER or SEER2 | Meets | Tier 1 | Three-Phase Split System Air-Source HP
Three-Phase Single Package Air-Source HP
Air-Source HP
Water-Source HP
PTAC (Std)
| Table 1: Minimum Baseline Efficiencies; Assumes Like-for-Like Replacement | [8 empty] | PTAC (Non-Std)
| System Type | Capacity Bin | Part-Load Efficiency |  | Full Load Efficiency |  |  |  |  | PTHP (Std)
|  |  | SEER or SEER2 | IEER | EER or EER2 | Concatenation |  |  |  | PTHP (Non-Std)
| Single-Phase Split System AC | < 45,000 Btu/h | 14.3 | -- | 11.7 | Single-Phase Split System AC - < 45,000 Btu/h |  |  |  | Vertical AC or HP
| Single-Phase Split System AC | ≥ 45,000 and < 65,000 Btu/h | 13.8 | -- | 11.2 | Single-Phase Split System AC - ≥ 45,000 and < 65,000 Btu/h
| Single-Phase Single Package AC | < 65,000 Btu/h | 13.4 | -- | 10.6 | Single-Phase Single Package AC - < 65,000 Btu/h |  |  |  | SEER or IEER?
| Three-Phase Split System AC | < 65,000 Btu/h | 13.4 | -- | 10.6 | Three-Phase Split System AC - < 65,000 Btu/h |  |  |  | SEER or SEER2
| Three-Phase Single Package AC | < 65,000 Btu/h | 13.4 | -- | 10.6 | Three-Phase Single Package AC - < 65,000 Btu/h |  |  |  | IEER
| Split System & Single Package AC | ≥ 65,000 and < 135,000 Btu/h | -- | 14.8 | 11.2 | Split System & Single Package AC - ≥ 65,000 and < 135,000 Btu/h
| Split System & Single Package AC | ≥ 135,000 and < 240,000 Btu/h | -- | 14.2 | 11 | Split System & Single Package AC - ≥ 135,000 and < 240,000 Btu/h
| Split System & Single Package AC | ≥ 240,000 Btu/h | -- | 13.2 | 10 | Split System & Single Package AC - ≥ 240,000 Btu/h |  |  |  | 1000 | < 65,000 Btu/h
| Single-Phase Split System HP | < 65,000 Btu/h | 14.3 | -- | 11.7 | Single-Phase Split System HP - < 65,000 Btu/h |  |  |  | 65000 | ≥ 65,000 and < 135,000 Btu/h
| Single-Phase Single Package HP | < 65,000 Btu/h | 13.4 | -- | 10.6 | Single-Phase Single Package HP - < 65,000 Btu/h |  |  |  | 135000 | ≥ 135,000 and < 240,000 Btu/h
| Three-Phase Split System Air-Source HP | < 65,000 Btu/h | 14.3 | -- | 11.7 | Three-Phase Split System Air-Source HP - < 65,000 Btu/h |  |  |  | 240000 | ≥ 240,000 Btu/h
| Three-Phase Single Package Air-Source HP | < 65,000 Btu/h | 13.4 | -- | 10.6 | Three-Phase Single Package Air-Source HP - < 65,000 Btu/h
| Air-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 14.1 | 11 | Air-Source HP - ≥ 65,000 and < 135,000 Btu/h |  |  |  | 1000 | < 17,000 Btu/h
| Air-Source HP | ≥ 135,000 and < 240,000 Btu/h | -- | 13.5 | 10.6 | Air-Source HP - ≥ 135,000 and < 240,000 Btu/h |  |  |  | 17000 | ≥ 17,000 and < 65,000 Btu/h
| Air-Source HP | ≥ 240,000 Btu/h | -- | 12.5 | 9.5 | Air-Source HP - ≥ 240,000 Btu/h |  |  |  | 65000 | ≥ 65,000 and < 135,000 Btu/h
| Water-Source HP | < 17,000 Btu/h | 12.2 | -- | 12.2 | Water-Source HP - < 17,000 Btu/h |  |  |  | 135000 | ≥ 135,000 Btu/h
| Water-Source HP | ≥ 17,000 and < 65,000 Btu/h | 13 | -- | 13 | Water-Source HP - ≥ 17,000 and < 65,000 Btu/h
| Water-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 13 | 13 | Water-Source HP - ≥ 65,000 and < 135,000 Btu/h |  |  |  | 1000 | < 45,000 Btu/h
| PTAC (Std) | < 7,000 Btu/h | 11.9 | -- | 11.9 | PTAC (Std) - < 7,000 Btu/h |  |  |  | 45000 | ≥ 45,000 and < 65,000 Btu/h
| PTAC (Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -5.2 | -- | -5.2 | PTAC (Std) - ≥ 7,000 and ≤ 15,000 Btu/h |  |  |  | 65000 | ≥ 65,000
| PTAC (Std) | > 15,000 and < 65,000 Btu/h | 9.5 | -- | 9.5 | PTAC (Std) - > 15,000 and < 65,000 Btu/h
| PTAC (Non-Std) | < 7,000 Btu/h | 9.4 | -- | 9.4 | PTAC (Non-Std) - < 7,000 Btu/h |  |  |  | 1000 | < 7,000 Btu/h
| PTAC (Non-Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -2.7 | -- | -2.7 | PTAC (Non-Std) - ≥ 7,000 and ≤ 15,000 Btu/h |  |  |  | 7000 | ≥ 7,000 and ≤ 15,000 Btu/h
| PTAC (Non-Std) | > 15,000 and < 65,000 Btu/h | 7.7 | -- | 7.7 | PTAC (Non-Std) - > 15,000 and < 65,000 Btu/h |  |  |  | 15001 | > 15,000 and < 65,000 Btu/h
| PTHP (Std) | < 7,000 Btu/h | 11.9 | -- | 11.9 | PTHP (Std) - < 7,000 Btu/h |  |  |  | 65000 | ≥ 65,000
| PTHP (Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -5.2 | -- | -5.2 | PTHP (Std) - ≥ 7,000 and ≤ 15,000 Btu/h
| PTHP (Std) | > 15,000 and < 65,000 Btu/h | 9.5 | -- | 9.5 | PTHP (Std) - > 15,000 and < 65,000 Btu/h |  |  |  | 1000 | < 65,000 Btu/h
| PTHP (Non-Std) | < 7,000 Btu/h | 9.3 | -- | 9.3 | PTHP (Non-Std) - < 7,000 Btu/h |  |  |  | 65000 | ≥ 65,000 and < 240,000 Btu/h
| PTHP (Non-Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -2.8 | -- | -2.8 | PTHP (Non-Std) - ≥ 7,000 and ≤ 15,000 Btu/h |  |  |  | 240000 | ≥ 240,000 Btu/h
| PTHP (Non-Std) | > 15,000 and < 65,000 Btu/h | 7.6 | -- | 7.6 | PTHP (Non-Std) - > 15,000 and < 65,000 Btu/h
| Vertical AC or HP | < 65,000 Btu/h | 11 | -- | 11 | Vertical AC or HP - < 65,000 Btu/h
| Vertical AC or HP | ≥ 65,000 and < 240,000 Btu/h | -- | 10 | 10 | Vertical AC or HP - ≥ 65,000 and < 240,000 Btu/h
Table 2: Minimum Qualifying Efficiencies - Tier 1
| System Type | Capacity Bin | Part-Load Efficiency |  | Full Load Efficiency
|  |  | SEER | IEER | EER
| Single-Phase Split System AC | < 45,000 Btu/h | 15.2 | -- | NA
| Single-Phase Split System AC | ≥ 45,000 and < 65,000 Btu/h | 15.2 | -- | NA
| Single-Phase Single Package AC | < 65,000 Btu/h | 15.2 | -- | NA
| Three-Phase Split System AC | < 65,000 Btu/h | 14.7 | -- | NA
| Three-Phase Single Package AC | < 65,000 Btu/h | 14.7 | -- | NA
| Split System & Single Package AC | ≥ 65,000 and < 135,000 Btu/h | -- | 16.3 | NA
| Split System & Single Package AC | ≥ 135,000 and < 240,000 Btu/h | -- | 15.6 | NA
| Split System & Single Package AC | ≥ 240,000 Btu/h | -- | 14.5 | NA
| Single-Phase Split System HP | < 65,000 Btu/h | 15.2 |  | NA
| Single-Phase Single Package HP | < 65,000 Btu/h | 15.2 |  | NA
| Three-Phase Split System Air-Source HP | < 65,000 Btu/h | 15.7 |  | NA
| Three-Phase Single Package Air-Source HP | < 65,000 Btu/h | 14.7 |  | NA
| Air-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 15.5 | NA
| Air-Source HP | ≥ 135,000 and < 240,000 Btu/h | -- | 14.9 | NA
| Air-Source HP | ≥ 240,000 Btu/h | -- | 13.8 | NA
| Water-Source HP | < 17,000 Btu/h | 13.4 | -- | 13.4
| Water-Source HP | ≥ 17,000 and < 65,000 Btu/h | 14.3 | -- | 14.3
| Water-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 14.3 | 14.3
| PTAC (Std) | < 7,000 Btu/h | 13.1 | -- | 13.1
| PTAC (Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -5.7 | -- | -5.7
| PTAC (Std) | > 15,000 and < 65,000 Btu/h | 10.5 | -- | 10.5
| PTAC (Non-Std) | < 7,000 Btu/h | 10.3 | -- | 10.3
| PTAC (Non-Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -3 | -- | -3
| PTAC (Non-Std) | > 15,000 and < 65,000 Btu/h | 8.5 | -- | 8.5
| PTHP (Std) | < 7,000 Btu/h | 13.1 | -- | 13.1
| PTHP (Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -5.7 | -- | -5.7
| PTHP (Std) | > 15,000 and < 65,000 Btu/h | 10.5 | -- | 10.5
| PTHP (Non-Std) | < 7,000 Btu/h | 10.2 | -- | 10.2
| PTHP (Non-Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -3.1 | -- | -3.1
| PTHP (Non-Std) | > 15,000 and < 65,000 Btu/h | 8.4 | -- | 8.4
| Vertical AC or HP | < 65,000 Btu/h | 12.1 | -- | 12.1
| Vertical AC or HP | ≥ 65,000 and < 240,000 Btu/h | -- | 11 | 11
Table 3: Minimum Qualifying Efficiencies - Tier 2
| System Type | Capacity Bin | Part-Load Efficiency |  | Full Load Efficiency
|  |  | SEER | IEER | EER
| Single-Phase Split System AC | < 45,000 Btu/h | 16.7 | -- | NA
| Single-Phase Split System AC | ≥ 45,000 and < 65,000 Btu/h | 16.7 | -- | NA
| Single-Phase Single Package AC | < 65,000 Btu/h | 16.7 | -- | NA
| Three-Phase Split System AC | < 65,000 Btu/h | 16.1 | -- | NA
| Three-Phase Single Package AC | < 65,000 Btu/h | 16.1 | -- | NA
| Split System & Single Package AC | ≥ 65,000 and < 135,000 Btu/h | -- | 17.8 | NA
| Split System & Single Package AC | ≥ 135,000 and < 240,000 Btu/h | -- | 17 | NA
| Split System & Single Package AC | ≥ 240,000 Btu/h | -- | 15.8 | NA
| Single-Phase Split System HP | < 65,000 Btu/h | 16.7 |  | NA
| Single-Phase Single Package HP | < 65,000 Btu/h | 16.7 |  | NA
| Three-Phase Split System Air-Source HP | < 65,000 Btu/h | 17.2 |  | NA
| Three-Phase Single Package Air-Source HP | < 65,000 Btu/h | 16.1 |  | NA
| Air-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 16.9 | NA
| Air-Source HP | ≥ 135,000 and < 240,000 Btu/h | -- | 16.2 | NA
| Air-Source HP | ≥ 240,000 Btu/h | -- | 15 | NA
| Water-Source HP | < 17,000 Btu/h | 14.6 | -- | 14.6
| Water-Source HP | ≥ 17,000 and < 65,000 Btu/h | 15.6 | -- | 15.6
| Water-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 15.6 | 15.6
| PTAC (Std) | < 7,000 Btu/h | 14.3 | -- | 14.3
| PTAC (Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -6.2 | -- | -6.2
| PTAC (Std) | > 15,000 and < 65,000 Btu/h | 11.4 | -- | 11.4
| PTAC (Non-Std) | < 7,000 Btu/h | 11.3 | -- | 11.3
| PTAC (Non-Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -3.2 | -- | -3.2
| PTAC (Non-Std) | > 15,000 and < 65,000 Btu/h | 9.2 | -- | 9.2
| PTHP (Std) | < 7,000 Btu/h | 14.3 | -- | 14.3
| PTHP (Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -6.2 | -- | -6.2
| PTHP (Std) | > 15,000 and < 65,000 Btu/h | 11.4 | -- | 11.4
| PTHP (Non-Std) | < 7,000 Btu/h | 11.2 | -- | 11.2
| PTHP (Non-Std) | ≥ 7,000 and ≤ 15,000 Btu/h | -3.4 | -- | -3.4
| PTHP (Non-Std) | > 15,000 and < 65,000 Btu/h | 9.1 | -- | 9.1
| Vertical AC or HP | < 65,000 Btu/h | 13.2 | -- | 13.2
| Vertical AC or HP | ≥ 65,000 and < 240,000 Btu/h | -- | 12 | 12
Table 4: Equivalent Full Load Hours and Coincident Factors for Commercial Cooling in Hawai‘i
| Building Type | EFLH | CF
| Avg. Commercial | 2594 | 0.38
| Cold Storage | Varies | Varies
| Education | 2549 | 0.43
| Grocery | 1531 | 0.27
| Health | 4891 | 0.55
| Hotel/Motel | 4910 | 0.6
| Industrial | Varies | Varies
| Office | 2754 | 0.48
| Restaurant | 2451 | 0.4
| Retail | 1913 | 0.29
| Warehouse | 1033 | 0.01
Note on G6: Reevaluate requirement by PY28.
Note on G7: Reevaluate requirement by PY28.
Note on D10: Will change according to AC size
Note on H11: Will change according to AC size
Note on F19: There is no federal or state minimum EER2 requirement for Hawaii. AEG's research of the AHRI database (Nov 2022 extracts) showed that each EER2 value in Table 1 represents the most common EER2 value for the given SEER2 minimum requirement. Refer to AEG's Analysis File named "PY23 TRM - Commercial AC and HP - Analysis File" for more information. These EER2 values are also consistent with ASHRAE's minimum requirements for single-phase central ACs and HPs in the Southwestern region (see Table F-1, ASHRAE 90.1-2019). Note that ASHRAE considers Hawaii to be part of the Southeastern region, which does not have minimum EER2 requirements.
Note on F24: There are no longer federal or ASHRAE minimum EER requirements for larger commercial unitary AC and Air-Source HP equipment (≥ 65,000 Btu/h). AEG's research of the AHRI database (Apr 2025 extract) showed that each EER value in Table 1 represents the most common EER value for the given IEER minimum requirement. These EER values also match the previous minimum federal code and ASHRAE 90.1-2016 standards for EER. Refer to AEG's Analysis File named "PY25 TRM - Commercial HVAC - Analysis File" for more information.
Note on C26: All units greater than 240 kBtu/h are recommended for custom evaluation
Note on R29: All units greater than 240 kBtu/h are recommended for custom evaluation
Note on D34: No ASHRAE requirement for water-source HP SEER; set equal to EER
Note on E36: No ASHRAE requirement for water-source HP IEER; set equal to EER
Note on D37: No ASHRAE requirement for PTAC/PTHP SEER; set equal to EER
Note on F38: PTAC EER varies with capacity
Note on F41: PTAC EER varies with capacity
Note on F44: PTHP EER varies with capacity
Note on F47: PTHP EER varies with capacity
Note on D49: No ASHRAE requirement for vertical AC/HP SEER; set equal to EER
Note on E50: No ASHRAE requirement for vertical AC/HP IEER; set equal to EER
Note on D57: ENERGY STAR 6.1
Note on D58: ENERGY STAR 6.1
Note on D59: ENERGY STAR 6.1
Note on D65: ENERGY STAR 6.1
Note on D66: ENERGY STAR 6.1
Note on D95: ENERGY STAR 6.1 +10%
Note on D96: ENERGY STAR 6.1 +10%
Note on D97: ENERGY STAR 6.1 +10%
Note on D103: ENERGY STAR 6.1 +10%
Note on D104: ENERGY STAR 6.1 +10%

## C_HVAC_Window AC
COMMERCIAL: Window AC
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM.
MEASURE DETAILS
Description
The early removal and recycling of a pre-existing inefficient window air conditioning unit and replacement with a new ENERGY STAR qualifying unit, or the installation of a new ENERGY STAR unit without recycling a previous unit through the program. This measure applies to ENERGY STAR dual inverter driven window AC systems.
Program Criteria
For early replacement with recycling projects, documentation must be provided to show that the pre-existing unit was operating and had a meaningful remaining useful life prior to replacement. The new unit must be ENERGY STAR-certified and must meet or exceed the ENERGY STAR requirements that are in effect during the given program year.
Special note for PY26: For projects involving the installation of a new ENERGY STAR unit without recycling a previous unit through the program, the new unit must be ENERGY STAR-certified and must meet or exceed ENERGY STAR Version 7.0 minimum standards. If ENERGY STAR Version 7.0 is not finalized before PY26 and/or if there are no ENERGY STAR-certified products available that meet the Version 7.0 standards, the portion of the measure allowing purchase and installation of a new ENERGY STAR unit without recycling a previous unit will be on hold until such products become available.
Unit of Measure
One window AC unit.
Baseline Equipment
Equipment is assumed to be a window AC unit without reverse cycle, with louvered sides, and a capacity range of less than 28,000 Btu/h. For window AC units not meeting this type or capacity range, confirm program eligibility with Hawai'i Energy and use a custom approach to calculate impacts.
For early replacement with recycling, a dual baseline is required to estimate impacts. The efficiency during the first baseline period corresponds to federal minimum requirements for units manufactured from June 1, 2014 through May 25, 2026 and the efficiency during the second baseline period corresponds to federal minimum requirements for units manufactured as of May 26, 2026. (See Table 1.)
For the installation of a new unit without recycling a previous unit through the program, a single baseline that corresponds to federal minimum requirements for units manufactured as of May 26, 2026 is used. (See Table 1.)
High Efficiency Equipment
High efficiency equipment is a new ENERGY STAR-certified dual inverter window AC unit without reverse cycle, with louvered sides, and with a capacity range of less than 28,000 Btu/h. The efficiency of the unit must meet or exceed the minimum ENERGY STAR requirements that are in effect during the given program year. As of April 2026, Version 5.0 is in effect, and Versions 6.0 and 7.0 are in draft form. Version 6.0 will address the heating mode efficiency for room heat pumps without changing other requirements. Version 7.0 will update all requirements in response to the new federal minimum standards going into effect on May 26, 2026. Version 7.0 will apply to this measure. (See Table 1.)
Table 1: Baseline and ENERGY STAR Specifications
| Capacity Bin (Btu/h) |  |  |  |  | 1st Baseline1 |  |  |  |  | 2nd Baseline2 | [6 empty] | ENERGY STAR
[6 empty] | CEERBL,1 |  |  | EERBL,1 |  | CEERBL,2 |  |  |  | EERBL,2 |  |  | Version 5.0 3 CEERMin | Version 7.0 4 (Draft 1) CEERMin
| < 6,000 |  |  |  |  | 11 |  |  | 11.1 |  | 13.1 |  |  |  | 13.2 |  |  | 13.1 | 14.4
| 6,000 to 7,999 |  |  |  |  | 11 |  |  | 11.1 |  | 13.7 |  |  |  | 13.8 |  |  | 13.7 | 15.1
| 8,000 to 13,999 |  |  |  |  | 10.9 |  |  | 11 |  | 16 |  |  |  | 16.2 |  |  | 14.7 | 17.6
| 14,000 to 19,999 |  |  |  |  | 10.7 |  |  | 10.8 |  | 16 |  |  |  | 16.2 |  |  | 14.4 | 17.6
| 20,000 to 27,999 |  |  |  |  | 9.4 |  |  | 9.5 |  | 13.8 |  |  |  | 13.9 |  |  | 12.7 | 15.2
1 See federal minimum CEERBL,1 requirements for units manufactured between June 1, 2014 and May 26, 2026 at <https://www.govinfo.gov/content/pkg/CFR-2025-title10-vol3/pdf/CFR-2025-title10-vol3-sec430-32.pdf>, paragraph (b) on page 882. EERBL,1 is assumed to be CEERBL,1 * 1.01.
2 See federal minimum CEERBL,2 requirements for units manufactured as of May 26, 2026 at <https://www.govinfo.gov/content/pkg/CFR-2025-title10-vol3/pdf/CFR-2025-title10-vol3-sec430-32.pdf>, paragraph (b) on page 883. EERBL,2 is assumed to be CEERBL,2 * 1.01.
3 See ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Version 5.0, available here: <https://www.energystar.gov/products/room_air_conditioner_specification_version_5_2>. There are no minimum EER requirements. Note that some of the Version 5.0 CEER values are lower than the federal minimum CEER values effective as of May 26, 2026. This is true for capacities of 8,000 Btu/h and higher.
4 See ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Draft 1, Version 7.0, available here: <https://www.energystar.gov/room_air_conditioner_specification_version_7_0_pd>. There are no minimum EER requirements.
ALGORITHMS
First Baseline Peak Demand Reduction, kW (Early Replacement Only)
(1)
Second Baseline Peak Demand Reduction, kW (or, Single Baseline for Replace on Burnout)
(2)
First Baseline Annual Energy Savings, kWh/yr (Early Replacement Only)
(3)
Second Baseline Annual Energy Savings, kWh/yr (or, Single Baseline for Replace on Burnout)
(4)
Early Replacement Lifetime Energy Savings, kWh
(5)
Replace on Burnout Lifetime Energy Savings, kWh
(6)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [6 empty] | Value |  |  |  | Unit |  | Source/Notes
Capacity | PY15_small | PY15_small | PY15_small | Rated cooling capacity of installed window AC unit | From a review of PY2015 rebates processed, the average size of a small unit | From a review of PY2015 rebates processed, the average size of a small unit | From a review of PY2015 rebates processed, the average size of a small unit |  | From a review of PY2015 rebates processed, the average size of a small unit | From a review of PY2015 rebates processed, the average size of a small unit | Based on installed unit | 1.28 | 1.28 | 1.28 | Btu/h |  | Assumes capacity of < 28,000 Btu/h.1
EERBL,1 | (S)EER_b | (S)EER_b | (S)EER_b | Energy efficiency ratio of baseline unit for first baseline period (early replacement) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Assumed to be CEERBL,1 * 1.01 per ENERGY STAR data.2
EERBL,2 | (S)EER_b | (S)EER_b | (S)EER_b | Energy efficiency ratio of baseline unit for second baseline period (early replacement) or for single baseline (replace on burnout) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Assumed to be CEERBL,2 * 1.01 per ENERGY STAR data.2
EEREE | (S)EER_ee | (S)EER_ee | (S)EER_ee | Energy efficiency ratio of installed high efficiency unit | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | As installed | see table 1 | see table 1 | see table 1 | Btu/Wh |  | If the EEREE value is unknown, it is assumed to be CEEREE * 1.01 per ENERGY STAR data.2
CEERBL,1 | (S)EER_b | (S)EER_b | (S)EER_b | Combined energy efficiency ratio of baseline unit for first baseline period (early replacement) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Federal minimum requirement for units manufactured from June 1, 2014 through May 25, 2026.
CEERBL,2 | (S)EER_b | (S)EER_b | (S)EER_b | Combined energy efficiency ratio of baseline unit for second baseline period (early replacement) or for single baseline (replace on burnout) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Federal minimum requirement for units manufactured as of May 26, 2026.
CEEREE | (S)EER_ee | (S)EER_ee | (S)EER_ee | Combined energy efficiency ratio of installed high efficiency unit | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | As installed | see table 1 | see table 1 | see table 1 | Btu/Wh |  | The new unit for projects that include early replacement and recycling of a pre-existing unit must be ENERGY STAR-certified, with a CEER value that also meets or exceeds the minimum federal standard effective as of May 26, 2026. The new unit for projects that do NOT include early replacement and recycling of a pre-existing unit must meet or exceed minimum ENERGY STAR Version 7.0 CEER standards. Table 1 shows minimum CEER requirements for ENERGY STAR Versions 5.0 (Final) and 7.0 (Draft 1), as well as minimum federal standards.
CF | CF | CF | CF | Coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm |  | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | See Table 2 | 0.5 | 0.5 | 0.5 | - | Deemed value; 50% VRFs operational between 5-9 pm | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period.
EFLH | HOURS | HOURS | HOURS | Equivalent full load cooling hours | equivalent full load cooling hours | equivalent full load cooling hours | equivalent full load cooling hours |  | equivalent full load cooling hours | equivalent full load cooling hours | See Table 2 | 0.5 | 0.5 | 0.5 | hrs/yr | Deemed value; 5 hrs per day cooling | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes and weather data.
PF | PF | PF | PF | Persistence factor | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) |  | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | 1 | 1 | 1 | 1 | -
Constant |  |  |  | Watt/kilowatt conversion | [6 empty] | 1000 |  |  |  | W/kW
RUL |  |  |  | Remaining useful life of measure | [6 empty] | 3 |  |  |  | yrs |  | Assumed to be 1/3 EUL.
EUL |  |  |  | Effective useful life of measure | [6 empty] | 9 |  |  |  | yrs |  | California eTRM.
1 For room AC units outside of this capacity range, use a custom approach to calculate impacts.
2 The Version 3.1 ENERGY STAR specification provided equivalent EER and CEER ratings. For the most popular size band, the EER rating is approximately 1% higher than the CEER. See ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Version 3.1, available here: <https://www.energystar.gov/products/spec/room_air_conditioners_specification_version_3_0_pd>.
SAVINGS
See the accompanying Window AC worksheet:
(C_HVAC_WindowAC_WKST)
The following equivalent full load hours and coincidence factors are recommended per building type based on simulations of DOE prototypes with Honolulu weather (OpenEI datasets). Applicable building types for this Window AC measure are Education, Grocery, Hotel/Motel, Office, Restaurant, and Retail.
Table 2: Equivalent Full Load Hours and Coincidence Factors for Commercial Cooling in Hawaii
| Building Type | [6 empty] | EFLH | [6 empty] | CF
| Avg. Commercial | [6 empty] | NA | [6 empty] | NA
| Cold Storage | [6 empty] | NA | [6 empty] | NA
| Education | [6 empty] | 2549 | [6 empty] | 0.43
| Grocery | [6 empty] | 1531 | [6 empty] | 0.27
| Health | [6 empty] | NA | [6 empty] | NA
| Hotel/Motel | [6 empty] | 4910 | [6 empty] | 0.6
| Industrial | [6 empty] | NA | [6 empty] | NA
| Office | [6 empty] | 2754 | [6 empty] | 0.48
| Restaurant | [6 empty] | 2451 | [6 empty] | 0.4
| Retail | [6 empty] | 1913 | [6 empty] | 0.29
| Warehouse | [6 empty] | NA | [6 empty] | NA
NA = Building type is not applicable for window AC measure.
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Window AC and Residential Central AC Retrofit - Analysis File."
• | ICF's 2025 Analysis File named "PY25 TRM - Commercial Window AC - Analysis File."
• | AEG's Analysis files titled "AEG HPUC Update of Commercial Chillers - Analysis File" and "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays" include Hawai‘i-specific simulation results for determining air conditioning EFLH and CF.
• | California eTRM. CPUC Support Tables. Effective Useful Life and Remaining Useful Life, available here: https://www.caetrm.com/cpuc/table/effusefullife/
• | Code of Federal Regulations, 10 CFR 430.32, Subpart C, Energy and Water Conservation Standards and Their Effective Dates, (b) Room Air Conditioners, pages 882-883, available here: <https://www.govinfo.gov/content/pkg/CFR-2025-title10-vol3/pdf/CFR-2025-title10-vol3-sec430-32.pdf>.
• | ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Version 3.1, available here: <https://www.energystar.gov/products/spec/room_air_conditioners_specification_version_3_0_pd>.
• | ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Version 5.0, available here: <https://www.energystar.gov/products/room_air_conditioner_specification_version_5_2>.
• | ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Draft 1, Version 7.0, available here: <https://www.energystar.gov/room_air_conditioner_specification_version_7_0_pd>.
• | Open EI Datasets. Office of Energy Efficiency and Renewable Energy. Commercial and Residential Hourly Load Profiles for All TMY3 Locations in the United States. U.S. Department of Energy Open Data Catalog. Available at: <https://openei.org/doe-opendata/dataset/commercial-and-residential-hourly-load-profiles-for-all-tmy3-locations-in-the-united-states>.
• | Oversizing of HVAC System: Signatures and Penalties, University of Idaho, Integrated Design Lab-Boise, available here: <http://www.idlboise.com/pdf/papers/ENB_3018_RTU_Measurement_accepted.pdf>. Used to determine correct HVAC oversizing adjustment for EFLH and CF analysis.
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒, 𝐸𝑅)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(𝐸𝑈𝐿−𝑅𝑈𝐿)
〖∆𝑘𝑊〗_1𝑠𝑡=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅〗_(𝐵𝐿,1)−〗 1∕〖〖𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐶𝐹∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐶𝐸𝐸𝑅〗_(𝐵𝐿,1)−〗 1∕〖〖𝐶𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻∗𝑃𝐹
〖∆𝑘𝑊〗_2𝑛𝑑=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅〗_(𝐵𝐿,2)−〗 1∕〖〖𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐶𝐹∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐶𝐸𝐸𝑅〗_(𝐵𝐿,2)−〗 1∕〖〖𝐶𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒, 𝑅𝑂𝐵)=〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗𝐸𝑈𝐿

## C_HVAC_WindowAC_WKST
COMMERCIAL: Window AC Savings Calculator
Return to TOC
| Step 1: Enter AC nameplate data |  |  | Step 2: Determine if it qualifies |  |  | Step 3: Calculate savings
| Enter Building Type: | Education
| Enter AC type: | Room AC w/o recycling (20,000-27,999 Btu/h) |  |  |  |  | CF: | 0.43
| Enter Rated AC Capacity (Btu/h): | 25000 |  | CEEREE,Min | 15.2 | Pass | EFLH: | 2549
| Enter Full Load Efficiency:* | 14 |  | EERBL,2 | 13.9 |  | PF: | 1
| Enter Part-Load Efficiency:** | 15.2 |  | CEERBL,2 | 13.8 |  | kW reduction: | 0.006
| * If EER is unknown, use EER = 1.01 * CEER |  |  | EERBL,1 | 0 | Only for early replacement | kW reduction (ER): | 0 | Only for early replacement; this is savings during first baseline period
| **If CEER is unknown, use CEER = EER / 1.01 |  |  | CEERBL,1 | 0 | Only for early replacement | kWh/yr savings: | 425.32
[7 empty] | kWh/yr savings (ER): | 0 | Only for early replacement; this is savings during first baseline period
| Baseline Specifications | [5 empty] | Lifetime kWh: | 3827.88
| System Type | Replace on Burnout (or, Second Baseline for Early Replacement) |  | Early Replacement (First Baseline)
65000 |  | CEERBL,2 | EERBL,2 | CEERBL,1 | EERBL,1
| Room AC w/ recycling (< 6,000 Btu/h) | 13.1 | 13.2 | 11 | 11.1
| Room AC w/o recycling (< 6,000 Btu/h) | 13.1 | 13.2
| Room AC w/ recycling (6,000-7,999 Btu/h) | 13.7 | 13.8 | 11 | 11.1
| Room AC w/o recycling (6,000-7,999 Btu/h) | 13.7 | 13.8
| Room AC w/ recycling (8,000-13,999 Btu/h) | 16 | 16.2 | 10.9 | 11
| Room AC w/o recycling (8,000-13,999 Btu/h) | 16 | 16.2
| Room AC w/ recycling (14,000-19,999 Btu/h) | 16 | 16.2 | 10.7 | 10.8
| Room AC w/o recycling (14,000-19,999 Btu/h) | 16 | 16.2
| Room AC w/ recycling (20,000-27,999 Btu/h) | 13.8 | 13.9 | 9.4 | 9.5
| Room AC w/o recycling (20,000-27,999 Btu/h) | 13.8 | 13.9
Minimum EE Qualifications and Parameters Table
| System Type | CEEREE,Min | EEREE,Min | PF | EUL
| Room AC w/ recycling (< 6,000 Btu/h) | 13.1 | NA | 1 | 9
| Room AC w/o recycling (< 6,000 Btu/h) | 14.4 | NA | 1 | 9
| Room AC w/ recycling (6,000-7,999 Btu/h) | 13.7 | NA | 1 | 9
| Room AC w/o recycling (6,000-7,999 Btu/h) | 15.1 | NA | 1 | 9
| Room AC w/ recycling (8,000-13,999 Btu/h) | 16 | NA | 1 | 9
| Room AC w/o recycling (8,000-13,999 Btu/h) | 17.6 | NA | 1 | 9
| Room AC w/ recycling (14,000-19,999 Btu/h) | 16 | NA | 1 | 9
| Room AC w/o recycling (14,000-19,999 Btu/h) | 17.6 | NA | 1 | 9
| Room AC w/ recycling (20,000-27,999 Btu/h) | 13.8 | NA | 1 | 9
| Room AC w/o recycling (20,000-27,999 Btu/h) | 15.2 | NA | 1 | 9
Applicable Building Types for Window AC Measure
Building Types
Education
Grocery
Hotel/Motel
Office
Restaurant
Retail
Equivalent Full Load Hours and Coincidence Factors for Commercial Cooling in Hawaii
| Building Type | EFLH | CF
| Avg. Commercial | NA | NA
| Cold Storage | NA | NA
| Education | 2549 | 0.43
| Grocery | 1531 | 0.27
| Health | NA | NA
| Hotel/Motel | 4910 | 0.6
| Industrial | NA | NA
| Office | 2754 | 0.48
| Restaurant | 2451 | 0.4
| Retail | 1913 | 0.29
| Warehouse | NA | NA
Note on C29: KP: ESTAR v5.0
Note on C30: KP: ESTAR v7.0
Note on C31: KP: ESTAR v5.0
Note on C32: KP: ESTAR v7.0
Note on C33: KP: Min Fed Stds
Note on C34: KP: ESTAR v7.0
Note on C35: KP: Min Fed Stds
Note on C36: KP: ESTAR v7.0
Note on C37: KP: Min Fed Stds
Note on C38: KP: ESTAR v7.0

## C_HVAC_VFD Water Pump
COMMERCIAL: VFD HVAC Water Pump and Fan
Return to TOC
UPDATE STATUS
Updated in Fall 2018 for PY19 TRM.
MEASURE DETAILS
Description
Variable frequency drive and control installed on full speed pumps and fans, or damped fans, used in HVAC systems.
Program Criteria
* Require pre-notification before projects begin. * The program reserves the right to perform on-site verifications, both pre- and post-installation. * Existing equipment must not have a VFD (i.e. – incentives are not available for replacement). * VFDs on pumps larger than 200 hp may be analyzed on a fully custom basis. * The VFDs must actively control and vary the pump speed. * Since VFDs are required by code for a variety of HVAC applications, this measure is only eligible if a VFD would not have been required otherwise.
Unit of Measure
One VFD.
Baseline Equipment
A chilled water or condenser water pump or HVAC fan with no VFD.
High Efficiency Equipment
Motor/pump with VFD installed.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  |  | Source/Notes
HP |  |  |  | Nameplate horsepower | [11 empty] | User input |  |  |  | HP |  |  | Project specific
kWperHP |  |  |  | kW equivalent of 1 horse power | [11 empty] | 0.746 |  |  |  | kW/HP |  |  | Project specific
LF |  |  |  | Load factor (% of full load power in typical operation) | [11 empty] | 75% |  |  |  | - |  |  | LBNL1
η |  |  |  | Rated motor efficiency | [11 empty] | User input |  |  |  | - |  |  | See "C_HVAC_VFD Water Pump Reference" table if nameplate efficiency is missing
SVGd |  |  |  | Demand savings factor, %. The assumed average reduction of full load enabled by the VFD as a result of lower speed or lower power need. | [11 empty] | Table 1 |  |  |  | - |  |  | Derived using CMUA calculator cited below. 2
SVGe |  |  |  | Energy savings factor, %. The assumed average reduction of kWh enabled by the VFD as a result of lower speed or power operation over time. | [11 empty] | Table 1 |  |  |  | - |  |  | CMUA TRM401 Energy Savings Calculator for Pump and Fan VFD 3
CF |  |  |  | Coincidence factor | [11 empty] | User input (CF = 0.5 if unknown) |  |  |  | - |  |  | Not accurately stipulated; a custom input is recommended 4
HRS |  |  |  | Annual equivalent full load operating hours of fan or pump | [11 empty] | User input (Table 2 if unknown) |  |  |  | hrs |  |  | Not accurately stipulated; a custom input is recommended 5
EUL |  |  |  | Effective useful life of measure | [11 empty] | 15 |  |  |  | yrs |  |  | No change from PY18 TRM; EUL was verified during AEG's 2018 benchmarking
1 Improving Motor and Drive System Performance: A Sourcebook for Industry, Prepared by Lawrence Berkeley National Laboratory and Resource Dynamics Corporation, Prepared for U.S. Department of Energy, September 2008, pg 15, available here: <https://www1.eere.energy.gov/manufacturing/tech_assistance/pdfs/motor.pdf>.
2 Approach for demand savings factors is not specified in PY18 TRM, but during the PY19 TRM update, AEG found the values to be reasonable based on the energy savings factors.
3 The calculator is available for download here: https://www.cmua.org/energy-efficiency-technical-reference-manual. Click "TRM Spreadsheet 3 - 300 through 505" and then the file is named "TRM401_energy savings calculator_pump and fan VFD_v4_1_14"
4 The coincidence factor cannot be stipulated based on the cooling system CF, since it will have an inverse relationship to cooling system CF. For example, if a chiller operates at full load during the entire peak demand period, its CF will be high (1.0), but the VFD's CF will be 0 (there will actually be demand penalty due to efficiency losses with addition of VFD controller operating at 100% flow). Therefore, the CF for the VFD measure must be determined by a custom method that ideally takes into account a difference in the load shapes before and after installation of the VFD. In absence of project-specific CF, assume CF = 0.5, since it is reasonable to expect that the VFD demand savings occur during half of the 5-9 pm peak demand period.
5 Equation 2 requires the annual equivalent full load operating hours of the fan or pump. These hours will vary by fan/pump operating hours, pre-existing control type, and load shape and cannot be accurately stipulated based on cooling system EFLHs. In absence of project-specific HRS, use either 1) the TRM401 calculator to estimate energy savings (preferred), or 2) the EFLHs in Table 2.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Table 1. Percent Demand and Energy Savings from VFD Given Various Baseline Controls, SVGd and SVGe
Measure Savings | [9 empty] | Fan kW (typical) |  |  |  |  | Fan kWh (total) |  |  |  |  | Pump kW |  |  |  |  | Pump kWh
Constant Volume | [9 empty] | 57% |  |  |  |  | 49.8% |  |  |  |  | 57% |  |  |  |  | 51%
Eddy Current Drive | [9 empty] | N/A |  |  |  |  | N/A |  |  |  |  | 20% |  |  |  |  | 24.3%
Inlet Damper Box | [9 empty] | 31% |  |  |  |  | 35.6% |  |  |  |  | N/A |  |  |  |  | N/A
Inlet Guide Vane, FC | [9 empty] | 6% |  |  |  |  | 10.1% |  |  |  |  | N/A |  |  |  |  | N/A
Outlet Damper | [9 empty] | 22% |  |  |  |  | 27.2% |  |  |  |  | N/A |  |  |  |  | N/A
Throttle Valve | [9 empty] | N/A |  |  |  |  | N/A |  |  |  |  | 47% |  |  |  |  | 45.5%
Average | [9 empty] | 29% |  |  |  |  | 31% |  |  |  |  | 41% |  |  |  |  | 40%
Source: Table 1 is derived from CMUA Energy Savings Calculator-Pump and Fan VFD Retrofit. The calculator is available for download here: https://www.cmua.org/energy-efficiency-technical-reference-manual. Click "TRM Spreadsheet 3 - 300 through 505" and then the file is named "TRM401_energy savings calculator_pump and fan VFD_v4_1_14". This calculator is cited in the CMUA 2017 TRM.
The most typical VFD operation (at 60-80% of rated flow) reduces load from 100% to 43%. However, at 0% flow the VFD is still drawing 5% load in the fan case and 27% load in the pump case.
SAVINGS
Preferred Approach: Semi-Prescriptive Savings Calculator
(Based on user input of project-specific parameters)
Select whether the VFD is for a fan or pump
Fan VFD
Select the type of baseline controls
|  | Constant Volume | [9 empty] | SVGd = | 57% | [6 empty] | SVGe = | 49.8%
Enter the nameplate horsepower, HP
2
Enter the rated motor efficiency, %
85.5%
Enter the coincidence factor
|  | 0.5 |  |  |  |  | Estimate using project-specific information (preferred). If unknown, use CF = 0.5.
Enter the annual equivalent full load operating hours of the pre-existing fan or pump
|  | 4000 |  |  |  |  | If equivalent full load hours for the fan or pump are unknown, use either: 1) the CMUA TRM410 calculator and enter fan or pump total operating hours and other project parameters to calculate energy (kWh) savings (preferred), or 2) enter the EFLH for cooling for the correct building type from Table 2.
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Fan VFD | [7 empty] | 0.373 | [7 empty] | 2607.07 | [7 empty] | 39106.05
Note: Savings in blue result from sample entries above. They are for illustrative purposes only.
Alternative Approach: Deemed Per-HP Savings
Table 2. Fan and Pump VFD: Deemed Energy and Demand Savings per HP (Use Rated Motor Efficiency or Water Pump Reference table for η)
Building Type |  |  |  | CF |  | HRS1 |  | Demand Savings Fan (kW/HP) |  |  |  | Energy Savings Fan (kWh/HP) |  |  |  | Demand Savings Chilled Water Pump (kW/hp) |  |  |  | Energy Savings Chilled Water Pump (kWh/hp) |  |  |  | Demand Savings Condenser Water Pump (kW/hp) |  |  |  | Energy Savings Condenser Water Pump (kWh/hp)
Misc. Commercial |  |  |  | 0.5 |  | 2594 |  | 0.081127 |  |  |  | 449.9163 |  |  |  | 0.1147 |  |  |  | 580.5372 |  |  |  | 0.1147 |  |  |  | 580.5372
Cold Storage |  |  |  | 0.5 |  | Varies |  | Varies |  |  |  | Varies |  |  |  | Varies |  |  |  | Varies |  |  |  | Varies |  |  |  | Varies
Education |  |  |  | 0.5 |  | 2549 |  | 0.081127 |  |  |  | 442.1113 |  |  |  | 0.1147 |  |  |  | 570.4662 |  |  |  | 0.1147 |  |  |  | 570.4662
Grocery |  |  |  | 0.5 |  | 1531 |  | 0.081127 |  |  |  | 265.5443 |  |  |  | 0.1147 |  |  |  | 342.6378 |  |  |  | 0.1147 |  |  |  | 342.6378
Health |  |  |  | 0.5 |  | 4891 |  | 0.081127 |  |  |  | 848.3195 |  |  |  | 0.1147 |  |  |  | 1094.6058 |  |  |  | 0.1147 |  |  |  | 1094.6058
Hotel/Motel |  |  |  | 0.5 |  | 4910 |  | 0.081127 |  |  |  | 851.615 |  |  |  | 0.1147 |  |  |  | 1098.858 |  |  |  | 0.1147 |  |  |  | 1098.858
Industrial |  |  |  | 0.5 |  | Varies |  | Varies |  |  |  | Varies |  |  |  | Varies |  |  |  | Varies |  |  |  | Varies |  |  |  | Varies
Office |  |  |  | 0.5 |  | 2754 |  | 0.081127 |  |  |  | 477.6675 |  |  |  | 0.1147 |  |  |  | 616.3452 |  |  |  | 0.1147 |  |  |  | 616.3452
Restaurant |  |  |  | 0.5 |  | 2451 |  | 0.081127 |  |  |  | 425.1137 |  |  |  | 0.1147 |  |  |  | 548.5338 |  |  |  | 0.1147 |  |  |  | 548.5338
Retail |  |  |  | 0.5 |  | 1913 |  | 0.081127 |  |  |  | 331.8003 |  |  |  | 0.1147 |  |  |  | 428.1294 |  |  |  | 0.1147 |  |  |  | 428.1294
Warehouse |  |  |  | 0.5 |  | 1033 |  | 0.081127 |  |  |  | 179.1687 |  |  |  | 0.1147 |  |  |  | 231.1854 |  |  |  | 0.1147 |  |  |  | 231.1854
1 These are EFLH values from AEG's analysis of DOE's OpenEI load shapes for the Cooling end-use using Hawai‘i-specific prototypes and weather data. Use as a proxy for "HRS" for the HVAC VFD measure only if project-specific data is not available.
Note: This measure has a single baseline. For deemed lifetime energy savings, multiply the energy savings by the EUL.
RESOURCES
• | AEG's Analysis File titled "AEG HPUC Update - Com-VFD Water Pump - Analysis file."
• | CMUA 2017 TRM, Section 8.1 Pump and Fan Variable Frequency Drive Control Measure, pg. 8.1, available here: <https://www.cmua.org/files/CMUA-POU-TRM_2017_FINAL_12-5-2017%20-%20Copy.pdf>. References the TRM401 pump and fan calculator for savings.
• | CMUA TRM401 Energy Savings Calculator for Pump and Fan VFD. The calculator is available for download here: https://www.cmua.org/energy-efficiency-technical-reference-manual. Click "TRM Spreadsheet 3 - 300 through 505" and then the file is named "TRM401_energy savings calculator_pump and fan VFD_v4_1_14"
• | Improving Motor and Drive System Performance: A Sourcebook for Industry, Prepared by Lawrence Berkeley National Laboratory and Resource Dynamics Corporation, Prepared for U.S. Department of Energy, September 2008, pg 15, available here: <https://www1.eere.energy.gov/manufacturing/tech_assistance/pdfs/motor.pdf>.
∆𝑘𝑊=〖𝐻𝑃∗𝑘𝑊〗_𝑝𝑒𝑟𝐻𝑃∗(𝐿𝐹∕𝜂)∗𝐶𝐹∗〖𝑆𝑉𝐺〗_𝑑
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊ℎ=〖𝐻𝑃∗𝑘𝑊〗_𝑝𝑒𝑟𝐻𝑃∗(𝐿𝐹∕𝜂)∗𝐻𝑅𝑆∗〖𝑆𝑉𝐺〗_𝑒

## C_HVAC_VFD Water Pump Reference
COMMERCIAL: VFD Water Pump / Fan Reference Attachment
Return to TOC
If nameplate rated motor efficiency is missing, this table may be used as a source of motor efficiency. Many motors manufactured after Jun 1, 2016 must now meet NEMA premium efficiency requirements. (For the current Federal codes, see https://www.ecfr.gov/cgi-bin/retrieveECFR?n=pt10.3.431#se10.3.431_125.)
Induction Motor Efficiency Standards
Prepared by Johnny Douglass, P.E.
Washington State University
Extension Energy Program
925 Plum Street SE, Bldg. 4
POB 43169
Olympia, WA 98504-3165
Induction Motor Efficiency Standards
See notes at end of tables
Enclosure | Speed | Horsepower | Volt | Old NEMA | NEMA EPACT | IEEE 841 | NEMA Premium
ODP | 3600 | 1 | 460 |  |  |  | 77
ODP | 3600 | 1.5 | 460 | 80 | 82.5 |  | 84
ODP | 3600 | 2 | 460 | 82.5 | 84 |  | 85.5
ODP | 3600 | 3 | 460 | 82.5 | 84 |  | 85.5
ODP | 3600 | 5 | 460 | 85.5 | 85.5 |  | 86.5
ODP | 3600 | 7.5 | 460 | 85.5 | 87.5 |  | 88.5
ODP | 3600 | 10 | 460 | 87.5 | 88.5 |  | 89.5
ODP | 3600 | 15 | 460 | 89.5 | 89.5 |  | 90.2
ODP | 3600 | 20 | 460 | 90.2 | 90.2 |  | 91
ODP | 3600 | 25 | 460 | 91 | 91 |  | 91.7
ODP | 3600 | 30 | 460 | 91 | 91 |  | 91.7
ODP | 3600 | 40 | 460 | 91.7 | 91.7 |  | 92.4
ODP | 3600 | 50 | 460 | 91.7 | 92.4 |  | 93
ODP | 3600 | 60 | 460 | 93 | 93 |  | 93.6
ODP | 3600 | 75 | 460 | 93 | 93 |  | 93.6
ODP | 3600 | 100 | 460 | 93 | 93 |  | 93.6
ODP | 3600 | 125 | 460 | 93 | 93.6 |  | 94.1
ODP | 3600 | 150 | 460 | 93.6 | 93.6 |  | 94.1
ODP | 3600 | 200 | 460 | 93.6 | 94.5 |  | 95
ODP | 3600 | 250 | 460 |  | 94.5 |  | 95
ODP | 3600 | 300 | 460 |  | 95 |  | 95.4
ODP | 3600 | 350 | 460 |  | 95 |  | 95.4
ODP | 3600 | 400 | 460 |  | 95.4 |  | 95.8
ODP | 3600 | 450 | 460 |  | 95.8 |  | 95.8
ODP | 3600 | 500 | 460 |  | 95.8 |  | 95.8
ODP | 1800 | 1 | 460 | 82.5 | 82.5 |  | 85.5
ODP | 1800 | 1.5 | 460 | 82.5 | 84 |  | 86.5
ODP | 1800 | 2 | 460 | 82.5 | 84 |  | 86.5
ODP | 1800 | 3 | 460 | 86.5 | 86.5 |  | 89.5
ODP | 1800 | 5 | 460 | 86.5 | 87.5 |  | 89.5
ODP | 1800 | 7.5 | 460 | 88.5 | 88.5 |  | 91
ODP | 1800 | 10 | 460 | 88.5 | 89.5 |  | 91.7
ODP | 1800 | 15 | 460 | 90.2 | 91 |  | 93
ODP | 1800 | 20 | 460 | 91 | 91 |  | 93
Page 1 of 8
Induction Motor Efficiency Standards
See notes at end of tables
Enclosure | Speed | Horsepower | Volt | Old NEMA | NEMA EPACT | IEEE 841 | NEMA Premium
ODP | 1800 | 15 | 460 | 90.2 | 91 |  | 93
ODP | 1800 | 20 | 460 | 91 | 91 |  | 93
ODP | 1800 | 25 | 460 | 91.7 | 91.7 |  | 93.6
ODP | 1800 | 30 | 460 | 91.7 | 92.4 |  | 94.1
ODP | 1800 | 40 | 460 | 92.4 | 93 |  | 94.1
ODP | 1800 | 50 | 460 | 92.4 | 93 |  | 94.5
ODP | 1800 | 60 | 460 | 93 | 93.6 |  | 95
ODP | 1800 | 75 | 460 | 93.6 | 94.1 |  | 95
ODP | 1800 | 100 | 460 | 93.6 | 94.1 |  | 95.4
ODP | 1800 | 125 | 460 | 93.6 | 94.5 |  | 95.4
ODP | 1800 | 150 | 460 | 94.1 | 95 |  | 95.8
ODP | 1800 | 200 | 460 | 94.1 | 95 |  | 95.8
ODP | 1800 | 250 | 460 |  | 95.4 |  | 95.8
ODP | 1800 | 300 | 460 |  | 95.4 |  | 95.8
ODP | 1800 | 350 | 460 |  | 95.4 |  | 95.8
ODP | 1800 | 400 | 460 |  | 95.4 |  | 95.8
ODP | 1800 | 450 | 460 |  | 95.8 |  | 96.2
ODP | 1800 | 500 | 460 |  | 95.8 |  | 96.2
ODP | 1200 | 1 | 460 | 77 | 80 |  | 82.5
ODP | 1200 | 1.5 | 460 | 82.5 | 84 |  | 86.5
ODP | 1200 | 2 | 460 | 84 | 85.5 |  | 87.5
ODP | 1200 | 3 | 460 | 85.5 | 86.5 |  | 88.5
ODP | 1200 | 5 | 460 | 86.5 | 87.5 |  | 89.5
ODP | 1200 | 7.5 | 460 | 88.5 | 88.5 |  | 90.2
ODP | 1200 | 10 | 460 | 90.2 | 90.2 |  | 91.7
ODP | 1200 | 15 | 460 | 89.5 | 90.2 |  | 91.7
ODP | 1200 | 20 | 460 | 90.2 | 91 |  | 92.4
ODP | 1200 | 25 | 460 | 91 | 91.7 |  | 93
ODP | 1200 | 30 | 460 | 91.7 | 92.4 |  | 93.6
ODP | 1200 | 40 | 460 | 91.7 | 93 |  | 94.1
ODP | 1200 | 50 | 460 | 91.7 | 93 |  | 94.1
ODP | 1200 | 60 | 460 | 92.4 | 93.6 |  | 94.5
ODP | 1200 | 75 | 460 | 93 | 93.6 |  | 94.5
ODP | 1200 | 100 | 460 | 93.6 | 94.1 |  | 95
Page 2 of 8
Induction Motor Efficiency Standards
See notes at end of tables
Enclosure | Speed | Horsepower | Volt | Old NEMA | NEMA EPACT | IEEE 841 | NEMA Premium
ODP | 1200 | 125 | 460 | 93.6 | 94.1 |  | 95
ODP | 1200 | 150 | 460 | 93.6 | 94.5 |  | 95.4
ODP | 1200 | 200 | 460 | 94.1 | 94.5 |  | 95.4
ODP | 1200 | 250 | 460 |  | 95.4 |  | 95.4
ODP | 1200 | 300 | 460 |  | 95.4 |  | 95.4
ODP | 1200 | 350 | 460 |  | 95.4 |  | 95.4
ODP | 1200 | 400 | 460 |  |  |  | 95.8
ODP | 1200 | 450 | 460 |  |  |  | 96.2
ODP | 1200 | 500 | 460 |  |  |  | 96.2
ODP | 900 | 1 | 460 | 72 | 74
ODP | 900 | 1.5 | 460 | 75.5 | 75.5
ODP | 900 | 2 | 460 | 85.5 | 85.5
ODP | 900 | 3 | 460 | 86.5 | 86.5
ODP | 900 | 5 | 460 | 87.5 | 87.5
ODP | 900 | 7.5 | 460 | 88.5 | 88.5
ODP | 900 | 10 | 460 | 89.5 | 89.5
ODP | 900 | 15 | 460 | 89.5 | 89.5
ODP | 900 | 20 | 460 | 90.2 | 90.2
ODP | 900 | 25 | 460 | 90.2 | 90.2
ODP | 900 | 30 | 460 | 91 | 91
ODP | 900 | 40 | 460 | 90.2 | 91
ODP | 900 | 50 | 460 | 91.7 | 91.7
ODP | 900 | 60 | 460 | 92.4 | 92.4
ODP | 900 | 75 | 460 | 93.6 | 93.6
ODP | 900 | 100 | 460 | 93.6 | 93.6
ODP | 900 | 125 | 460 | 93.6 | 93.6
ODP | 900 | 150 | 460 | 93.6 | 93.6
ODP | 900 | 200 | 460 | 93.6 | 93.6
ODP | 900 | 250 | 460 |  | 94.5
ODP | 900 | 300 | 460
ODP | 900 | 350 | 460
ODP | 900 | 400 | 460
ODP | 900 | 450 | 460
ODP | 900 | 500 | 460
Page 3 of 8
Induction Motor Efficiency Standards
See notes at end of tables
Enclosure | Speed | Horsepower | Volt | Old NEMA | NEMA EPACT | IEEE 841 | NEMA Premium
TEFC | 3600 | 1 | 460 |  | 75.5 | 77 | 77
TEFC | 3600 | 1.5 | 460 | 78.5 | 82.5 | 84 | 84
TEFC | 3600 | 2 | 460 | 81.5 | 84 | 85.5 | 85.5
TEFC | 3600 | 3 | 460 | 82.5 | 85.5 | 86.5 | 86.5
TEFC | 3600 | 5 | 460 | 85.5 | 87.5 | 88.5 | 88.5
TEFC | 3600 | 7.5 | 460 | 85.5 | 88.5 | 89.5 | 89.5
TEFC | 3600 | 10 | 460 | 87.5 | 89.5 | 90.2 | 90.2
TEFC | 3600 | 15 | 460 | 87.5 | 90.2 | 91 | 91
TEFC | 3600 | 20 | 460 | 88.5 | 90.2 | 91 | 91
TEFC | 3600 | 25 | 460 | 89.5 | 91 | 91.7 | 91.7
TEFC | 3600 | 30 | 460 | 89.5 | 91 | 91.7 | 91.7
TEFC | 3600 | 40 | 460 | 90.2 | 91.7 | 92.4 | 92.4
TEFC | 3600 | 50 | 460 | 90.2 | 92.4 | 93 | 93
TEFC | 3600 | 60 | 460 | 91.7 | 93 | 93.6 | 93.6
TEFC | 3600 | 75 | 460 | 92.4 | 93 | 93.6 | 93.6
TEFC | 3600 | 100 | 460 | 93 | 93.6 | 94.1 | 94.1
TEFC | 3600 | 125 | 460 | 93 | 94.5 | 95 | 95
TEFC | 3600 | 150 | 460 | 93 | 94.5 | 95 | 95
TEFC | 3600 | 200 | 460 | 94.1 | 95 | 95.4 | 95.4
TEFC | 3600 | 250 | 460 |  | 95.4 | 95.4 | 95.8
TEFC | 3600 | 300 | 460 |  | 95.4 | 95.4 | 95.8
TEFC | 3600 | 350 | 460 |  | 95.4 | 95.4 | 95.8
TEFC | 3600 | 400 | 460 |  | 95.4 | 95.4 | 95.8
TEFC | 3600 | 450 | 460 |  | 95.4 | 95.4 | 95.8
TEFC | 3600 | 500 | 460 |  | 95.4 | 95.4 | 95.8
TEFC | 1800 | 1 | 460 | 80 | 82.5 | 84 | 85.5
TEFC | 1800 | 1.5 | 460 | 81.5 | 84 | 85.5 | 86.5
TEFC | 1800 | 2 | 460 | 82.5 | 84 | 85.5 | 86.5
TEFC | 1800 | 3 | 460 | 84 | 87.5 | 88.5 | 89.5
TEFC | 1800 | 5 | 460 | 85.5 | 87.5 | 88.5 | 89.5
TEFC | 1800 | 7.5 | 460 | 87.5 | 89.5 | 90.2 | 91.7
TEFC | 1800 | 10 | 460 | 87.5 | 89.5 | 90.2 | 91.7
TEFC | 1800 | 15 | 460 | 88.5 | 91 | 91.7 | 92.4
Page 4 of 8
Induction Motor Efficiency Standards
See notes at end of tables
Enclosure | Speed | Horsepower | Volt | Old NEMA | NEMA EPACT | IEEE 841 | NEMA Premium
TEFC | 1800 | 20 | 460 | 90.2 | 91 | 91.7 | 93
TEFC | 1800 | 25 | 460 | 91 | 92.4 | 93 | 93.6
TEFC | 1800 | 30 | 460 | 91 | 92.4 | 93 | 93.6
TEFC | 1800 | 40 | 460 | 91.7 | 93 | 93.6 | 94.1
TEFC | 1800 | 50 | 460 | 92.4 | 93 | 93.6 | 94.5
TEFC | 1800 | 60 | 460 | 93 | 93.6 | 94.1 | 95
TEFC | 1800 | 75 | 460 | 93 | 94.1 | 94.5 | 95.4
TEFC | 1800 | 100 | 460 | 93.6 | 94.5 | 95 | 95.4
TEFC | 1800 | 125 | 460 | 93.6 | 94.5 | 95 | 95.4
TEFC | 1800 | 150 | 460 | 94.1 | 95 | 95.4 | 95.8
TEFC | 1800 | 200 | 460 | 94.5 | 95 | 95.4 | 96.2
TEFC | 1800 | 250 | 460 |  | 95 | 95 | 96.2
TEFC | 1800 | 300 | 460 |  | 95.4 | 95.4 | 96.2
TEFC | 1800 | 350 | 460 |  | 95.4 | 95.4 | 96.2
TEFC | 1800 | 400 | 460 |  | 95.4 | 95.4 | 96.2
TEFC | 1800 | 450 | 460 |  | 95.4 | 95.4 | 96.2
TEFC | 1800 | 500 | 460 |  | 95.8 | 95.4 | 96.2
TEFC | 1200 | 1 | 460 | 75.5 | 80 | 81.5 | 82.5
TEFC | 1200 | 1.5 | 460 | 82.5 | 85.5 | 86.5 | 87.5
TEFC | 1200 | 2 | 460 | 82.5 | 86.5 | 87.5 | 88.5
TEFC | 1200 | 3 | 460 | 84 | 87.5 | 88.5 | 89.5
TEFC | 1200 | 5 | 460 | 85.5 | 87.5 | 88.5 | 89.5
TEFC | 1200 | 7.5 | 460 | 87.5 | 89.5 | 90.2 | 91
TEFC | 1200 | 10 | 460 | 87.5 | 89.5 | 90.2 | 91
TEFC | 1200 | 15 | 460 | 89.5 | 90.2 | 91 | 91.7
TEFC | 1200 | 20 | 460 | 89.5 | 90.2 | 91 | 91.7
TEFC | 1200 | 25 | 460 | 90.2 | 91.7 | 92.4 | 93
TEFC | 1200 | 30 | 460 | 91 | 91.7 | 92.4 | 93
TEFC | 1200 | 40 | 460 | 91.7 | 93 | 93.6 | 94.1
TEFC | 1200 | 50 | 460 | 91.7 | 93 | 93.6 | 94.1
TEFC | 1200 | 60 | 460 | 91.7 | 93.6 | 94.1 | 94.5
TEFC | 1200 | 75 | 460 | 93 | 93.6 | 94.1 | 94.5
TEFC | 1200 | 100 | 460 | 93 | 94.1 | 94.5 | 95
Page 5 of 8
Induction Motor Efficiency Standards
See notes at end of tables
Enclosure | Speed | Horsepower | Volt | Old NEMA | NEMA EPACT | IEEE 841 | NEMA Premium
TEFC | 1200 | 125 | 460 | 93 | 94.1 | 94.5 | 95
TEFC | 1200 | 150 | 460 | 94.1 | 95 | 95.4 | 95.8
TEFC | 1200 | 200 | 460 | 94.1 | 95 | 95.4 | 95.8
TEFC | 1200 | 250 | 460 |  | 95 | 95 | 95.8
TEFC | 1200 | 300 | 460 |  | 95 | 95 | 95.8
TEFC | 1200 | 350 | 460 |  | 95 | 95 | 95.8
TEFC | 1200 | 400 | 460 |  |  |  | 95.8
TEFC | 1200 | 450 | 460 |  |  |  | 95.8
TEFC | 1200 | 500 | 460 |  |  |  | 95.8
TEFC | 900 | 1 | 460 | 72 | 74 | 75.5
TEFC | 900 | 1.5 | 460 | 75.5 | 77 | 78.5
TEFC | 900 | 2 | 460 | 82.5 | 82.5 | 84
TEFC | 900 | 3 | 460 | 81.5 | 84 | 85.5
TEFC | 900 | 5 | 460 | 84 | 85.5 | 86.5
TEFC | 900 | 7.5 | 460 | 85.5 | 85.5 | 86.5
TEFC | 900 | 10 | 460 | 87.5 | 88.5 | 89.5
TEFC | 900 | 15 | 460 | 88.5 | 88.5 | 89.5
TEFC | 900 | 20 | 460 | 89.5 | 89.5 | 90.2
TEFC | 900 | 25 | 460 | 89.5 | 89.5 | 90.2
TEFC | 900 | 30 | 460 | 90.2 | 91 | 91.7
TEFC | 900 | 40 | 460 | 90.2 | 91 | 91.7
TEFC | 900 | 50 | 460 | 91 | 91.7 | 92.4
TEFC | 900 | 60 | 460 | 91.7 | 91.7 | 92.4
TEFC | 900 | 75 | 460 | 93 | 93 | 93.6
TEFC | 900 | 100 | 460 | 93 | 93 | 93.6
TEFC | 900 | 125 | 460 | 93.6 | 93.6 | 94.1
TEFC | 900 | 150 | 460 | 93.6 | 93.6 | 94.1
TEFC | 900 | 200 | 460 | 94.1 | 94.1 | 94.5
TEFC | 900 | 250 | 460 |  | 94.5 | 94.5
TEFC | 900 | 300 | 460
TEFC | 900 | 350 | 460
TEFC | 900 | 400 | 460
TEFC | 900 | 450 | 460
Page 6 of 8
Induction Motor Efficiency Standards
See notes at end of tables
Enclosure | Speed | Horsepower | Volt | Old NEMA | NEMA EPACT | IEEE 841 | NEMA Premium
TEFC | 900 | 500 | 460
ODP | 3600 | 250 | 4000 |  |  |  | 94.5
ODP | 3600 | 300 | 4000 |  |  |  | 94.5
ODP | 3600 | 350 | 4000 |  |  |  | 94.5
ODP | 3600 | 400 | 4000 |  |  |  | 94.5
ODP | 3600 | 450 | 4000 |  |  |  | 94.5
ODP | 3600 | 500 | 4000 |  |  |  | 94.5
ODP | 1800 | 250 | 4000 |  |  |  | 95
ODP | 1800 | 300 | 4000 |  |  |  | 95
ODP | 1800 | 350 | 4000 |  |  |  | 95
ODP | 1800 | 400 | 4000 |  |  |  | 95
ODP | 1800 | 450 | 4000 |  |  |  | 95
ODP | 1800 | 500 | 4000 |  |  |  | 95
ODP | 1200 | 250 | 4000 |  |  |  | 95
ODP | 1200 | 300 | 4000 |  |  |  | 95
ODP | 1200 | 350 | 4000 |  |  |  | 95
ODP | 1200 | 400 | 4000 |  |  |  | 95
ODP | 1200 | 450 | 4000 |  |  |  | 95
ODP | 1200 | 500 | 4000 |  |  |  | 95
ODP | 3600 | 300 | 4000 |  |  |  | 94.5
ODP | 3600 | 350 | 4000 |  |  |  | 94.5
ODP | 3600 | 400 | 4000 |  |  |  | 94.5
ODP | 3600 | 450 | 4000 |  |  |  | 94.5
ODP | 3600 | 500 | 4000 |  |  |  | 94.5
ODP | 900 | 250 | 4000
ODP | 900 | 300 | 4000
ODP | 900 | 350 | 4000
ODP | 900 | 400 | 4000
ODP | 900 | 450 | 4000
ODP | 900 | 500 | 4000
TEFC | 3600 | 250 | 4000 |  |  | 95 | 95
TEFC | 3600 | 300 | 4000 |  |  | 95 | 95
TEFC | 3600 | 350 | 4000 |  |  | 95 | 95
Page 7 of 8
Induction Motor Efficiency Standards
See notes at end of tables
Enclosure | Speed | Horsepower | Volt | Old NEMA | NEMA EPACT | IEEE 841 | NEMA Premium
TEFC | 3600 | 400 | 4000 |  |  | 95 | 95
TEFC | 3600 | 450 | 4000 |  |  | 95 | 95
TEFC | 3600 | 500 | 4000 |  |  | 95 | 95
TEFC | 1800 | 250 | 4000 |  |  | 95 | 95
TEFC | 1800 | 300 | 4000 |  |  | 95 | 95
TEFC | 1800 | 350 | 4000 |  |  | 95 | 95
TEFC | 1800 | 400 | 4000 |  |  | 95 | 95
TEFC | 1800 | 450 | 4000 |  |  | 95 | 95
TEFC | 1800 | 500 | 4000 |  |  | 95 | 95
TEFC | 1200 | 250 | 4000 |  |  | 95 | 95
TEFC | 3600 | 300 | 4000 |  |  | 95 | 95
TEFC | 3600 | 350 | 4000 |  |  | 95 | 95
TEFC | 3600 | 400 | 4000 |  |  | 95 | 95
TEFC | 3600 | 450 | 4000 |  |  | 95 | 95
TEFC | 3600 | 500 | 4000 |  |  | 95 | 95
TEFC | 900 | 250 | 4000 |  |  | 95
TEFC | 900 | 300 | 4000 |  |  | 95
TEFC | 900 | 350 | 4000 |  |  | 95
TEFC | 900 | 400 | 4000 |  |  | 95
TEFC | 900 | 450 | 4000 |  |  | 95
TEFC | 900 | 500 | 4000 |  |  | 95
Notes:
Speed |  | Synchronous speed: equal to 7200 / #poles
Horsepower |  | Rated Horsepower
Volt |  | Volt Code: 460 means = or < 600 V; 4000 means > 600 V
Old NEMA |  | Earliest NEMA standard for “Energy Efficient” label.
Lower than current “Energy Efficient” standard
NEMA EPACT |  | Current NEMA standard for “Energy Efficient” label.
Sames as EPAct but EPAct doesn’t exist at >200 HP or <1200 RPM
IEEE 841 |  | IEEE 841-2001 standard
NEMA Premium |  | NEMA standard for “Premium Efficient” label.
© 2005 Washington State University Extension Energy Program. This publication contains material written and produced for public distribution. You may reprint this written material, provided you do not use it to endorse a commercial product. Please reference by title and credit Washington State University Extension Energy Program and the Northwest Energy Efficiency Alliance.
WSUEEP02_029 April 2002, Revised July 2002, Updated October 2005
Page 8 of 8

## C_HVAC_VRF
COMMERCIAL: VRF
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the PY25 TRM. Reevaluate the full load efficiency requirement for split-system and single-package air-cooled AC and air-source heat pump systems by PY28.
MEASURE DETAILS
Description
Inverter-driven direct expansion AC and heat pump systems that use variable flow distributed refrigerant technology for cooling and heating can more closely match the AC system's output with the building's cooling requirements. These systems consist of an outdoor unit with a single variable speed compressor or multiple staged compressors capable of varying system capacity and distributing refrigerant through a piping network, indoor evaporator units with variable speed fans designed for single zone air distribution, and zonal temperature controls. Variable refrigerant flow (VRF) implies three or more steps of control on standard, interconnecting piping.
An air-cooled VRF system is assumed to replace an air-cooled AC or air-source HP system, while a water-source VRF system is assumed to replace a water-source HP system.
Program Criteria
Eligible VRF equipment must meet or exceed the federal code for VRF multi-split AC or heat pump systems or exceed ASHRAE minimum efficiencies by 10% or more, as applicable for the given system type.
The following VRF projects require a custom approach:
| • | Systems with capacities ≥ 240,000 Btu/h in total
| • | Water-source VRF HP systems with capacities ≥ 135,000 Btu/h in total
| • | Water-source VRF systems replacing air-cooled AC or air-source HP systems
| • | Air-cooled VRF systems replacing water-source HP systems
| • | Early retirement (ER) projects
| • | Installations in industrial and cold storage applications
Unit of Measure
Measure impacts are calculated per system.
Baseline Equipment
The baseline assumes the customer would install the minimum efficiency (non-VRF) split/package AC/HP system without the program since VRF systems are such a new technology.
The baseline equipment meets the current federal and state requirements and ASHRAE 90.1-2019 standards as of January 1, 2025. Split-system and single-package air-cooled AC and air-source HP systems with capacities < 65,000 Btu/h have minimum SEER2 requirements. Split-system and single-package air-cooled AC and air-source HP systems with capacities ≥ 65,000 Btu/h have minimum IEER requirements. Water-source HP systems have minimum EER requirements.
Split-system and single-package air-cooled AC and air-source HP systems do not have state, federal, or ASHRAE minimum EER2 (or EER) requirements. An "industry standard practice" baseline was used to calculate the peak demand savings. It involved setting the baseline values equal to the most common EER2 (or EER) value for the given SEER2 (or IEER) minimum requirement, as determined through analysis of AHRI data.
Water-source HP systems do not have state, federal, or ASHRAE minimum SEER (or IEER) requirements. The baseline SEER (or IEER) values were set equal to the baseline EER requirements in the calculation worksheet to calculate energy savings.
The semi-prescriptive savings approach presented here assumes replace-on-burnout (ROB). Early retirement (ER) projects require a custom dual baseline approach: use the pre-existing equipment for the 1st ER baseline; use ASHRAE 90.1-2019 and current state requirements for the 2nd ER baseline. Documentation that shows the pre-existing equipment was operating and had a meaningful remaining useful life before replacement is required to be eligible for a custom ER savings approach.
High Efficiency Equipment
Residential-scale high-efficiency equipment must meet or exceed 15.2 SEER2. VRF systems must meet or exceed the federal code for VRFs. All other eligible high-efficiency equipment must exceed baseline minimum efficiencies by 10% or more, as applicable for the given system type. An additional tier (20% above baseline) has also been included for this measure.
There are no program requirements for full-load efficiency (EER2 or EER) for split-system and single-package air-cooled AC and air-source HP systems.
Water-source heat pumps do not have state, federal, or ASHRAE minimum SEER (or IEER) requirements. Therefore, the high efficiency SEER (or IEER) values are equal to the high efficiency EER requirements in the calculation worksheet.
ALGORITHMS
Peak Demand Reduction, kW
(1)
[EER2 used in place of EER for split/single-package AC and HP units <65,000 Btu/h]
Annual Energy Savings, kWh/yr
(2)
[SEER2 used in place of IEER for split/single-package AC and HP units <65,000 Btu/h]
[SEER used in place of IEER for all other units <65,000 Btu/h]
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | Value |  | Unit | Source/Notes
Capacity |  |  |  | Rated capacity, in Btu/h, of installed unit | Based on installed unit |  | Btu/h | As installed
EERBL or EER2BL |  |  |  | Energy Efficiency Ratio of baseline unit. Used to represent full-load operation. | See Table 1 in C_HVAC_VRF_WKST |  | Btu/Wh | Equal to the state, federal, and ASHRAE 90.1-2019 minimum efficiency requirements, as applicable to the given system type. (Refer to the Baseline Equipment description above for more information.)
EEREE or EER2EE |  |  |  | Energy Efficiency Ratio of installed high efficiency unit. Used to represent full-load operation. | User input |  | Btu/Wh | As installed. At least 10% better than the baseline efficiency, as applicable to the given system type. (Refer to the High Efficiency Equipment description above for more information.)
IEERBL, SEER2BL or SEERBL |  |  |  | Integrated or Seasonal Energy Efficiency Ratio of baseline unit. Used to represent part-load operation. SEER2 or SEER is used for units <65,000 Btu/h. | See Table 1 in C_HVAC_VRF_WKST |  | Btu/Wh | Equal to the state, federal, and ASHRAE 90.1-2019 minimum efficiency requirements, as applicable to the given system type. (Refer to the Baseline Equipment description above for more information.)
IEEREE, SEER2EE or SEEREE |  |  |  | Integrated or Seasonal Energy Efficiency Ratio of installed high efficiency unit. Used to represent part-load operation. SEER2 or SEER is used for units <65,000 Btu/h. | User input |  | Btu/Wh | As installed. At least 10% better than the baseline efficiency, as applicable to the given system type. (Refer to the High Efficiency Equipment description above for more information.)
EFLH |  |  |  | Equivalent full load cooling hours | See Table 1 in C_HVAC_VRF_WKST |  | hrs | AEG's analysis of DOE's OpenEI load shapes using Hawaii-specific prototypes and weather data
CF |  |  |  | Coincidence factor | See Table 1 in C_HVAC_VRF_WKST |  | - | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period
EUL |  |  |  | Effective useful life of measure | 20 |  | years | AEG's Fall 2018 Benchmarking
SAVINGS
| For calculations specific to the unit in question, please see the accompanying VRF calculation worksheet: |  |  |  |  | (C_HVAC_VRF_WKST)
RESOURCES
• | ICF's PY25 Analysis File named "PY25 TRM - Commercial HVAC - Analysis file."
• | AEG's PY24 Analysis File named "PY24 TRM - Commercial HVAC VRF - Analysis file."
• | AEG's PY19 Analysis File named "AEG HPUC Update - Ductless Systems - Analysis File," and the PY20 files named "AEG HPUC C_HVAC_VRF AC & HP - Analysis File," and "AEG HPUC - HVAC Measures - Analysis File_Jan 2021."
• | Air-Conditioning, Heating, & Refrigeration Institute (AHRI), Directory of Certified Products, accessed Sep. 2022, Nov. 2022, and Apr. 2025, available here: <https://ahridirectory.org/>.
• | ANSI/ASHRAE/IES Standard 90.1-2019, Energy Standard for Buildings Except Low-Rise Residential Buildings, (I-P Edition), 2019, available here: <https://www.ashrae.org/technical-resources/bookstore/standard-90-1>.
• | Code of Federal Regulations, 10 CFR 430.32, Subpart C, Energy and Water Conservation Standards and their Effective Dates, Paragraph (c): Central Air Conditioners and Heat Pumps, available here: <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>.
• | Code of Federal Regulations, 10 CFR 431.97, Subpart F, Energy Efficiency Standards and their Compliance Dates, Paragraphs (b), (c), and (d), available here: <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-F/subject-group-ECFR2640f6ad978e4e6/section-431.97>.
• | National Renewable Energy Laboratory. (2014). Commercial and Residential Hourly Load Profiles for all TMY3 Locations in the United States [data set]. Retrieved from <https://dx.doi.org/10.25984/1788456>.
• | Ery Djunaedy, Kevin van den Wymelenberg, Brad Acker, Harshana Thimmana, Oversizing of HVAC system: Signatures and penalties, Energy and Buildings, Volume 43, Issues 2–3, 2011, Pages 468-475, ISSN 0378-7788, <https://doi.org/10.1016/j.enbuild.2010.10.011>. Used to determine correct HVAC oversizing adjustment for EFLH and CF analysis.
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅〗_𝐵𝐿−〗 1∕〖〖𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐶𝐹
∆𝑘𝑊ℎ=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐼𝐸𝐸𝑅〗_𝐵𝐿−〗 1∕〖〖𝐼𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻

## C_HVAC_VRF_WKST
Commercial: HVAC Savings Calculator - Variable Refrigerant Flow Systems
Return to TOC
| Step 1: Enter AC or HP nameplate data* |  |  |  | Step 2: Determine if it qualifies |  |  | Step 3: Calculate savings |  | Single-Phase Split System AC
[6 empty] | Full Load | Part Load |  |  | Single-Phase Single Package AC
| Enter AC or HP Type: | Single-Phase Split System AC |  |  | Tier 1 | NA | Pass | CF: | 0.43 | Three-Phase Split System AC
| Enter Rated AC or HP Capacity (Btu/h): | 64000 |  |  | Tier 2 | NA | Fail | EFLH: | 2549 | Three-Phase Single Package AC
| Enter Building Type: | Education | [5 empty] | kW savings: | 0.622 | Split System & Single Package AC
| Enter Full Load Efficiency: | 15 | EER or EER2 |  | Capacity Bin: | ≥ 45,000 and < 65,000 Btu/h |  | kWh/yr savings: | 1625.45 | Single-Phase Split System HP
| Enter Part-Load Efficiency: | 16 | SEER or SEER2 |  | Corresponding Baseline Efficiency (Full Load): | 11.2 | EER or EER2 | Lifetime kWh: | 32509 | Single-Phase Single Package HP
| Notes: 1) If an efficiency value is unknown, check AHRI Directory (www.ahridirectory.org); 2) Use EER2 and SEER2 for Split System and Single Package Systems < 65,000 Btu/h. |  |  |  | Corresponding Baseline Efficiency (Part-Load): | 13.8 | SEER or SEER2 | Meets | Tier 1 | Three-Phase Split System Air-Source HP
Three-Phase Single Package Air-Source HP
Air-Source HP
Water-Source HP
Table 1: Minimum Baseline Efficiencies; Assumes non-VRF Baseline
| System Type | Capacity Bin | Part-Load Efficiency |  | Full Load Efficiency
|  |  | SEER or SEER2 | IEER | EER or EER2 | Concatenation
| Single-Phase Split System AC | < 45,000 Btu/h | 14.3 | -- | 11.7 | Single-Phase Split System AC - < 45,000 Btu/h
| Single-Phase Split System AC | ≥ 45,000 and < 65,000 Btu/h | 13.8 | -- | 11.2 | Single-Phase Split System AC - ≥ 45,000 and < 65,000 Btu/h
| Single-Phase Single Package AC | < 65,000 Btu/h | 13.4 | -- | 10.6 | Single-Phase Single Package AC - < 65,000 Btu/h |  |  |  | SEER or IEER?
| Three-Phase Split System AC | < 65,000 Btu/h | 13.4 | -- | 10.6 | Three-Phase Split System AC - < 65,000 Btu/h |  |  |  | SEER or SEER2
| Three-Phase Single Package AC | < 65,000 Btu/h | 13.4 | -- | 10.6 | Three-Phase Single Package AC - < 65,000 Btu/h |  |  |  | IEER
| Split System & Single Package AC | ≥ 65,000 and < 135,000 Btu/h | -- | 14.8 | 11.2 | Split System & Single Package AC - ≥ 65,000 and < 135,000 Btu/h
| Split System & Single Package AC | ≥ 135,000 and < 240,000 Btu/h | -- | 14.2 | 11 | Split System & Single Package AC - ≥ 135,000 and < 240,000 Btu/h
| Split System & Single Package AC | ≥ 240,000 Btu/h | -- | 13.2 | 10 | Split System & Single Package AC - ≥ 240,000 Btu/h |  |  |  | 1000 | < 65,000 Btu/h
| Single-Phase Split System HP | < 65,000 Btu/h | 14.3 | -- | 11.7 | Single-Phase Split System HP - < 65,000 Btu/h |  |  |  | 65000 | ≥ 65,000 and < 135,000 Btu/h
| Single-Phase Single Package HP | < 65,000 Btu/h | 13.4 | -- | 10.6 | Single-Phase Single Package HP - < 65,000 Btu/h |  |  |  | 135000 | ≥ 135,000 and < 240,000 Btu/h
| Three-Phase Split System Air-Source HP | < 65,000 Btu/h | 14.3 | -- | 11.7 | Three-Phase Split System Air-Source HP - < 65,000 Btu/h |  |  |  | 240000 | ≥ 240,000 Btu/h
| Three-Phase Single Package Air-Source HP | < 65,000 Btu/h | 13.4 | -- | 10.6 | Three-Phase Single Package Air-Source HP - < 65,000 Btu/h
| Air-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 14.1 | 11 | Air-Source HP - ≥ 65,000 and < 135,000 Btu/h |  |  |  | 1000 | < 17,000 Btu/h
| Air-Source HP | ≥ 135,000 and < 240,000 Btu/h | -- | 13.5 | 10.6 | Air-Source HP - ≥ 135,000 and < 240,000 Btu/h |  |  |  | 17000 | ≥ 17,000 and < 65,000 Btu/h
| Air-Source HP | ≥ 240,000 Btu/h | -- | 12.5 | 9.5 | Air-Source HP - ≥ 240,000 Btu/h |  |  |  | 65000 | ≥ 65,000 and < 135,000 Btu/h
| Water-Source HP | < 17,000 Btu/h | 12.2 | -- | 12.2 | Water-Source HP - < 17,000 Btu/h |  |  |  | 135000 | ≥ 135,000 Btu/h
| Water-Source HP | ≥ 17,000 and < 65,000 Btu/h | 13 | -- | 13 | Water-Source HP - ≥ 17,000 and < 65,000 Btu/h
| Water-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 13 | 13 | Water-Source HP - ≥ 65,000 and < 135,000 Btu/h |  |  |  | 1000 | < 45,000 Btu/h
[10 empty] | 45000 | ≥ 45,000 and < 65,000 Btu/h
| Table 2: Minimum Qualifying Efficiencies - Tier 1 (Baseline + 10%) | [8 empty] | 65000 | ≥ 65,000
| System Type | Capacity Bin | Part-Load Efficiency |  | Full Load Efficiency
|  |  | SEER | IEER | EER
| Single-Phase Split System AC | < 45,000 Btu/h | 15.2 | -- | NA
| Single-Phase Split System AC | ≥ 45,000 and < 65,000 Btu/h | 15.2 | -- | NA
| Single-Phase Single Package AC | < 65,000 Btu/h | 15.2 | -- | NA
| Three-Phase Split System AC | < 65,000 Btu/h | 14.7 | -- | NA
| Three-Phase Single Package AC | < 65,000 Btu/h | 14.7 | -- | NA
| Split System & Single Package AC | ≥ 65,000 and < 135,000 Btu/h | -- | 16.28 | NA
| Split System & Single Package AC | ≥ 135,000 and < 240,000 Btu/h | -- | 15.62 | NA
| Split System & Single Package AC | ≥ 240,000 Btu/h | -- | 14.52 | NA
| Single-Phase Split System HP | < 65,000 Btu/h | 15.2 |  | NA
| Single-Phase Single Package HP | < 65,000 Btu/h | 15.2 |  | NA
| Three-Phase Split System Air-Source HP | < 65,000 Btu/h | 15.7 |  | NA
| Three-Phase Single Package Air-Source HP | < 65,000 Btu/h | 14.7 |  | NA
| Air-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 15.51 | NA
| Air-Source HP | ≥ 135,000 and < 240,000 Btu/h | -- | 14.85 | NA
| Air-Source HP | ≥ 240,000 Btu/h | -- | 13.75 | NA
| Water-Source HP | < 17,000 Btu/h | 16 | 16 | NA
| Water-Source HP | ≥ 17,000 and < 65,000 Btu/h | 16 | 16 | NA
| Water-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 16 | NA
Table 3: Minimum Qualifying Efficiencies - Tier 2 (Tier 1 + 10%)
| System Type | Capacity Bin | Part-Load Efficiency |  | Full Load Efficiency
|  |  | SEER | IEER | EER
| Single-Phase Split System AC | < 45,000 Btu/h | 16.7 | -- | NA
| Single-Phase Split System AC | ≥ 45,000 and < 65,000 Btu/h | 16.7 | -- | NA
| Single-Phase Single Package AC | < 65,000 Btu/h | 16.7 | -- | NA
| Three-Phase Split System AC | < 65,000 Btu/h | 16.1 | -- | NA
| Three-Phase Single Package AC | < 65,000 Btu/h | 16.1 | -- | NA
| Split System & Single Package AC | ≥ 65,000 and < 135,000 Btu/h | -- | 17.9 | NA
| Split System & Single Package AC | ≥ 135,000 and < 240,000 Btu/h | -- | 17.2 | NA
| Split System & Single Package AC | ≥ 240,000 Btu/h | -- | 16 | NA
| Single-Phase Split System HP | < 65,000 Btu/h | 16.7 |  | NA
| Single-Phase Single Package HP | < 65,000 Btu/h | 16.7 |  | NA
| Three-Phase Split System Air-Source HP | < 65,000 Btu/h | 17.2 |  | NA
| Three-Phase Single Package Air-Source HP | < 65,000 Btu/h | 16.1 |  | NA
| Air-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 17.1 | NA
| Air-Source HP | ≥ 135,000 and < 240,000 Btu/h | -- | 16.3 | NA
| Air-Source HP | ≥ 240,000 Btu/h | -- | 15.1 | NA
| Water-Source HP | < 17,000 Btu/h | 17.6 | 17.6 | NA
| Water-Source HP | ≥ 17,000 and < 65,000 Btu/h | 17.6 | 17.6 | NA
| Water-Source HP | ≥ 65,000 and < 135,000 Btu/h | -- | 17.6 | NA
Table 4: Equivalent Full Load Hours and Coincident Factors for Commercial Cooling in Hawaii
| Building Type | EFLH | CF
| Avg. Commercial | 2594 | 0.38
| Cold Storage | Varies | Varies
| Education | 2549 | 0.43
| Grocery | 1531 | 0.27
| Health | 4891 | 0.55
| Hotel/Motel | 4910 | 0.6
| Industrial | Varies | Varies
| Office | 2754 | 0.48
| Restaurant | 2451 | 0.4
| Retail | 1913 | 0.29
| Warehouse | 1033 | 0.01
Note on G6: Reevaluate requirement by PY28.
Note on G7: Reevaluate requirement by PY28.
Note on D10: Will change according to AC size
Note on H11: Will change according to AC size
Note on F19: There is no federal or state minimum EER2 requirement for Hawaii. AEG's research of the AHRI database (Nov 2022 extracts) showed that each EER2 value in Table 1 represents the most common EER2 value for the given SEER2 minimum requirement. Refer to AEG's Analysis File named "PY23 TRM - Commercial AC and HP - Analysis File" for more information. These EER2 values are also consistent with ASHRAE's minimum requirements for single-phase central ACs and HPs in the Southwestern region (see Table F-1, ASHRAE 90.1-2019). Note that ASHRAE considers Hawaii to be part of the Southeastern region, which does not have minimum EER2 requirements.
Note on F24: There are no longer federal or ASHRAE minimum EER requirements for larger commercial unitary AC and Air-Source HP equipment (≥ 65,000 Btu/h). AEG's research of the AHRI database (Apr 2025 extract) showed that each EER value in Table 1 represents the most common EER value for the given IEER minimum requirement. These EER values also match the previous minimum federal code and ASHRAE 90.1-2016 standards for EER. Refer to AEG's Analysis File named "PY25 TRM - Commercial HVAC - Analysis File" for more information.
Note on C26: All units greater than 240 kBtu/h are recommended for custom evaluation
Note on R29: All units greater than 240 kBtu/h are recommended for custom evaluation
Note on D34: No ASHRAE requirement for water-source HP SEER; set equal to EER
Note on E36: No ASHRAE requirement for water-source HP IEER; set equal to EER
Note on D42: ENERGY STAR 6.1
Note on D43: ENERGY STAR 6.1
Note on D44: ENERGY STAR 6.1
Note on D50: ENERGY STAR 6.1
Note on D51: ENERGY STAR 6.1
Note on D57: No ASHRAE requirement for VRF water-source HP SEER; set equal to IEER
Note on D58: No ASHRAE requirement for VRF water-source HP SEER; set equal to IEER
Note on D65: ENERGY STAR 6.1 +10%
Note on D66: ENERGY STAR 6.1 +10%
Note on D67: ENERGY STAR 6.1 +10%
Note on D73: ENERGY STAR 6.1 +10%
Note on D74: ENERGY STAR 6.1 +10%
Note on D80: No ASHRAE requirement for VRF water-source HP SEER; set equal to IEER
Note on D81: No ASHRAE requirement for VRF water-source HP SEER; set equal to IEER

## C_HVAC_EMS
COMMERCIAL: Guest Room Energy Management System
Return to TOC
UPDATE STATUS
Updated in Fall 2019 for PY19 TRM v2.0.
MEASURE DETAILS
Description
A Guest Room Energy Management System uses a passive infrared occupancy sensor to sense whether the guest room in a hotel/motel is occupied or unoccupied, and then powers down or adjusts the setpoints of the HVAC unit during periods of no occupancy. The controller may be physically located in a separate control box, jointly with an occupancy sensor, or jointly with a thermostat depending on the vendor and existing site parameters.
Program Criteria
• All entry and lanai doors must have door switches or other technologies that will de-energize the fan coil unit (FCU) when the door remains open. • All main rooms must have occupancy sensors that will de-energize the FCU when no movement is detected for a given period of time (not to exceed 15 minutes). • Thermostat controls must be preset. • Applicant must be on a Commercial Rate Schedule (reference utility bill).
Unit of Measure
Per room/unit controlled by EMS.
Baseline Equipment
No Guest Room EMS controls.
High Efficiency Equipment
Guest Room EMS controls.
ALGORITHMS
Peak Demand Reduction, kW/room
(1)
Annual Energy Savings, kWh/yr-room
(2)
Lifetime Energy Savings, kWh/room
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Value | Unit | Source/Notes
∆kWh per Room |  | Deemed annual energy savings per room, per unit |  |  | See Table 1 | kWh/yr | See Footnote 1
∆kW per Room |  | Deemed demand reduction per room, per unit |  |  | See Table 1 | kW | See Footnote 1
EUL |  | Effective useful life of measure |  |  | 15 | years | No change from PY18 TRM; EUL was verified during AEG's 2018 benchmarking.
1 Savings were determined using an average savings percentage of 35% from five (5) PTAC case studies documented in a 2016 Pacific Gas & Electric (PG&E) Non-DEER Workpaper applied to consumption estimates from Hawai‘i commercial prototype hourly load profiles from the U.S. DOE OpenEI Data Catalog. Demand reductions were then determined using the method recommended by the PG&E workpaper and coincidence factors determined from Hawai‘i hourly load profiles.
SAVINGS
Table 1: Deemed Savings per Room/Unit for Guest Room Energy Management System
Building Type |  |  | Peak Demand Savings | Annual Energy Savings |  |  | Lifetime Energy Savings
Large Hotel, 100+ Rooms |  |  | 0.368 | 1214.1 |  |  | 18211.5
Small Hotel/Motel, <100 Rooms |  |  | 0.274 | 872.29 |  |  | 13084.35
RESOURCES
• | AEG's Analysis File titled "AEG HPUC Update - Guest Room EMS - Analysis File" and "AEG HPUC Mid-Year PY19 TRM Updates_Analysis File."
• | BC Hydro M&V Study. The Blue Horizon Hotel, “Two Passive Infrared Motion Sensor Systems for in Room Energy Hotel Management” November 2007.
• | DOE New Construction Commercial Reference Building Prototype Summary Files. Version 1.3_5.0. September 27, 2010. Available as part of the compressed files at: https://www.energy.gov/eere/buildings/new-construction-commercial-reference-buildings.
• | FEMP Case Study. The Music Road Hotel, “Demonstration and Evaluation of HVAC Controller for Lodging Facilities”, July 2002.
• | KEMA Focus On Energy Evaluation, WI: bpdeemedsavingsmanuav10_evaluationreport.pdf.
• | Office of Energy Efficiency and Renewable Energy. Commercial and Residential Hourly Load Profiles for All TMY3 Locations in the United States. U.S. Department of Energy Open Data Catalog. Available at: https://openei.org/doe-opendata/dataset/commercial-and-residential-hourly-load-profiles-for-all-tmy3-locations-in-the-united-states.
• | Pacific Gas and Electric Company. PTAC/PTHP/Split AC Controller. Work Paper PGE3PHVC149 Revision 2, Measure Code HA82. January 1, 2016. Available at: http://www.deeresources.net/workpapers.
• | QuEST PTAC Controls Program, Technical Work Paper (PG&E): HOSPITALITY – PTAC QUEST).doc
∆𝑘𝑊=∆𝑘𝑊 𝑝𝑒𝑟 𝑅𝑜𝑜𝑚
∆𝑘𝑊ℎ=∆𝑘𝑊ℎ 𝑝𝑒𝑟 𝑅𝑜𝑜𝑚
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿

## C_HVAC_FEI-Certified Fan
COMMERCIAL: FEI-Certified Standalone Fan
Return to TOC
UPDATE STATUS
Introduced in Spring 2026 for the PY26 TRM.
MEASURE DETAILS
Description
The Fan Energy Index (FEI) is a wire‑to‑air efficiency metric that characterizes the performance of an entire fan system, including the fan, motor, and drive. FEI replaces the former Fan Efficiency Grade (FEG) and is defined by ANSI/AMCA Standard 208. FEI is calculated using data from standardized laboratory performance tests and represents the ratio of the electrical input power of a reference fan to that of the actual fan operating at a specified duty point (airflow and pressure).
FEI provides a standardized basis for comparing fan system energy performance at a common duty point across fan types and sizes. Higher FEI values indicate lower electrical input power at the design operating condition and therefore higher overall fan system efficiency.
FEI is incorporated into ASHRAE Standard 90.1‑2019 and the 2021 International Energy Conservation Code (IECC‑2021), which require FEI ratings to be certified by an approved third‑party laboratory. Minimum code requirements are FEI ≥ 1.0 for constant‑speed fans and FEI ≥ 0.95 for variable‑speed fans. Certified FEI ratings and participating manufacturers are listed at www.amca.org/find-FEI.
This measure applies to the installation of a standalone fan that exceeds applicable code minimum efficiency requirements through the selection of a fan with an FEI greater than the code‑mandated minimum and greater than the minimum FEI requirements established under Hawai'i Energy’s prescriptive FEI program.
This measure evaluates savings attributable solely to improvements in fan efficiency for fans with equivalent control strategies. Measures that involve control system changes, such as the addition of variable frequency drives (VFDs), are addressed under the Commercial VFD HVAC Water Pump and Fan measure (C_HVAC_VFD_Water Pump), in which FEPEE replaces the (0.746 * HP * Load Factor/ Motor Efficiency ) term in the VFD savings calculation.
Program Criteria
To qualify for a Hawai‘i Energy FEI incentive, all of the following conditions must be met: 1. FEI Certification Each fan or fan array must have an AMCA‑certified minimum FEI rating of: • FEI≥1.12 for fan ≤10 hp • FEI≥1.22 for 10 hp < fan ≤ 60 hp • FEI≥1.25 for fans 60 hp < fan ≤ 200 hp
2. Fan Configuration Fans must be standalone fans and may not be embedded within packaged equipment. A standalone fan may include, or exclude, a motor, variable speed drive (VSD), and/or transmission (e.g., belt drive).
3. Fan Size Threshold Fans must have either: • A motor nameplate horsepower greater than 1.0 hp, or • A fan nameplate electrical input power greater than 0.89 kW.
4. Applicable End Uses Eligible fans include HVAC supply, return, exhaust, and relief fans.
5. Eligible Fan Types Qualifying fan types include: • Axial, cylindrical housed • Panel • Centrifugal, housed • Centrifugal, unhoused • Inline and mixed‑flow • Radial • Power roof ventilators
6. Exclusions The following fan types are not eligible: • Ceiling fans • Reversible fans used for tunnel ventilation • Fans that operate exclusively under emergency conditions
Unit of Measure
One fan
Baseline Equipment
The baseline equipment is a standardized fan with an FEI of 1.00 for constant speed operation and 0.95 for variable speed operation.
High Efficiency Equipment
The high efficiency equipment is a fan with an FEI≥1.12 for fans ≤ 10 hp, FEI ≥1.22 for 10 hp < fan ≤ 60 hp, and FEI≥1.25 for 60 hp < fan ≤ 200 hp
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  | Unit | Source/Notes
FEPEE |  |  |  | Fan electric power of energy efficient fan at 100% flow fraction | [11 empty] | User input |  | kW | Available in fan specifications
FEIEE |  |  |  | Fan energy index for energy efficient fan at 100% fraction | [11 empty] | User input |  | - | Available in fan specifications
FEIBL |  |  |  | Fan energy index of baseline fan at 100% flow fraction | [11 empty] | See Table 1 |  | - | ASHRAE 90.1-2019 [1]
EFLH |  |  |  | Equivalent full load hours for commercial fan | [11 empty] | See Table 2 |  | hours | Hawaii TRM "ELFH & CF" sheet summarizing Equipment Operating Hours and Coincidence Factors [2]
%FF |  |  |  | Percentage of run time spent within a given flow fraction range | [11 empty] | See Table 3 |  | - | ICF analysis file named "FEI Measure - HI Ventilation Load Shape Analysis for Percent_FF". See "Bins" sheet. [3]
PLR |  |  |  | Part load ratio for a given flow fraction range | [11 empty] | See Table 4 |  | - | Illinois TRM [4]
|  |  |  | Resultant values based on %FF and PLR | [11 empty] | See Table 5 |  | - | ICF analysis file named "FEI Measure - HI Ventilation Load Shape Analysis for Percent_FF". See "Bins" sheet. [3]
CF |  |  |  | Coincidence factor | [11 empty] | See Table 2 |  | - | Hawaii TRM "ELFH & CF" sheet summarizing Equipment Operating Hours and Coincidence Factors. [2]
EUL |  |  |  | Effective useful life of measure | [11 empty] | 16 |  | years | ICF analysis file named "PY26 TRM - Commercial FEI Certified Standalone Fan - Analysis File". See "EUL Benchmarking" sheet.
1. ANSI/ASHRAE/IES Standard 90.1-2019. Energy Standard for Buildings Except Low-Rise Residential Buildings. <https://ashrae.iwrapper.com/ASHRAE_PREVIEW_ONLY_STANDARDS/STD_90.1_2019>
2. ICF applied the Equivalent Full Load Hours and Coincidence Factors for Commercial Fans from the Hawaii TRM "EFLH & CF" sheet to the Commercial FEI Certified Standalone Fan measure.
3. ICF analysis of Hawaii-specific ventilation end-use load shapes developed for the 2020 Market Potential Study. The underlying load shapes are derived from the National Renewable Energy Laboratories End-Use Load Shape data (now National Laboratory of the Rockies). ICF converted the load shapes to flow shapes using the fan affinity laws. ICF then developed Hawaii-specific %FF and Resultant values and applied them to the Commercial FEI Certified Standalone Fan measure.
4. Illinois Statewide Technical Reference Manual for Energy Efficiency Version 14.0 Volume 2: Commercial and Industrial Measures. <https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010126_v14.0_Vol_2_C_and_I_09192025_FINAL.pdf >
Table 1. Baseline FEI in Commercial Fan Applications
Commercial Fan Application | [8 empty] | FEIBL
Constant Speed Fan | [8 empty] | 1
Variable Speed Fan | [8 empty] | 0.95
1. ANSI/ASHRAE/IES Standard 90.1-2019. Energy Standard for Buildings Except Low-Rise Residential Buildings.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Table 2. EFLH and CF for Fan Based on Building Type
Building Type | [8 empty] | EFLH | [5 empty] | CF
Avg./Misc. Commercial | [8 empty] | 5384 | [5 empty] | 0.7
Cold Storage | [8 empty] | 3436 | [5 empty] | 0.01
Education | [8 empty] | 2639 | [5 empty] | 0.46
Grocery | [8 empty] | 5840 | [5 empty] | 1
Health | [8 empty] | 5849 | [5 empty] | 0.67
Hotel/Motel | [8 empty] | 7837 | [5 empty] | 0.94
Industrial | [8 empty] | N/A | [5 empty] | N/A
Office | [8 empty] | 3675 | [5 empty] | 0.63
Restaurant | [8 empty] | 7300 | [5 empty] | 1
Retail | [8 empty] | 5278 | [5 empty] | 0.86
Warehouse | [8 empty] | 3436 | [5 empty] | 0.01
Source: AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period. The analysis was conducted using the commercial building fan end-use with Hawaii-specific prototypes, weather data, and peak demand period. See the EFLH & CF sheet of the Hawaii TRM for more information.
Table 3. %FF, Percentage of Run Time Spent within a Given Flow Fraction Range
Flow Fraction (% of design CFM) | [8 empty] | Percentage of Time at Flow Fraction
0% to 10% | [8 empty] | 0%
10% to 20% | [8 empty] | 0%
20% to 30% | [8 empty] | 0%
30% to 40% | [8 empty] | 0%
40% to 50% | [8 empty] | 0%
50% to 60% | [8 empty] | 30.7%
60% to 70% | [8 empty] | 5.2%
70% to 80% | [8 empty] | 12.6%
80% to 90% | [8 empty] | 29.9%
90% to 100% | [8 empty] | 21.6%
Source: ICF's analysis of Hawaii-specific ventilation end-use load shapes used for the 2020 Market Potential Study. The underlying load shapes are derived from the National Renewable Energy Laboratories End-Use Load Shape data (now National Laboratory of the Rockies). ICF converted the load shapes to flow shapes using the fan affinity laws. See the ICF analysis file named "FEI Measure - HI Ventilation Load Shape Analysis for Percent_FF".
Table 4. PLR, Part Load Ratio for a Given Flow Fraction Range
Control Type | [7 empty] | Flow Fraction
[8 empty] | 10% |  | 20% |  | 30% |  | 40% |  | 50% | 60% | 70% | 80% | 90% | 100%
No Control or Bypass Damper | [7 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 1 | 1 | 1 | 1 | 1
Discharge Dampers | [7 empty] | 0.46 |  | 0.55 |  | 0.63 |  | 0.7 |  | 0.77 | 0.83 | 0.88 | 0.93 | 0.97 | 1
Outlet Damper, Blade & Airfoils Fans | [7 empty] | 0.53 |  | 0.53 |  | 0.57 |  | 0.64 |  | 0.72 | 0.8 | 0.89 | 0.96 | 1.02 | 1.05
Inet Damper Box | [7 empty] | 0.56 |  | 0.6 |  | 0.62 |  | 0.64 |  | 0.66 | 0.69 | 0.74 | 0.81 | 0.92 | 1.07
Inlet Guide Vane, Blade & Airfoil Fans | [7 empty] | 0.53 |  | 0.56 |  | 0.57 |  | 0.59 |  | 0.6 | 0.62 | 0.67 | 0.74 | 0.85 | 1
Inlet Vane Dampers | [7 empty] | 0.38 |  | 0.4 |  | 0.42 |  | 0.44 |  | 0.48 | 0.53 | 0.6 | 0.7 | 0.83 | 0.99
Outlet Damper, FC Fans | [7 empty] | 0.22 |  | 0.26 |  | 0.3 |  | 0.37 |  | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06
Eddy Current Drives | [7 empty] | 0.17 |  | 0.2 |  | 0.25 |  | 0.32 |  | 0.41 | 0.51 | 0.63 | 0.76 | 0.9 | 1.04
Inlet Guide Vane, FC Fans | [7 empty] | 0.21 |  | 0.22 |  | 0.23 |  | 0.26 |  | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04
VFD with Duct Static Pressure Control | [7 empty] | 0.09 |  | 0.1 |  | 0.11 |  | 0.15 |  | 0.2 | 0.29 | 0.41 | 0.57 | 0.76 | 1.01
VFD with Low/No Duct Static Pressure Control | [7 empty] | 0.05 |  | 0.06 |  | 0.09 |  | 0.12 |  | 0.18 | 0.27 | 0.39 | 0.55 | 0.75 | 1
Source: Illinois Statewide Technical Reference Manual for Energy Efficiency Version 14.0 Volume 2: Commercial and Industrial Measures. <https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010126_v14.0_Vol_2_C_and_I_09192025_FINAL.pdf>
Table 5. Resultant Based on Values in Table 3 and Table 4
Control Type
No Control or Bypass Damper | [12 empty] | 1
Discharge Dampers | [12 empty] | 0.92
Outlet Damper, Blade & Airfoil Fans | [12 empty] | 0.94
Inet Damper Box | [12 empty] | 0.86
Inlet Guide Vane, Blade & Airfoil Fans | [12 empty] | 0.79
Inlet Vane Dampers | [12 empty] | 0.74
Outlet Damper, FC Fans | [12 empty] | 0.8
Eddy Current Drives | [12 empty] | 0.78
Inlet Guide Vane, FC Fans | [12 empty] | 0.69
VFD with Duct Static Pressure Control | [12 empty] | 0.63
VFD with Low/No Duct Static Pressure Control | [12 empty] | 0.61
Source: ICF analysis of Hawaii-specific ventilation end-use load shapes developed for the 2020 Market Potential Study. The underlying load shapes are derived from National Renewable Energy Laboratory (NREL) End-Use Load Shape data (now National Laboratory of the Rockies). See ICF analysis file named "FEI Measure - HI Ventilation Load Shape Analysis for Percent_FF".
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Enter FEP of New Fan at 100% Flow Fraction (units of kW)
50
Enter FEI for New Fan (Must exceed Hawaii Energy's program requirements)
1.6
Enter Fan Speed Type
Constant Speed Fan
Enter Fan Control Type
No Control or Bypass Damper
Enter Building Type
Avg./Misc. Commercial
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings |  |  |  | Lifetime Energy Savings
FEI-Certified Standalone Fan | [7 empty] | 21 | [7 empty] | 161520 |  |  |  | 2584320
Note: Savings shown in blue result from sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's Analysis File named "PY26 TRM - Commercial Fan Energy Index Certified Standalone Fan - Analysis File."
• | ICF's Analysis File named "FEI Measure - HI Ventilation Load Shape Analysis for Percent_FF."
• | AMCA Advocacy Brief, Update State Energy Codes to Save Fan Energy Using New Metric and Scope. October 2020. <https://www.amca.org/assets/resources/public/pdf/Advocacy/FEI%20for%20Energy%20Codes%20-%2020201022%20-%20v3.pdf>
• | AMCA. 2025 Update on Fan-Efficiency Codes and Regulations. <https://www.amca.org/educate/articles-and-technical-papers/amca-inmotion-articles/2025-update-on-u.s.-fan-efficiency-codes-and-regulations.html>
• | ANSI/AMCA Standard 208-18. Calculation of The Fan Energy Index. <https://webstore.ansi.org/preview-pages/AMCA/preview_ANSI+AMCA+208-18.pdf>
• | ANSI/AMCA Standard 214-21. Test Procedure for Calculating Fan Energy Index (FEI) for Commercial and Industrial Fans and Blowers.
• | ANSI/ASHRAE/IES Standard 90.1-2019, Energy Standard for Buildings Except Low-Rise Residential Buildings.
• | 2021 International Energy Conservation Code. <https://codes.iccsafe.org/content/IECC2021P1>
• | 2026 Illinois Statewide Technical Reference Manual for Energy Efficiency Version 14.0 Volume 2: Commercial and Industrial Measures. FINAL. September 19, 2025. Effective: January 1, 2026. <https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010126_v14.0_Vol_2_C_and_I_09192025_FINAL.pdf>
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Programs. Version 5.0. FINAL. January 1, 2026. <https://mn.gov/commerce-stat/trm/releases/5.0.pdf>
• | US DOE. 10 CFR Parts 429 and 431 [EERE-2022-BT-STD-0002] RIN 1904-AF40. Proposed Rule withdrawn on January 17, 2025. Energy Conservation Program: Energy Conservation Standards for Fans and Blowers. 01/19/2024. < https://www.energy.gov/sites/default/files/2023-12/fans_blowers_nopr.pdf>
• | Regional Technical Forum. Commercial & Industrial Fans Research Strategy v3.0/ June 24, 2025. <https://rtf.nwcouncil.org/measure/commercial-industrial-fans/>
• | Xcel Energy Colorado. 2024-2026 Demand-Side Management and Beneficial Electrification Plan. Proceeding No. 23A-XXXXXEG. Appendix H: Technical Reference Manual. <https://www.xcelenergy.com/staticfiles/xe-responsive/Company/Rates%20&%20Regulations/Regulatory%20Filings/CO-DSM/HE%20101_Attachment%20NCM-1,%202024-2026%20DSM%20BE%20Plan_without%20header.pdf>
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒 = ∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊ℎ = 𝐹𝐸𝑃𝐸𝐸 " ∗ (" 𝐹𝐸𝐼𝐸𝐸/𝐹𝐸𝐼𝐵𝐿 −1 ) "∗ EFLH ∗ " ∑_(0%)^(100%)▒(%𝐹𝐹 ∗𝑃𝐿𝑅)
CF / EFLH
∆𝑘𝑊 = ∆𝑘𝑊ℎ ∗ CF / EFLH
∑_(0%)^(100%)▒(%𝐹𝐹 ∗𝑃𝐿𝑅)

## C_HVAC_DX-DOAS
COMMERCIAL: Direct Expansion Dedicated Outdoor Air System (DX-DOAS)
Return to TOC
UPDATE STATUS
Introduced in Spring 2026 for the PY26 TRM.
MEASURE DETAILS
Description
Federal standards establish minimum efficiency requirements for direct expansion-dedicated outdoor air systems (DX-DOAS). New construction and major renovations are required to comply with the current Hawaii Energy Code, which is based on the 2018 International Energy Conservation Code (IECC) with state‑ and county‑level amendments. One compliance pathway for meeting mandatory efficiency requirements for new multiple-zone HVAC systems is the installation of a DOAS. The DOAS operates separately from the main HVAC system and supplies 100% of the outdoor air required to meet ventilation requirements. By handling all ventilation air, the DOAS reduces the load and runtime of the primary HVAC system, which operates only when additional heating or cooling beyond ventilation is required.
This measure applies to the installation of a DX‑DOAS with moisture removal efficiency that exceeds the current minimum federal efficiency standard. The energy and peak demand savings presented for this measure reflect only the incremental improvement in moisture removal efficiency relative to the code-minimum DX-DOAS baseline. Impacts on the primary HVAC system are not included in this measure. Savings associated with other DOAS features or related measures must be calculated separately.
Program Criteria
This measure applies to new construction or major renovations in which a new DX-DOAS unit is installed. The installed system must have an Integrated Seasonal Moisture Removal Efficiency 2 (ISMRE2) greater than the code-minimum ISMRE2 specified in the Code of Federal Regulations, 10 CFR 431.97(h), effective May 1, 2024.
The following types of DX-DOAS units are eligible:
| • | Air-cooled (AC), with or without ventilation energy recovery system (VERS)
| • | Air-source heat pump (ASHP), with or without VERS
| • | Water-cooled (WC), with or without VERS
| • | Water-source heat pump (WSHP), with or without VERS
Manufacturer datasheets for installed equipment and/or documentation of certification from the Air Conditioning, Heating, and Refrigeration Institute (AHRI) or Department of Energy Compliance Certification Management System (DOE CCMS) must be provided.
Unit of Measure
Per system.
Baseline Equipment
DX-DOAS meeting the minimum federal standard for ISMRE2 for the installed system type.
High Efficiency Equipment
DX-DOAS with an ISMRE2 rating greater than the minimum federal standard for the given system type.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  |  | Value | Unit | Source/Notes
ISMRE2Base |  |  | Integrated Seasonal Moisture Removal Efficiency 2 for the baseline system [1] |  |  |  | See Table 1 | lb of water per kWh | Code of Federal Regulations, 10 CFR 431.97(h), effective May 1, 2024.
ISMRE2EE |  |  | Integrated Seasonal Moisture Removal Efficiency 2 for the high efficiency system |  |  |  | Actual rated value | lb of water per kWh | The rated value of the new DOAS unit must be greater than the minimum federal standard for the given system type. Refer to AHRI database, DOE CCMS, or manufacturer datasheets for rated value.
MRCA |  |  | Moisture removal capacity at AHRI 920-2020 Standard Rating Condition A |  |  |  | Actual rated value | lb of water per hour | Condition A represents full load, hot/humid conditions. It corresponds to an entering air dry bulb temperature of 95°F and wet-bulb temperature of 78°F. Refer to AHRI database, DOE CCMS, or manufacturer datasheets for rated value.
CF |  |  | Coincidence factor for commercial ventilation |  |  |  | See Table 2 | - | AEG's PY19 analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period.
EFLH |  |  | Equivalent full load hours for commercial ventilation |  |  |  | See Table 2 | hrs | AEG's PY19 analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes and weather data.
EUL |  |  | Effective useful life of measure |  |  |  | 15 | yrs | Texas TRM, Version 13.0, Volume 4, PY26 TRM.
Notes:
1. ISMRE2 is a combined Moisture Removal Efficiency (MRE) rating of a DX-DOAS unit operating at four standard rating conditions using the equation: ISMRE2 = (MREA*0.14) + (MREB*0.34) + (MREC*0.39) + (MRED*0.13). Refer to this document for more information: ANSI/AHRI Standard 920-2026 (SI/I-P). Performance Rating of Direct Expansion-dedicated Outdoor Air System Units. URL: https://www.ahrinet.org/sites/default/files/ANSI.AHRI%20Standard%20920-2026%20SI.I-P.pdf.
Table 1: Minimum Federal Efficiency Standards for Direct Expansion-Dedicated Outdoor Air Systems
DX-DOAS Type | [6 empty] | Efficiency Level (ISMRE2)
Air-cooled (AC), without VERS | [6 empty] | 3.8
Air-cooled (AC), with VERS | [6 empty] | 5
Air-source heat pump (ASHP), without VERS | [6 empty] | 3.8
Air-source heat pump (ASHP), with VERS | [6 empty] | 5
Water-cooled (WC), without VERS | [6 empty] | 4.7
Water-cooled (WC), with VERS | [6 empty] | 5.1
Water-source heat pump (WSHP), without VERS | [6 empty] | 3.8
Water-source heat pump (WSHP), with VERS | [6 empty] | 4.6
Table 2: Equivalent Full Load Hours & Coincidence Factors for Direct Expansion-Dedicated Outdoor Air Systems
Building Type |  |  |  |  | EFLH | CF
Misc./Avg. Commercial |  |  |  |  | 5668 | 0.8
Cold Storage |  |  |  |  | NA | NA
Education |  |  |  |  | 2639 | 0.46
Grocery |  |  |  |  | 5840 | 1
Health |  |  |  |  | 5849 | 0.67
Hotel/Motel |  |  |  |  | 7837 | 0.94
Industrial |  |  |  |  | NA | NA
Office |  |  |  |  | 3675 | 0.63
Restaurant |  |  |  |  | 7300 | 1
Retail |  |  |  |  | 5278 | 0.86
Warehouse |  |  |  |  | NA | NA
Source: AEG's PY19 analysis of DOE's Commercial and Residential Hourly Load Profiles for all TMY3 Locations in the United States. The analysis was conducted using the commercial building fan end-use with Hawaii-specific prototypes, weather data, and peak demand period. ICF did not include the Cold Storage, Industrial, or Warehouse building types on this list because the DX-DOAS measure is unlikely to apply to those building types. Therefore, the EFLH and CF values for the "Misc./Avg. Commercial" building type in this DX-DOAS table differ from those in the General Commercial Fan table in the TRM's EFLH & CF sheet because they were calculated using the subset of building types applicable to the DX-DOAS measure. See ICF's PY26 Analysis File named "PY26 TRM - DX-DOAS - Analysis File" for more information.
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Select type of DX-DOAS unit.
Air-cooled (AC), without VERS
Select building type.
Retail
Enter rated ISMRE2EE value from equipment datasheets, AHRI, or DOE CCMS.
5.6
Enter rated MRCA value from equipment datasheets, AHRI, or DOE CCMS.
81
Measure Name |  |  |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Air-cooled (AC), without VERS |  |  |  |  | 5.892 |  | 36162.24 |  |  | 542433.6
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - DX-DOAS - Analysis File."
• | AEG's PY19 analysis file named "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays."
• | Air Conditioning, Heating, and Refrigeration Institute (AHRI). AHRI Certification Directory. URL: https://www.ahridirectory.org/. Product Function = "Ventilation and Air Movement" and then "Dedicated Outdoor Air Systems."
• | ANSI/AHRI Standard 920-2026 (SI/I-P). Performance Rating of Direct Expansion-dedicated Outdoor Air System Units. URL: https://www.ahrinet.org/sites/default/files/ANSI.AHRI%20Standard%20920-2026%20SI.I-P.pdf.
• | Appendix B to Subpart F of Part 431, Title 10. Uniform Test Method For Measuring the Energy Consumption of Direct Expansion-Dedicated Outdoor Air Systems. URL: https://www.ecfr.gov/current/title-10/part-431/appendix-Appendix B to Subpart F of Part 431.
• | Code of Federal Regulations. 10 CFR 431.97(h). Table 17 to Paragraph (h)—Minimum Efficiency Standards for Direct Expansion-Dedicated Outdoor Air Systems. URL: https://www.ecfr.gov/current/title-10/part-431/section-431.97#p-431.97(h).
• | Commercial Checklist. 2018 IECC with State Amendments. Hawaii State Energy Office. URL: https://energy.hawaii.gov/wp-content/uploads/2025/05/Checklist-2018-IECC_State_Commercial_2025-05-12.pdf.
• | Hawaii Energy Code 2018. UpCodes. Section C406 Additional Efficiency Packages. C406.1 Requirements. URL: https://up.codes/viewer/hawaii/iecc-2018/chapter/CE_4/ce-commercial-energy-efficiency#C406.1.
• | NREL. U.S. Department of Energy Commercial Reference Building Models of the National Building Stock. Technical Report. NREL/TP-5500-46861. February 2011. URL: https://docs.nlr.gov/docs/fy11osti/46861.pdf.
• | Public Utility Commission of Texas. Texas Technical Reference Manual. Version 13.0. Volume 4: Measurement and Verification Protocols. Program Year 2026. URL: https://texasefficiency.com/wp-content/uploads/2025/11/trm13v4.pdf.
• | U.S. Department of Energy. Compliance Certification Management System (CCMS). URL: https://www.regulations.doe.gov/ccms. Click "Compliance Certification Database." Choose Product Group = "Air Conditioners and Heat Pumps - Dehumidifying Direct-Expansion Dedicated Outdoor Air Systems."
• | U.S. Department of Energy. Commercial and Residential Hourly Load Profiles for all TMY3 Locations in the United States. DOI 10.25984/1788456. URL: https://data.openei.org/submissions/153.
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
∆𝑘𝑊ℎ=(1/〖𝐼𝑆𝑀𝑅𝐸2〗_𝐵𝑎𝑠𝑒 −1/〖𝐼𝑆𝑀𝑅𝐸2〗_𝐸𝐸 )∗〖𝑀𝑅𝐶〗_𝐴∗𝐸𝐹𝐿𝐻
∆𝑘𝑊=(1/〖𝐼𝑆𝑀𝑅𝐸2〗_𝐵𝑎𝑠𝑒 −1/〖𝐼𝑆𝑀𝑅𝐸2〗_𝐸𝐸 )∗〖𝑀𝑅𝐶〗_𝐴∗𝐶𝐹

## C_Light_General
COMMERCIAL: Interior Lighting
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. The update consisted of adding a sunset date of June 30, 2030, for "early replacement" measures affected by the linear fluorescent lighting ban that took effect on January 1, 2026. In addition, the update removed several "replace on burnout" fluorescent lighting measures that reached their sunset date on December 31, 2025.
MEASURE DETAILS
Description
Hawai‘i Energy offers several types of prescriptive lighting measures for Commercial buildings through the Business Energy Efficiency Measures (BEEM) and Business Hard to Reach (BHTR) programs. The measures related to replacing lamps and fixtures with LED alternatives of comparable brightness (lumens) are covered here.
Program Criteria
This measure is applicable to both the BEEM and BHTR programs.
The replacement LED lamp must be on the Consortium for Energy Efficiency's (CEE's) most recent Commercial Lighting Qualifying Products List, have an ENERGY STAR label, or be on DesignLights Consortium's Qualified Product List (DLC QPL).
For direct install projects, the replacement lamps must be of equivalent brightness (measured in lumens) as the baseline lamps. In the case of the delamping measure, the replacement lamp (with an added reflector as needed) must be of sufficient brightness to meet the requirements of the space. For delamping, the lamp and lamp holder ("tombstone") must be permanently removed.
Unit of Measure
One lamp.
Baseline Equipment
A few lighting measures require a dual baseline approach to account for early replacement and expected changes in state and federal standards.
For BEEM, lighting is delivered through a midstream approach; the most applicable baseline is replace on burnout (ROB). For BHTR, lighting is delivered through the Small Business Direct Install Lighting (SBDIL) program; since lighting is directly installed, the most applicable baseline is early replacement.
For ROB projects, the baseline must comply with the state and federal standards that are in place at the time of the replacement and any known future state and federal requirements expected to be in place during the equipment's lifetime.
All early replacement projects (only applicable to BHTR/SBDIL linear lamps) require a dual baseline. The first baseline is the pre-existing equipment, which has been estimated as a blend of 30% T12 and 70% T8 fluorescent lamps. The pre-existing equipment is assumed to have a remaining useful life (RUL) of one-third of the Effective Useful Life (EUL) of the pre-existing fluorescent lamps. The second baseline must comply with any known future state and federal requirements expected to be in place during the equipment's lifetime. Only lamps that are in working order at the time of the replacement qualify for early replacement. If the pre-existing lamps cannot be verified to be in working order, an ROB baseline must be used.
High Efficiency Equipment
For lamp replacement projects, the high efficiency case is an LED lamp that meets program criteria. As an alternative to more traditional LED bulbs or tubes, LED retrofit kit engines qualify as applicable LED replacement lighting, as long as the LED retrofit kit engines have appropriate form factors compared to the baseline lighting. For delamping projects, the high efficiency case is no lamp.
Linear tubes installed through the early replacement (SBDIL) portion of the measure have a sunset date of June 30, 2030, which is the end of PY29. Linear tubes and pin-based fluorescent lighting installed as replace on burnout measures already reached their sunset date on December 31, 2025. The extra four years for the SBDIL portion of the measure allows for early replacement of pre-existing linear fluorescent tubes, which have an RUL of four years for "average" commercial buildings (see Table 8 below).
ALGORITHMS
First Baseline Peak Demand Reduction, kW
(1)
Second Baseline Peak Demand Reduction, kW
(2)
First Baseline Annual Energy Savings, kWh/yr
(3)
Second Baseline Annual Energy Savings, kWh/yr
(4)
Lifetime Energy Savings, kWh (Dual Baseline, ROB)
(5)
Lifetime Energy Savings, kWh (Dual Baseline, Early Replacement)
(6)
Lifetime Energy Savings, kWh (Single Baseline)
(7)
Remaining Useful Life
(8)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description | [8 empty] | Value |  |  | Unit |  | Source/Notes
kWbase,1 |  | Wattage of the first baseline lamp | [8 empty] | See Table 1 |  |  | kW |  | ROB: Current state/federal standard Early replacement: Pre-existing
kWbase,2 |  | Wattage of the second baseline lamp | [8 empty] | See Table 1 |  |  | kW |  | ROB: Future state/federal standard Early replacement: Current/future state/federal standard
kWEE |  | Wattage of the proposed efficient lamp | [8 empty] | See Table 2 |  |  | kW |  | DLC QPL and other benchmarking performed in 2018
ISR |  | Lifetime in-service rate | [8 empty] | 0.98 |  |  | - |  | AEG's Fall 2018 Benchmarking resulted in ISR = 0.98 for most lighting measures, except for the delamping measure and early replacement through BHTR, which have an ISR = 1
CF |  | Peak demand coincidence factor | [8 empty] | See Table 3 |  |  | - |  | AEG's analysis of DOE's OpenEI load shapes using Hawaii-specific prototypes, weather data, and peak demand period, adjusted to specific lighting types
IEC,D |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting | [8 empty] | See Table 4 |  |  | - |  | DEER20201 interactive effect factors for San Diego, adjusted to Hawaii's weather zone using LBNL simulation results2
IEC,E |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting | [8 empty] | See Table 4 |  |  | - |  | DEER20201 interactive effect factors for San Diego, adjusted to Hawaii's weather zone using LBNL simulation results2
HOUyear |  | Average hours of use per year | [8 empty] | See Table 5 |  |  | hr/yr |  | BEEM: DEER20201 hours of use for San Diego (CA's southern-most latitude); no occupancy sensor BHTR/SBDIL: Custom hours
PF |  | Persistence factor | [8 empty] | 1 |  |  | - |  | Footnote 3
EUL1st |  | Effective useful life of first baseline lamp | [8 empty] | See Table 6 |  |  | yrs |  | Calculated by dividing rated lamp life4 by HOUyear and setting upper bound EUL = 25 yr and lower bound EUL = 1 yr
EULEE |  | Effective useful life of efficient lamp | [8 empty] | See Table 7 |  |  | yrs |  | Calculated by dividing rated lamp life4 by HOUyear and setting upper bound EUL = 25 yr and lower bound EUL = 1 yr
RUL |  | Remaining useful life of pre-existing lamp | [8 empty] | See Table 8 |  |  | yrs |  | See Equation 8
EULpre-existing |  | Effective useful life of pre-existing lamp | [8 empty] | See Table 6 |  |  | yrs |  | Assumes EUL of fluorescent T12/T8 blend is equal to EUL of Fluorescent lamps listed in Table 6
1 The DEER interactive effect factors and hours of use were developed for DEER2016 and they are still applicable to DEER2020.
2 "Lighting/HVAC Interactions and Their Effects on Annual and Peak HVAC Requirements in Commercial Buildings," Sezgen, A. O., Y. J. Huang, Lawrence Berkeley Laboratory, ACEEE Summer Study, 1994.
3 Use value of PF=1 until more data is available on PF of LEDs relative to baseline lighting.
4 Sources of rated lamp life include DEER, DLC, and other benchmarking.
Table 1. Baseline Wattages, kWbase,1 and kWbase,2
Lighting Type |  |  | Baseline #1 | [12 empty] | Baseline #2 |  |  |  | Base-line |  | Source
|  |  | Pre-Existing (SBDIL only) | [6 empty] | Meets Current Standard (Replace on Burnout) | [5 empty] | Meets Current/Future Standard
|  |  | Lamp Type |  |  |  |  | kW |  | Lamp Type |  |  |  | kW |  | Lamp Type |  |  | kW
LED Exit Sign |  |  | - |  |  |  |  | - |  | Incandescent sign, various types ranging from 1x5W to 2x50W |  |  |  | 0.038 |  | - |  |  | - | Single |  | Appendix B SFW, average across incandescent exit signs
LED Linear (T8), 8' |  |  | 8', various ballast types, 70% F96T8 & 30% F96T12 |  |  |  |  | 0.059 |  | 8' F96T8, electronic ballast (delamping only) |  |  |  | 0.057 |  | LED Linear (T8), 8' (Type A, B, or C installation) |  |  | See Table 2 | Dual |  | Appendix B SFW, per lamp averages across fixture types; LED wattages are from DLC QPL and other benchmarking performed in 2018
LED Linear (T8), 4' |  |  | 4', various ballast types, 70% F32T8 & 30% F40T12 |  |  |  |  | 0.036 |  | 4' F32T8, electronic ballast (delamping only) |  |  |  | 0.031 |  | LED Linear (T8), 4' (Type A, B, or C installation) |  |  | See Table 2 | Dual |  | Appendix B SFW, per lamp averages across fixture types; LED wattages are from DLC QPL and other benchmarking performed in 2018
LED Linear (T8), 3' |  |  | 3', various ballast types, 70% F25T8 & 30% F30T12 |  |  |  |  | 0.027 |  | 3' F25T8, electronic ballast (delamping only) |  |  |  | 0.023 |  | LED Linear (T8), 3' (Type A, B, or C installation) |  |  | See Table 2 | Dual |  | Appendix B SFW, per lamp averages across fixture types; LED wattages are from DLC QPL and other benchmarking performed in 2018
LED Linear (T8), 2' |  |  | 2', various ballast types, 70% F17T8 & 30% F20T12 |  |  |  |  | 0.019 |  | 2' F17T8, electronic ballast (delamping only) |  |  |  | 0.016 |  | LED Linear (T8), 2' (Type A, B, or C installation) |  |  | See Table 2 | Dual |  | Appendix B SFW, per lamp averages across fixture types; LED wattages are from DLC QPL and other benchmarking performed in 2018
LED: HID replacement, <35W |  |  | - |  |  |  |  | - |  | HID 50W-100W Baseline: 64W, 86W, 128W |  |  |  | 0.093 |  | - |  |  | - | Single |  | Fixture wattage from benchmarking; no change from PY18 TRM
LED: HID replacement, 35W-149W |  |  | - |  |  |  |  | - |  | HID 150W-250W Baseline: 188W, 240W, 295W |  |  |  | 0.241 |  | - |  |  | - | Single |  | Fixture wattage from benchmarking; no change from PY18 TRM
LED: HID replacement, 150W-220W |  |  | - |  |  |  |  | - |  | HID 310W-600W Baseline: 365W, 457W, 665W |  |  |  | 0.496 |  | - |  |  | - | Single |  | Fixture wattage from benchmarking; no change from PY18 TRM
LED: HID replacement, >220W |  |  | - |  |  |  |  | - |  | HID 750W-1000W Baseline: 840W, 1100W |  |  |  | 0.97 |  | - |  |  | - | Single |  | Fixture wattage from benchmarking; no change from PY18 TRM
Table 2. High Efficiency Wattages, kWEE | [8 empty] | Table 3. Coincidence Factors, CF (Applicable to Counties of Oahu, Maui, and Hawaii)
Lighting Type |  |  | Linear LED, kW |  |  | Other LED, kW5
|  |  | Type A1 |  | Type B2 and Type C3 |  |  |  | Building Type |  |  | Exit Sign |  |  | Omni-Directional, Directional, and Decorative |  | High Bay |  |  | Linear, U-Bend, Troffer
LED Exit Sign |  |  | - |  | - | 0.005 |  |  | Avg. Commercial |  |  | 1 |  |  | Sunset |  | 0.53 |  |  | 0.34
LED Linear (T8), 8' |  |  | 0.0415 |  | 0.039 | - |  |  | Cold Storage |  |  | 1 |  |  | Sunset |  | 0.2 |  |  | 0.2
LED Linear (T8), 4' |  |  | 0.0184 |  | 0.0159 | - |  |  | Education |  |  | 1 |  |  | Sunset |  | 0.4 |  |  | 0.32
LED Linear (T8), 3' |  |  | 0.016 |  | 0.0135 | - |  |  | Grocery |  |  | 1 |  |  | Sunset |  | 0.78 |  |  | 0.68
LED Linear (T8), 2' |  |  | 0.0128 |  | 0.0103 | - |  |  | Health |  |  | 1 |  |  | Sunset |  | 0.72 |  |  | 0.63
LED Linear (T5), 4' |  |  | Reached sunset date | [5 empty] | Hotel/Motel |  |  | 1 |  |  | Sunset |  | 0.96 |  |  | 0.23
LED Linear (T5 HO), 4' |  |  | Reached sunset date | [5 empty] | Industrial |  |  | 1 |  |  | Sunset |  | 0.58 |  |  | 0.59
LED Omni-Direct. lamp, Screw Base4 |  |  | Reached sunset date | [5 empty] | Office |  |  | 1 |  |  | Sunset |  | 0.31 |  |  | 0.25
LED Omni-Direct. lamp, Pin Base4 |  |  | Reached sunset date | [5 empty] | Restaurant |  |  | 1 |  |  | Sunset |  | 0.5 |  |  | 0.49
LED MR16 lamp4 |  |  | Reached sunset date | [5 empty] | Retail |  |  | 1 |  |  | Sunset |  | 0.54 |  |  | 0.5
LED PAR20 lamp4 |  |  | Reached sunset date | [5 empty] | Warehouse |  |  | 1 |  |  | Sunset |  | 0.1 |  |  | 0.08
LED PAR30 lamp4 |  |  | Reached sunset date | [5 empty] | Notes:
LED PAR38 lamp4 |  |  | Reached sunset date | [5 empty] | a. The CF values were derived using a three step process:
LED Decorative Candelabra 25W eq. |  |  | Reached sunset date | [6 empty] | 1) AEG analysis of DOE's OpenEI general lighting load shapes simulated with Hawaii-specific prototypes, weather data, and peak demand period to determine i) unadjusted CF values for general lighting during Hawaii's peak demand period of 5-9 pm on non-holiday weekdays, and ii) unadjusted EFLH values for general lighting (= annual lighting energy use in kWh divided by maximum lighting demand in kW).
LED Decorative Candelabra 40W eq. |  |  | Reached sunset date | [6 empty] | 2) Mapping of OpenEI's and DEER's building types to Hawai‘i Energy's building types listed above;
LED Decorative Med Base 40W eq. |  |  | Reached sunset date | [6 empty] | 3) Adjustment of the OpenEI CF values to specific lighting types (bulbs, highbay, linear lamps) using DEER's annual HOUs for San Diego. The adjustment equation is CFOpenEI*(HOUSD/EFLHOpenEI).
LED Decorative Med Base 60W eq. |  |  | Reached sunset date | [5 empty] | b. San Diego is a good proxy for Hawaii for lighting usage. The OpenEI prototypes yield the same energy, demand, EFLH, and CF factors for San Diego, Honolulu, Kahului, and Keahole-Kona weather stations. (Therefore, the same results are applicable to all Hawaiian counties.)
LED Troffer, 1 ft x 4 ft |  |  | Reached sunset date
LED Troffer, 2 ft x 2 ft |  |  | Reached sunset date | [5 empty] | Table 4. Interactive Effects Factors, IEC,D and IEC,E (Applicable to Counties of Oahu, Maui, and Hawaii)
LED Troffer, 2 ft x 4 ft |  |  | Reached sunset date
(2) LED 2' linear replace (2) Fl. U-bend |  |  | Reached sunset date | [5 empty] | Building Type |  |  | Omni-Directional, Directional, and Decorative |  |  |  |  | High Bay, Linear, U-Bend, Troffer
(1) LED U-bend replace (1) Fl. U-bend |  |  | Reached sunset date
(2) LED U-bend replace (2) Fl. U-bend |  |  | Reached sunset date | [8 empty] | IEC,D |  |  | IEC,E |  | IEC,D |  |  | IEC,E
LED: HID replace, <35W |  |  | - |  | - | 0.028 |  |  | Avg. Commercial |  |  | Sunset |  |  | Sunset |  | 1.26 |  |  | 1.13
LED: HID replace, 35W-149W |  |  | - |  | - | 0.078 |  |  | Cold Storage |  |  | Sunset |  |  | Sunset |  | 1.25 |  |  | 1.62
LED: HID replace, 150W-220W |  |  | - |  | - | 0.17 |  |  | Education |  |  | Sunset |  |  | Sunset |  | 1.31 |  |  | 1.25
LED: HID replace, >220W |  |  | - |  | - | 0.27 |  |  | Grocery |  |  | Sunset |  |  | Sunset |  | 1.09 |  |  | 1.14
1 Type A installation: Ballast left in place, reduced savings due to losses. | [8 empty] | Health |  |  | Sunset |  |  | Sunset |  | 1.24 |  |  | 1.15
2 Type B installation: Bypassing fluorescent ballast and utilizing internal LED driver. | [8 empty] | Hotel/Motel |  |  | Sunset |  |  | Sunset |  | 1.27 |  |  | 1.36
3 Type C installation: Removing fluorescent ballast and utilizing an external driver; more efficient than the Type B internal driver. However, this also consumes a little more power. | [8 empty] | Industrial |  |  | Sunset |  |  | Sunset |  | 1.2 |  |  | 1.13
Therefore, this program assumes Types B & C energy and demand savings to be equivalent. However, a Type C installation is preferred for longevity due to use of an external LED driver and complete removal of the fluorescent ballast. | [8 empty] | Office |  |  | Sunset |  |  | Sunset |  | 1.07 |  |  | 1.26
4 Wattages represent a blend of dimmable and non-dimmable equipment. See C_Light_Dimmable(Nonlinear LED) for details. | [8 empty] | Restaurant |  |  | Sunset |  |  | Sunset |  | 1.24 |  |  | 1.28
5 Wattages are from DLC QPL and other benchmarking performed in 2018. | [8 empty] | Retail |  |  | Sunset |  |  | Sunset |  | 1.36 |  |  | 1.15
[9 empty] | Warehouse |  |  | Sunset |  |  | Sunset |  | 1.16 |  |  | 1.01
Notes:
a. The IE values were derived using a four step process:
1) Tabulation of DEER's IE factors for San Diego (IECC CZ 3B);
2) Tabulation of IE factors from LBNL 1994 study for IECC CZ 3B and IECC CZ 1A;
3) Mapping of DEER and LBNL building types to Hawai‘i Energy's building types listed above;
4) Adjustment of the DEER IE factors for CZ 3B using ratio of LBNL factors for CZ 1A and CZ 3B to determine IE factors for Hawaii (CZ 1A). The equation is: IEHawaii = IEDEER, 3B*(IELBNL,1A/IELBNL,3B).
b. Assume no interactive effects for exit signs due to lack of representative data.
Table 5. Annual Hours of Use, HOUyear
Building Type |  | Exit Sign |  | Omni-Directional, Directional, and Decorative |  |  | High Bay |  |  | Linear, U-Tube, Troffer
Avg. Commercial |  | 8760 |  | Sunset |  |  | 3047 |  |  | 1963
Cold Storage |  | 8760 |  | Sunset |  |  | 4820 |  |  | 4700
Education |  | 8760 |  | Sunset |  |  | 2176 |  |  | 1702
Grocery |  | 8760 |  | Sunset |  |  | 5450 |  |  | 4770
Health |  | 8760 |  | Sunset |  |  | 5870 |  |  | 5100
Hotel/Motel |  | 8760 |  | Sunset |  |  | 4775 |  |  | 1130
Industrial |  | 8760 |  | Sunset |  |  | 2860 |  |  | 2305
Office |  | 8760 |  | Sunset |  |  | 2480 |  |  | 1980
Restaurant |  | 8760 |  | Sunset |  |  | 3610 |  |  | 3500
Retail |  | 8760 |  | Sunset |  |  | 3983 |  |  | 3690
Warehouse |  | 8760 |  | Sunset |  |  | 2245 |  |  | 1970
Source: DEER2020 hours of use for San Diego IOU; no occupancy sensor. HOU were originally developed for DEER2016.
Table 6. Effective Useful Life of Baseline Lamp (Dual Baseline, ROB), EUL1st
Building Type |  | Incandescent Exit Sign |  |  | Fluorescent Linear, U-bend, Troffer |  |  | CFL |  |  | HID
Avg. Commercial |  | 1 |  |  | 12 |  |  | Sunset |  |  | 23
Cold Storage |  | 1 |  |  | 5 |  |  | Sunset |  |  | 15
Education |  | 1 |  |  | 14 |  |  | Sunset |  |  | 25
Grocery |  | 1 |  |  | 5 |  |  | Sunset |  |  | 13
Health |  | 1 |  |  | 5 |  |  | Sunset |  |  | 12
Hotel/Motel |  | 1 |  |  | 21 |  |  | Sunset |  |  | 15
Industrial |  | 1 |  |  | 10 |  |  | Sunset |  |  | 24
Office |  | 1 |  |  | 12 |  |  | Sunset |  |  | 25
Restaurant |  | 1 |  |  | 7 |  |  | Sunset |  |  | 19
Retail |  | 1 |  |  | 7 |  |  | Sunset |  |  | 18
Warehouse |  | 1 |  |  | 12 |  |  | Sunset |  |  | 25
Source: Calculated by dividing rated lamp life by HOUyear and setting upper bound EUL = 25 yr and lower bound EUL = 1 yr. Sources of rated lamp life include DEER, DLC, Lighting Research Center, and other benchmarking.
Table 7. Effective Useful Life of Efficient Lamp, EULEE | [12 empty] | Table 8. Remaining Useful Life of Pre-Existing Lamp, RUL
Building Type |  | LED Exit Sign |  | LED Omni-Directional, Directional, and Decorative |  |  | LED High Bay |  |  | LED Linear, U-Tube, Troffer |  |  | Building Type |  |  | Fluorescent Linear, U-bend, Troffer
Avg. Commercial |  | 18 |  | Sunset |  |  | 16 |  |  | 25 |  |  | Avg. Commercial |  |  | 4
Cold Storage |  | 18 |  | Sunset |  |  | 10 |  |  | 11 |  |  | Cold Storage |  |  | 2
Education |  | 18 |  | Sunset |  |  | 23 |  |  | 25 |  |  | Education |  |  | 5
Grocery |  | 18 |  | Sunset |  |  | 9 |  |  | 10 |  |  | Grocery |  |  | 2
Health |  | 18 |  | Sunset |  |  | 9 |  |  | 10 |  |  | Health |  |  | 2
Hotel/Motel |  | 18 |  | Sunset |  |  | 10 |  |  | 25 |  |  | Hotel/Motel |  |  | 7
Industrial |  | 18 |  | Sunset |  |  | 17 |  |  | 22 |  |  | Industrial |  |  | 3
Office |  | 18 |  | Sunset |  |  | 20 |  |  | 25 |  |  | Office |  |  | 4
Restaurant |  | 18 |  | Sunset |  |  | 14 |  |  | 14 |  |  | Restaurant |  |  | 2
Retail |  | 18 |  | Sunset |  |  | 13 |  |  | 14 |  |  | Retail |  |  | 2
Warehouse |  | 18 |  | Sunset |  |  | 22 |  |  | 25 |  |  | Warehouse |  |  | 4
Source: Calculated by dividing rated lamp life by HOUyear and setting upper bound EUL = 25 yr and lower bound EUL = 1 yr. Sources of rated lamp life include DEER, DLC, and other benchmarking. | [12 empty] | Note: Only applies to SBDIL and Type A linear lamp replacements. Assumes EUL of pre-existing lamp divided by 3.
SAVINGS
Table 9. Menu of Deemed Savings Tables (click to navigate to correct savings tables)
| Lighting Type | [5 empty] | Savings Table Pointer
| Delamping | [5 empty] | First Year Savings |  |  |  |  | Lifetime Savings
| Exit Signs | [5 empty] | First Year Savings |  |  |  |  | Lifetime Savings
| T8 Linear (Early Replacement)1 | [5 empty] | First Year Savings |  |  |  |  | Lifetime Savings
| LED HID Replacement | [5 empty] | First Year Savings |  |  |  |  | Lifetime Savings
1 First year and lifetime kWh calculations for SBDIL early replacement use custom HOU, so no deemed savings are provided.
First Year Savings: Delamping
Table 10. Calculated First Year Unit Savings: Delamping (With or Without Reflector)
|  |  | Peak Demand Savings (kW) | [12 empty] | Annual Energy Savings (kWh/year)
Building Type |  |  | 2' Lamp |  |  | 3' Lamp |  |  |  | 4' Lamp |  |  | 8' Lamp |  |  | 2' Lamp |  | 3' Lamp |  |  | 4' Lamp |  | 8' Lamp
Avg. Commercial |  |  | 0.007 |  |  | 0.01 |  |  |  | 0.013 |  |  | 0.024 |  |  | 35.49 |  | 51.02 |  |  | 68.76 |  | 126.44
Cold Storage |  |  | 0.004 |  |  | 0.006 |  |  |  | 0.008 |  |  | 0.014 |  |  | 121.82 |  | 175.12 |  |  | 236.03 |  | 434
Education |  |  | 0.007 |  |  | 0.01 |  |  |  | 0.013 |  |  | 0.024 |  |  | 34.04 |  | 48.93 |  |  | 65.95 |  | 121.27
Grocery |  |  | 0.012 |  |  | 0.017 |  |  |  | 0.023 |  |  | 0.042 |  |  | 87 |  | 125.07 |  |  | 168.57 |  | 309.95
Health |  |  | 0.012 |  |  | 0.018 |  |  |  | 0.024 |  |  | 0.045 |  |  | 93.84 |  | 134.9 |  |  | 181.82 |  | 334.31
Hotel/Motel |  |  | 0.005 |  |  | 0.007 |  |  |  | 0.009 |  |  | 0.017 |  |  | 24.59 |  | 35.35 |  |  | 47.64 |  | 87.6
Industrial |  |  | 0.011 |  |  | 0.016 |  |  |  | 0.022 |  |  | 0.04 |  |  | 41.67 |  | 59.91 |  |  | 80.74 |  | 148.47
Office |  |  | 0.004 |  |  | 0.006 |  |  |  | 0.008 |  |  | 0.015 |  |  | 39.92 |  | 57.38 |  |  | 77.34 |  | 142.2
Restaurant |  |  | 0.01 |  |  | 0.014 |  |  |  | 0.019 |  |  | 0.035 |  |  | 71.68 |  | 103.04 |  |  | 138.88 |  | 255.36
Retail |  |  | 0.011 |  |  | 0.016 |  |  |  | 0.021 |  |  | 0.039 |  |  | 67.9 |  | 97.6 |  |  | 131.55 |  | 241.88
Warehouse |  |  | 0.001 |  |  | 0.002 |  |  |  | 0.003 |  |  | 0.005 |  |  | 31.84 |  | 45.76 |  |  | 61.68 |  | 113.41
Note: Assumes the baseline is a fluorescent T8 lamp with electronic ballast that meets current federal standard.
Lifetime Savings: Delamping
Table 11. Calculated Lifetime Unit Savings: Delamping (With or Without Reflector)
Lifetime Energy Savings (kWh)
Building Type |  |  | 2' Lamp |  |  | 3' Lamp |  |  |  | 4' Lamp |  |  | 8' Lamp
Avg. Commercial |  |  | 887.25 |  |  | 1275.5 |  |  |  | 1719 |  |  | 3161
Cold Storage |  |  | 1340.02 |  |  | 1926.32 |  |  |  | 2596.33 |  |  | 4774
Education |  |  | 851 |  |  | 1223.25 |  |  |  | 1648.75 |  |  | 3031.75
Grocery |  |  | 870 |  |  | 1250.7 |  |  |  | 1685.7 |  |  | 3099.5
Health |  |  | 938.4 |  |  | 1349 |  |  |  | 1818.2 |  |  | 3343.1
Hotel/Motel |  |  | 614.75 |  |  | 883.75 |  |  |  | 1191 |  |  | 2190
Industrial |  |  | 916.74 |  |  | 1318.02 |  |  |  | 1776.28 |  |  | 3266.34
Office |  |  | 998 |  |  | 1434.5 |  |  |  | 1933.5 |  |  | 3555
Restaurant |  |  | 1003.52 |  |  | 1442.56 |  |  |  | 1944.32 |  |  | 3575.04
Retail |  |  | 950.6 |  |  | 1366.4 |  |  |  | 1841.7 |  |  | 3386.32
Warehouse |  |  | 796 |  |  | 1144 |  |  |  | 1542 |  |  | 2835.25
Note: Assumes the baseline is a fluorescent T8 lamp with electronic ballast that meets current federal standard.
First Year Savings: Exit Signs, Replace on Burnout
Table 12. Calculated First Year Unit Savings: LED Exit Signs (8760 HOURS)
Building Type |  |  | Peak Demand Savings (kW) | [9 empty] | Annual Energy Savings (kWh/year)
All |  |  | 0.032 | [9 empty] | 283.3
Lifetime Savings: Exit Signs, Replace on Burnout
Table 13. Calculated Lifetime Unit Savings: LED Exit Signs (8760 HOURS)
Building Type |  |  | Lifetime Energy Savings (kWh)
All |  |  | 5099.4
First Year Savings: T8 Linear LED Lamps, Early Replacement, SBDIL Only (Only Applicable through June 30, 2030)
Table 14. Calculated First Year Unit Savings: T8 Linear LED Lamps, Demand Savings (Pre-Existing baseline, SBDIL only)
First Baseline Peak Demand Savings (kW)
Building Type |  |  | 2' Type A |  |  | 2' Type B/C |  |  |  | 3' Type A |  |  | 3' Type B/C |  |  | 4' Type A |  | 4' Type B/C |  |  | 8' Type A |  | 8' Type B/C
Avg. Commercial |  |  | 0.003 |  |  | 0.004 |  |  |  | 0.005 |  |  | 0.006 |  |  | 0.008 |  | 0.009 |  |  | 0.007 |  | 0.009
Cold Storage |  |  | 0.002 |  |  | 0.002 |  |  |  | 0.003 |  |  | 0.003 |  |  | 0.004 |  | 0.005 |  |  | 0.004 |  | 0.005
Education |  |  | 0.003 |  |  | 0.004 |  |  |  | 0.005 |  |  | 0.006 |  |  | 0.007 |  | 0.008 |  |  | 0.007 |  | 0.008
Grocery |  |  | 0.005 |  |  | 0.006 |  |  |  | 0.008 |  |  | 0.01 |  |  | 0.013 |  | 0.015 |  |  | 0.013 |  | 0.015
Health |  |  | 0.005 |  |  | 0.007 |  |  |  | 0.009 |  |  | 0.011 |  |  | 0.014 |  | 0.016 |  |  | 0.014 |  | 0.016
Hotel/Motel |  |  | 0.002 |  |  | 0.003 |  |  |  | 0.003 |  |  | 0.004 |  |  | 0.005 |  | 0.006 |  |  | 0.005 |  | 0.006
Industrial |  |  | 0.004 |  |  | 0.006 |  |  |  | 0.008 |  |  | 0.01 |  |  | 0.012 |  | 0.014 |  |  | 0.012 |  | 0.014
Office |  |  | 0.002 |  |  | 0.002 |  |  |  | 0.003 |  |  | 0.004 |  |  | 0.005 |  | 0.005 |  |  | 0.005 |  | 0.005
Restaurant |  |  | 0.004 |  |  | 0.005 |  |  |  | 0.007 |  |  | 0.008 |  |  | 0.011 |  | 0.012 |  |  | 0.011 |  | 0.012
Retail |  |  | 0.004 |  |  | 0.006 |  |  |  | 0.007 |  |  | 0.009 |  |  | 0.012 |  | 0.014 |  |  | 0.012 |  | 0.014
Warehouse |  |  | 0.001 |  |  | 0.001 |  |  |  | 0.001 |  |  | 0.001 |  |  | 0.002 |  | 0.002 |  |  | 0.002 |  | 0.002
Note: 2nd baseline savings are zero because the baseline becomes an LED after the fluorescent lighting ban.
Note: First Year Energy Savings for SBDIL are to be calculated with custom HOU using Equation (3) for the first (Pre-Existing) baseline period. See the "C_Light_Energy Advantage" sheet for more detail. The second baseline savings are zero because the baseline becomes an LED after the fluorescent lighting ban.
Lifetime Savings: T8 Linear LED Lamps, Early Replacement, SBDIL Only (Only Applicable through June 30, 2030)
Note: Lifetime Energy Savings for SBDIL are to be calculated with custom HOU using Equation (6). See the "C_Light_Energy Advantage" sheet for more detail. The second baseline savings are zero because the baseline becomes an LED after the fluorescent lighting ban.
First Year Savings: HID Replacement, Replace on Burnout, Single Baseline
Table 15. Calculated First Year Unit Savings: HID Replacement
|  |  | Peak Demand Savings (kW) | [12 empty] | Annual Energy Savings (kWh/year)
Building Type |  |  | <35W |  |  | 35W-149W |  |  |  | 150W-220W |  |  | >220W |  |  | <35W |  | 35W-149W |  |  | 150W-220W |  | >220W
Avg. Commercial |  |  | 0.043 |  |  | 0.107 |  |  |  | 0.213 |  |  | 0.458 |  |  | 219.33 |  | 550 |  |  | 1100 |  | 2361.97
Cold Storage |  |  | 0.016 |  |  | 0.04 |  |  |  | 0.08 |  |  | 0.172 |  |  | 497.4 |  | 1247.31 |  |  | 2494.63 |  | 5356.56
Education |  |  | 0.033 |  |  | 0.084 |  |  |  | 0.167 |  |  | 0.359 |  |  | 173.26 |  | 434.49 |  |  | 868.99 |  | 1865.92
Grocery |  |  | 0.054 |  |  | 0.136 |  |  |  | 0.272 |  |  | 0.583 |  |  | 395.77 |  | 992.46 |  |  | 1984.93 |  | 4262.12
Health |  |  | 0.057 |  |  | 0.143 |  |  |  | 0.285 |  |  | 0.612 |  |  | 430.01 |  | 1078.32 |  |  | 2156.65 |  | 4630.84
Hotel/Motel |  |  | 0.078 |  |  | 0.195 |  |  |  | 0.39 |  |  | 0.836 |  |  | 413.67 |  | 1037.35 |  |  | 2074.7 |  | 4454.88
Industrial |  |  | 0.044 |  |  | 0.111 |  |  |  | 0.222 |  |  | 0.477 |  |  | 205.87 |  | 516.25 |  |  | 1032.5 |  | 2217.01
Office |  |  | 0.021 |  |  | 0.053 |  |  |  | 0.106 |  |  | 0.228 |  |  | 199.05 |  | 499.16 |  |  | 998.31 |  | 2143.61
Restaurant |  |  | 0.039 |  |  | 0.099 |  |  |  | 0.198 |  |  | 0.425 |  |  | 294.34 |  | 738.13 |  |  | 1476.25 |  | 3169.87
Retail |  |  | 0.047 |  |  | 0.117 |  |  |  | 0.235 |  |  | 0.504 |  |  | 291.77 |  | 731.68 |  |  | 1463.36 |  | 3142.19
Warehouse |  |  | 0.007 |  |  | 0.019 |  |  |  | 0.037 |  |  | 0.08 |  |  | 144.44 |  | 362.2 |  |  | 724.4 |  | 1555.47
Lifetime Savings: HID Replacement, Replace on Burnout, Single Baseline
Table 16. Calculated Lifetime Unit Savings: HID Replacement
Lifetime Energy Savings (kWh)
Building Type |  |  | <35W |  |  | 35W-149W |  |  |  | 150W-220W |  |  | >220W
Avg. Commercial |  |  | 3509.28 |  |  | 8800 |  |  |  | 17600 |  |  | 37791.52
Cold Storage |  |  | 4974 |  |  | 12473.1 |  |  |  | 24946.3 |  |  | 53565.6
Education |  |  | 3984.98 |  |  | 9993.27 |  |  |  | 19986.77 |  |  | 42916.16
Grocery |  |  | 3561.93 |  |  | 8932.14 |  |  |  | 17864.37 |  |  | 38359.08
Health |  |  | 3870.09 |  |  | 9704.88 |  |  |  | 19409.85 |  |  | 41677.56
Hotel/Motel |  |  | 4136.7 |  |  | 10373.5 |  |  |  | 20747 |  |  | 44548.8
Industrial |  |  | 3499.79 |  |  | 8776.25 |  |  |  | 17552.5 |  |  | 37689.17
Office |  |  | 3981 |  |  | 9983.2 |  |  |  | 19966.2 |  |  | 42872.2
Restaurant |  |  | 4120.76 |  |  | 10333.82 |  |  |  | 20667.5 |  |  | 44378.18
Retail |  |  | 3793.01 |  |  | 9511.84 |  |  |  | 19023.68 |  |  | 40848.47
Warehouse |  |  | 3177.68 |  |  | 7968.4 |  |  |  | 15936.8 |  |  | 34220.34
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Multiple Lighting Measures - Analysis File."
• | ICF's 2025 Analysis File named "PY25 TRM - Commercial Lighting - Analysis File."
• | AEG's 2023 Analysis File named "Mid-Year PY23 TRM - Commercial General Lighting - U-Bends - Analysis File."
• | AEG's 2022 Analysis File named "Mid-year PY22 TRM - LED Retrofit Kit Language - Analysis File."
• | AEG's 2022 Analysis File named "PY24 TRM - Commercial General Lighting - Analysis File."
• | AEG's 2020 Analysis File named "AEG HPUC - PY20 v2.0 Lighting Baselines - Analysis."
• | AEG's 2018 Analysis File named "AEG HPUC Update of Com-Lighting Measures - Analysis file."
• | AEG's 2018 Analysis of U.S. Department of Energy's OpenEI Commercial Hourly Load Profiles using Hawaii-specific data. OpenEI data files available here: https://data.openei.org/submissions/153.
• | 10 CFR 430.32(n) General service fluorescent lamps and incandescent reflector lamps. Paragraph (4). https://www.ecfr.gov/current/title-10/part-430/section-430.32#p-430.32(n).
• | 2016 Statewide Customized Offering Procedures Manual for Business. Appendix B: Table of Standard Fixture Wattages. July 2014. Version 6.0. https://static.aesc-inc.com/spc/2013SPCDocs/PGE/App%20B%20Standard%20Fixture%20Watts.pdf.
• | ACEEE, "Lighting/HVAC Interactions and Their Effects on Annual and Peak HVAC Requirements in Commercial Buildings," Sezgen, A. O., Y. J. Huang, Lawrence Berkeley Laboratory, ACEEE Summer Study, 1994.
• | Arkansas Technical Reference Manual, Version 7.0, Arkansas Public Service Commission, 2017.
• | California Public Utilities Commission (CPUC), DEER2016, Interior Lighting Hours-of-Use (HOU), Peak Period Coincident Demand (CDF), and HVAC Interactive Effects (IE) for San Diego, CA, Updated May 27, 2015, available here: https://cedars.cpuc.ca.gov/deer-resources/. (There were no additional updates to interior lighting HOU, CDF, and IE factors in DEER2020.)
• | California Public Utilities Commission (CPUC), DEER2020, Ex Ante database Support Table Export, EUL_basis, 1/1/2013 - 1/1/2021, available here: https://cedars.cpuc.ca.gov/deer-resources/.
• | Consortium of Energy Efficiency (CEE), Commercial Lighting Qualifying Product Lists, August 2018 T8 Replacement Lamps.xlsx, https://cee1.org/program-resources/.
• | DesignLights Consortium (DLC), https://www.designlights.org, https://designlights.org/resources/reports/technical-requirements-resources.
• | Efficiency Vermont Technical Reference User Manual, Measure Savings Algorithms and Cost Assumptions, 2015.
• | ENERGY STAR, https://www.energystar.gov/.
• | Hawai‘i Energy PY17 Program Data for BEEM. Filename: "EMV Extract UPDATED 20181015." Spreadsheet. AEG used data to develop shares of participant energy savings (kWh) by building type. The shares were then used to estimate weighted averages of key parameters for the average commercial building type ("Avg. Commercial").
• | Hawaii HB192 HD2 SD1 CD1, A Bill for an Act, Relating to Energy Efficiency, Act 225, Jul. 5, 2023.
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0, Volume 2: Commercial and Industrial Measures, FINAL, Feb. 8, 2017.
• | Lighting Research Center, Publications, 061Incandescent, page 114, Halogen A, https://www.lrc.rpi.edu/, accessed 11/7/2018.
• | Mid-Atlantic Technical Reference Manual, Version 8, Final, May 2018.
• | Program Year 2017 (PY17) Program Tracking Data for Hawai‘i Energy's BEEM program.
• | Regional Technical Forum. Non-Residential Lighting, Midstream - Unit Energy Savings Workbook, Version 1.3 (NonResLightingMidstream_v1.3.xlsm). Northwest Power and Conservation Council. April 10, 2018. Spreadsheet.
• | Rhode Island Technical Reference Manual – 2018 Program Year, National Grid, 2017.
• | SBDIL Custom Hours Investigation Results, Memorandum, Submitted by Opinion Dynamics, Submitted to Energy Efficiency Manager, Dec. 12, 2017.
• | U.S. Department of Energy, Appliance and Equipment Standards Rulemakings and Notices, General Service Fluorescent Lamps, accessed 11/4/2018, https://www.energy.gov/cmei/buildings/standards-and-test-procedures.
• | Uniform Methods Project, Chapter 2: Commercial and Industrial Lighting Evaluation Protocol, D. Gowans, Left Fork Energy, and C. Telarico, DNV GL, C. Kurnik, National Renewable Energy Laboratory, October 2017.
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,1)−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟∗〖𝐼𝐸〗_(𝐶,𝐸)∗𝑃𝐹
〖∆𝑘𝑊〗_1𝑠𝑡=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,1)−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗𝐶𝐹∗〖𝐼𝐸〗_(𝐶,𝐷)∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒,𝑑𝑢𝑎𝑙)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗〖𝐸𝑈𝐿〗_1𝑠𝑡+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(〖𝐸𝑈𝐿〗_𝐸𝐸−〖𝐸𝑈𝐿〗_1𝑠𝑡 )
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,2)−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟∗〖𝐼𝐸〗_(𝐶,𝐸)∗𝑃𝐹
〖∆𝑘𝑊〗_2𝑛𝑑=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,2)−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗𝐶𝐹∗〖𝐼𝐸〗_(𝐶,𝐷)∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒,𝑠𝑖𝑛𝑔𝑙𝑒)=〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗〖𝐸𝑈𝐿〗_𝐸𝐸
)
𝑅𝑈𝐿=〖〖𝑅𝑂𝑈𝑁𝐷(1〗∕3∗𝐸𝑈𝐿〗_(𝑝𝑟𝑒−𝑒𝑥𝑖𝑠𝑡𝑖𝑛𝑔))
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒,𝑑𝑢𝑎𝑙)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(〖𝐸𝑈𝐿〗_𝐸𝐸−𝑅𝑈𝐿)

## C_Light_Exterior
COMMERCIAL: Exterior Lighting
Return to TOC
UPDATE STATUS
Updated in Fall 2022 for PY22 TRM V2.
MEASURE DETAILS
Description
Replacement of exterior High Intensity Discharge (HID) fixtures with LED luminaires in outdoor street and exterior area applications. Other types of exterior lighting may be addressed with a custom approach.
Program Criteria
The replacement LED fixture must be on the Consortium for Energy Efficiency's (CEE's) most recent Commercial Lighting Qualifying Products List, have an ENERGY STAR label, or be on DesignLights Consortium's Qualified Product List (DLC QPL).
Unit of Measure
One fixture.
Baseline Equipment
Exterior HID fixture.
High Efficiency Equipment
Exterior LED fixture. As an alternative to more traditional LED bulbs or tubes, LED retrofit kit engines qualify as applicable LED replacement lighting, as long as the LED retrofit kit engines have appropriate form factors compared to the baseline lighting.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  | Source/Notes
kWbase | kW_b | kW_b | kW_b | Wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | See Table 1 | see Table 1 | see Table 1 | see Table 1 | kW |  | Assumes replace on burnout (ROB)
kWEE | kW_led | kW_led | kW_led | Wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | See Table 1 |  |  |  | kW |  | DLC QPL and other benchmarking performed in 2018
ISR |  |  |  | In-service rate | [11 empty] | 1 |  |  |  | - |  | AEG's Fall 2018 Benchmarking
CF |  |  |  | Peak demand coincidence factor | [11 empty] | 0.62 |  |  |  | - |  | AEG's analysis of average annual sunset time in Honolulu (6:32 PM) and overlap with the 5-9 PM peak demand period.
HOUyear |  |  |  | Average hours of use per year | [11 empty] | 4100 |  |  |  | hr/yr |  | HECO Rate Schedule F, 2018. Assumes no motion sensors.
PF | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 1 | 1 | 1 | 1 | - |  | Footnote 1
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of efficient lamp | [11 empty] | 12 |  |  |  | yrs |  | Based on Rated Lamp Life2 of 50,000 hr and HOU of 4,100 hr/yr
1 Use value of PF=1 until more data is available on PF of LEDs relative to baseline lighting.
2 Source of rated lamp life includes DEER, DLC, and other benchmarking.
Table 1. Wattages, kWbase and kWEE
Lighting Type | [5 empty] | Baseline Wattage, kWbase | [7 empty] | Efficient Wattage, kWEE | [6 empty] | Source
LED: HID replacement, <35W | [5 empty] | HID 50W-100W Baseline: 64W, 86W, 128W | [5 empty] | 0.093 |  | LED: HID replace, <35W |  |  |  |  | 0.028 |  | Benchmarking; no change from PY18 TRM
LED: HID replacement, 35W-149W | [5 empty] | HID 150W-250W Baseline: 188W, 240W, 295W | [5 empty] | 0.241 |  | LED: HID replace, 35W-149W |  |  |  |  | 0.078 |  | Benchmarking; no change from PY18 TRM
LED: HID replacement, 150W-220W | [5 empty] | HID 310W-600W Baseline: 365W, 457W, 665W | [5 empty] | 0.496 |  | LED: HID replace, 150W-220W |  |  |  |  | 0.17 |  | Benchmarking; no change from PY18 TRM
LED: HID replacement, >220W | [5 empty] | HID 750W-1000W Baseline: 840W, 1100W | [5 empty] | 0.97 |  | LED: HID replace, >220W |  |  |  |  | 0.27 |  | Benchmarking; no change from PY18 TRM
SAVINGS
First Year Savings: LED Exterior Fixtures, ROB, Single Baseline
Table 2. Calculated First Year Unit Demand Savings
Peak Demand Savings (kW)
Lighting Type | [5 empty] | <35W |  |  |  | 35W-149W |  |  |  | 150W-220W |  |  |  | >220W
Exterior | [5 empty] | 0.04 |  |  |  | 0.101 |  |  |  | 0.202 |  |  |  | 0.434
Table 3. Calculated First Year Unit Energy Savings
Annual Energy Savings (kWh/year)
Lighting Type | [5 empty] | <35W |  |  |  | 35W-149W |  |  |  | 150W-220W |  |  |  | >220W
Exterior | [5 empty] | 266.5 |  |  |  | 668.3 |  |  |  | 1336.6 |  |  |  | 2870
Lifetime Savings: LED Exterior Fixtures, ROB, Single Baseline
Table 4. Calculated Lifetime Unit Savings
Lifetime Energy Savings (kWh)
Lighting Type | [5 empty] | <35W |  |  |  | 35W-149W |  |  |  | 150W-220W |  |  |  | >220W
Exterior | [5 empty] | 3198 |  |  |  | 8019.6 |  |  |  | 16039.2 |  |  |  | 34440
RESOURCES
• | 2016 Statewide Customized Offering Procedures Manual for Business. Appendix B: Table of Standard Fixture Wattages. July 2014, Version 6.0.
• | AEG's 2022 Analysis File named "Mid-year PY22 TRM - LED Retrofit Kit Language - Analysis File."
• | AEG's 2018 Analysis File named "AEG HPUC Update of Com-Lighting Measures - Analysis file."
• | AEG's Analysis of Sunset Data for Honolulu, HI. Source: Sunrise-Sunset online tool, accessed 11/4/2018, https://sunrise-sunset.org/.
• | DesignLights Consortium (DLC), https://www.designlights.org, https://www.designlights.org/solid-state-lighting/qualification-requirements/technical-requirements/.
• | Hawaiian Electric Company, Rate Schedule F, Public Street Lighting, Highway Lighting and Park and Playground Floodlighting, Revised Sheet No. 59, Effective September 1, 2018.
• | Mid-Atlantic Technical Reference Manual, Version 8, Final, May 2018.
∆𝑘𝑊ℎ=(〖𝑘𝑊〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟∗𝑃𝐹
∆𝑘𝑊=(〖𝑘𝑊〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗𝐶𝐹∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## C_Lighting_Refrigerated Case
COMMERCIAL: Refrigerated Case Lighting
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the PY25 TRM. The replace on burnout portion of this measure will sunset on December 31, 2025. The early replacement portion will sunset on December 31, 2026.
MEASURE DETAILS
Description
This measure involves retrofitting the linear fluorescent lighting system within an existing low or medium temperature refrigerated case with efficient LED refrigerated case lighting.
Program Criteria
New refrigerated cases do not qualify for this measure. The qualifying technology must be specifically designed for refrigerated case lighting applications. For example, lamps in the DLC "General Application: Case Lighting" category qualify. An equivalent category of lamps rated by ENERGY STAR or Lighting Facts may qualify as well, pending Program approval.
Unit of Measure
One retrofit kit.
Baseline Equipment
Early replacement projects require a dual baseline. The first baseline is the pre-existing equipment, which has been estimated as a blend of 40% T12 and 60% T8 fluorescent lamps. The pre-existing equipment is assumed to have a remaining useful life (RUL) of one-third of the Effective Useful Life (EUL) of the fluorescent lamps. The second baseline must comply with the current Hawaii standard, which will ban linear fluorescent tubes effective January 1, 2026. As a result, the second baseline will be a linear LED tube, and there will be no savings during the second baseline period. Only lamps that are in working order at the time of the replacement qualify for early replacement. If the pre-existing lamps cannot be verified to be in working order, a replace on burnout (ROB) baseline must be used.
ROB projects have a single baseline. The baseline must comply with current federal codes and standards for general service fluorescent lamps, which took effect January 26, 2018. The EUL used to calculate lifetime savings is capped at the EUL of the baseline lamp. This is due to the ban of fluorescent lamps in Hawaii. Because of the ban, the baseline would convert to an LED after the EUL of the fluorescent lighting has been reached.
High Efficiency Equipment
LED replacement lamp unit. As an alternative to more traditional LED bulbs or tubes, LED retrofit kit engines qualify as applicable LED replacement lighting, as long as the LED retrofit kit engines have appropriate form factors compared to the baseline lighting.
The replace on burnout portion of this measure has a sunset date of December 31, 2025, which is the day before Hawaii's ban on linear fluorescent tubes takes effect. The early replacement portion of this measure has a sunset date of December 31, 2026, which is one year after the ban; the extra year for this portion of the measure allows for early replacement of pre-existing fluorescent tubes, which have an RUL of one year.
ALGORITHMS
First Baseline Peak Demand Reduction, kW
(1)
Second Baseline Peak Demand Reduction, kW
(2)
First Baseline Annual Energy Savings, kWh/yr
(3)
Second Baseline Annual Energy Savings, kWh/yr
(4)
Lifetime Energy Savings, kWh (Dual Baseline, Early Replacement)
(5)
Lifetime Energy Savings, kWh (Single Baseline, ROB)
(6)
The EUL is capped at the baseline lamp EUL, since the baseline fluorescent lamps will no longer be available after ban. LEDs will become the baseline after that.
Remaining Useful Life (only applicable to Early Replacement)
(7)
Waste Heat Factors due to Interaction with Building Space Cooling System
(8)
(9)
Waste Heat Factors due to Interaction with Case Refrigeration System
(10)
(11)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  | Unit | Source/Notes
kWbase,1 | kW_b | kW_b | kW_b | Wattage of the first baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | Table 1 |  | kW | Manufacturer catalogs; includes ballast power factor of 0.98 for T8 and 0.90 for T12, as cited in RTF 2018 workbook1
kWbase,2 | kW_b | kW_b | kW_b | Wattage of the second baseline lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | Table 1 |  | kW | Manufacturer catalogs; includes ballast power factor of 0.98 for T8, as cited in RTF 2018 workbook1
kWEE | kW_led | kW_led | kW_led | Wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | Table 1 |  | kW | Hawai‘i Energy PY17 installation data for measure; assumes LED driver efficiency of 0.89 (driver efficiency from RTF 2018 workbook1)
ISR |  |  |  | Lifetime in-service rate | [11 empty] | 1 |  | - | AEG's Fall 2018 Benchmarking
CF |  |  |  | Peak demand coincidence factor | [11 empty] | 0.88457 |  | - | Adjustment of AEG's general lighting CF for the Grocery segment by ratio of HOUrefrig_case/HOUgen_grocery_light
HOUyear |  |  |  | Average hours of use per year | [11 empty] | 6205 |  | hr/yr | No change from PY18 TRM2
PF | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 1 |  | - | Footnote 3
WHC,D |  |  |  | Waste heat factor due to lighting interaction with building space cooling system demand | [11 empty] | 0.045 |  | - | See Equation 8; assumes 50% of lighting impacts general space cooling demand4
WHC,E |  |  |  | Waste heat factor due to lighting interaction with building space cooling system energy use | [11 empty] | 0.07 |  | - | See Equation 9; assumes 50% of lighting impacts general space cooling energy use4
IEC,D |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting | [11 empty] | 1.09 |  | - | From C_Light_General tab, Table 4
IEC,E |  |  |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting | [11 empty] | 1.14 |  | - | From C_Light_General tab, Table 4
WHR,D |  |  |  | Waste heat factor due to lighting interaction with case refrigeration system demand | [11 empty] | See Table 2 |  | - | Assumes 50% of lighting impacts case refrigeration demand4
WHR,E |  |  |  | Waste heat factor due to lighting interaction with case refrigeration system energy use | [11 empty] | See Table 2 |  | - | Assumes 50% of lighting impacts case refrigeration energy use4
EERR |  |  |  | Energy efficiency ratio of case refrigeration system | [11 empty] | See Table 2 |  | kBtu/ kWh | From RTF 20181
RUL | Measure Life | Measure Life | Measure Life | Remaining useful life of pre-existing lamp | [11 empty] | 1 |  | yrs | Per Equation 7, assumes 1/3 EULpre-existing, rounded to nearest year
EULpre-existing | Measure Life | Measure Life | Measure Life | Effective useful life of pre-existing lamp | [11 empty] | 4 |  | yrs | Assumes lamp life of 24,000 hours
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of efficient lamp | [11 empty] | 8 |  | yrs | Assumes lamp life of 50,000 hours
1 Regional Technical Forum. Commercial Grocery Display Case Lighting - Unit Energy Savings Workbook, Version 1.1. Northwest Power and Conservation Council. Oct. 1, 2018. Spreadsheet.
2 The original source is Theobald, M. A., Emerging Technologies Program: Application Assessment Report #0608, LED Supermarket Case Lighting Grocery Store, Northern California, Pacific Gas and Electric Company, January 2006. Assumes refrigerated case lighting typically operates 17 hours per day, 365 days per year. Benchmarking results indicate that refrigerated case lighting is not tied to general store lighting.
3 Use value of PF=1 until more data is available on PF of LEDs relative to baseline lighting.
4 Based on a ratio of 0.5 used in the Department of Energy TSD for Commercial Refrigeration, Table 5.6.1. "Fraction of lighting power into case for lighting outside of air curtain (W/W)" (https://www1.eere.energy.gov/buildings/appliance_standards/pdfs/cre2_nopr_tsd_2013_08_28.pdf). The same logic implies the fraction of lighting power outside of the refrigerated case for lighting that is inside of the case is 50%. So, the assumption is that 50% of lighting affects general cooling load and 50% of lighting affects case refrigeration load.
Table 1. Measure Descriptions: Wattages1
Lighting Type | [5 empty] | Early Replace-ment2 |  |  |  | Replace on Burnout |  |  |  | Early Replace-ment |  |  | kWEE
[6 empty] | kWbase,1 |  |  |  | kWbase,1 |  |  |  | kWbase,2
4' retrofit kit | [5 empty] | 0.04424 |  |  |  | 0.03824 |  |  |  | 0.0188 |  |  | 0.0188
5' retrofit kit | 5' retrofit kit | 5' retrofit kit | 5' retrofit kit | 5' retrofit kit | 5' retrofit kit | 0.0553 |  |  |  | 0.0478 |  |  |  | 0.0225 |  |  | 0.0225
6' retrofit kit | 6' retrofit kit | 6' retrofit kit | 6' retrofit kit | 6' retrofit kit | 6' retrofit kit | 0.06636 |  |  |  | 0.05736 |  |  |  | 0.0252 |  |  | 0.0252
1The underlying per-foot wattages used to calculate wattages by retrofit kit are from the RTF 2018 Workbook.
2The pre-existing baseline (kWbase,1) consists of a 60%/40% T8/T12 blend.
Table 2. Waste Heat Factors for Refrigeration
Case Type | [5 empty] | EERR1 |  |  |  | WHR,D |  |  |  | WHR,E2
Medium Temperature (Refrigerators/ Coolers) | [5 empty] | 10.6 |  |  |  | 0.16094 |  |  |  | 0.16094
Low Temperature (Freezers) | [5 empty] | 4.1 |  |  |  | 0.4161 |  |  |  | 0.4161
1 From RTF 2018 Workbook. EERs are the regional weighted averages from Standard Information Workbook v3.2. A future update to the Hawai‘i TRM should include Hawai‘i-specific EER data from market research.
2 Assume the energy and demand waste heat factors for refrigeration are equivalent. This is consistent with other sources reviewed.
SAVINGS
Annual Savings: Early Replacement, Dual Baseline (Applicable through December 31, 2026)
Case Type | [7 empty] | Measure Name | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings
[16 empty] | 1st BL |  | 2nd BL |  | 1st BL | 2nd BL
Medium Temperature (Refrigerators/Coolers) | [7 empty] | 4 | [7 empty] | 0.027 |  | 0 |  | 194.31 | 0
[8 empty] | 5 | [7 empty] | 0.035 |  | 0 |  | 250.53 | 0
[8 empty] | 6 | [7 empty] | 0.044 |  | 0 |  | 314.38 | 0
Low Temperature (Freezers) | [7 empty] | 4 | [7 empty] | 0.033 |  | 0 |  | 234.59 | 0
[8 empty] | 5 | [7 empty] | 0.042 |  | 0 |  | 302.46 | 0
[8 empty] | 6 | [7 empty] | 0.053 |  | 0 |  | 379.55 | 0
Annual Savings: Replace on Burnout, Single Baseline (Applicable through December 31, 2025)
Case Type | [7 empty] | Measure Name | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings
Medium Temperature (Refrigerators/Coolers) | [7 empty] | 4 | [7 empty] | 0.021 |  |  |  | 148.48
[8 empty] | 5 | [7 empty] | 0.027 |  |  |  | 193.24
[8 empty] | 6 | [7 empty] | 0.034 |  |  |  | 245.64
Low Temperature (Freezers) | [7 empty] | 4 | [7 empty] | 0.025 |  |  |  | 179.26
[8 empty] | 5 | [7 empty] | 0.033 |  |  |  | 233.3
[8 empty] | 6 | [7 empty] | 0.042 |  |  |  | 296.55
Lifetime Savings: Early Replacement, Dual Baseline (Applicable through December 31, 2026)
Case Type | [7 empty] | Measure Name | [7 empty] | Lifetime Energy Savings
Medium Temperature (Refrigerators/Coolers) | [7 empty] | 4 | [7 empty] | 194.31
[8 empty] | 5 | [7 empty] | 250.53
[8 empty] | 6 | [7 empty] | 314.38
Low Temperature (Freezers) | [7 empty] | 4 | [7 empty] | 234.59
[8 empty] | 5 | [7 empty] | 302.46
[8 empty] | 6 | [7 empty] | 379.55
Note: The EUL used to calculate lifetime savings is capped at the EUL of the baseline lamp. This is due to the ban of fluorescent lamps in Hawaii. Because of the ban, the baseline would convert to an LED after the EUL of the fluorescent lighting has been reached. Therefore, EULpre-existing is used to calculate Lifetime Energy Savings.
Lifetime Savings: Replace on Burnout, Single Baseline (Applicable through December 31, 2025)
Case Type | [7 empty] | Measure Name | [7 empty] | Lifetime Energy Savings
Medium Temperature (Refrigerators/Coolers) | [7 empty] | 4 | [7 empty] | 593.92
[8 empty] | 5 | [7 empty] | 772.96
[8 empty] | 6 | [7 empty] | 982.56
Low Temperature (Freezers) | [7 empty] | 4 | [7 empty] | 717.04
[8 empty] | 5 | [7 empty] | 933.2
[8 empty] | 6 | [7 empty] | 1186.2
Note: The EUL used to calculate lifetime savings is capped at the EUL of the baseline lamp. This is due to the ban of fluorescent lamps in Hawaii. Because of the ban, the baseline would convert to an LED after the EUL of the fluorescent lighting has been reached.
RESOURCES
• | ICF's 2025 Analysis File named "PY25 TRM - Commercial Lighting - Analysis File."
• | AEG's 2022 Analysis File named "Mid-year PY22 TRM - LED Retrofit Kit Language - Analysis File."
• | AEG's Analysis Files named "AEG HPUC Dual BL and TRB - Analysis File" and "AEG HPUC Update of Com-Lighting Measures - Analysis file."
• | California Public Utilities Commission, Database of Energy Efficiency Resources, 2020 update, (DEER2020), READI v.2.5.0, Ex Ante Database Support Table Export, EUL_basis, created on 8/24/2018, available here: www.deeresources.com/index.php/homepage. Spreadsheet.
• | Department of Energy, TSD for Commercial Refrigeration, Table 5.6.1. "Fraction of lighting power into case for lighting outside of air curtain (W/W)" (https://www1.eere.energy.gov/buildings/appliance_standards/pdfs/cre2_nopr_tsd_2013_08_28.pdf).
• | Hawaii HB192 HD2 SD1 CD1, A Bill for an Act, Relating to Energy Efficiency, Act 225, Jul. 5, 2023.
• | Michigan Energy Measure Database, v. 2018, https://www.michigan.gov/mpsc/0,4639,7-159-52495_55129---,00.html, filename: "mi_master_measure_database_2018-112917_609672_7"
• | Mid-Atlantic Technical Reference Manual, Version 8, Final, May 2018.
• | Program Year 2017 (PY17) Program Tracking Data for Hawai‘i Energy's LED Refrigerated Case Lighting projects.
• | Regional Technical Forum. Commercial Grocery Display Case Lighting - Unit Energy Savings Workbook, Version 1.1. Northwest Power and Conservation Council. Oct. 1, 2018. Spreadsheet.
• | State of Minnesota, Technical Reference Manual for Energy Conservation Improvement Programs, Version 2.2, May 2, 2018.
• | State of Pennsylvania Technical Reference Manual, Pennsylvania Public Utilities Commission, June 2016.
• | Tennessee Valley Authority Technical Reference Manual, Version 6.0, Oct. 1, 2017.
• | Theobald, M. A., Emerging Technologies Program: Application Assessment Report #0608, LED Supermarket Case Lighting Grocery Store, Northern California, Pacific Gas and Electric Company, January 2006.
〖∆𝑘𝑊〗_1𝑠𝑡=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,1)−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗𝐶𝐹∗(1+〖𝑊𝐻〗_(𝐶,𝐷)+〖𝑊𝐻〗_(𝑅,𝐷) )∗𝑃𝐹
〖∆𝑘𝑊〗_2𝑛𝑑=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,2)−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗𝐶𝐹∗(1+〖𝑊𝐻〗_(𝐶,𝐷)+〖𝑊𝐻〗_(𝑅,𝐷) )∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,1)−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟∗(1+〖𝑊𝐻〗_(𝐶,𝐸)+〖𝑊𝐻〗_(𝑅,𝐸) )∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,2)−〖𝑘𝑊〗_𝐸𝐸 )∗𝐼𝑆𝑅∗〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟∗(1+〖𝑊𝐻〗_(𝐶,𝐸)+〖𝑊𝐻〗_(𝑅,𝐸) )∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒,𝑑𝑢𝑎𝑙)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(〖𝐸𝑈𝐿〗_𝐸𝐸−𝑅𝑈𝐿)
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒,𝑠𝑖𝑛𝑔𝑙𝑒)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗〖𝐸𝑈𝐿〗_(𝑝𝑟𝑒−𝑒𝑥𝑖𝑠𝑡𝑖𝑛𝑔)
𝑅𝑈𝐿=〖1∕3∗𝐸𝑈𝐿〗_(𝑝𝑟𝑒−𝑒𝑥𝑖𝑠𝑡𝑖𝑛𝑔)
〖𝑊𝐻〗_(𝐶,𝐷)=(〖𝐼𝐸〗_(𝐶,𝐷)−1)∗0.5
〖𝑊𝐻〗_(𝐶,𝐸)=(〖𝐼𝐸〗_(𝐶,𝐸)−1)∗0.5
〖𝑊𝐻〗_(𝑅,𝐷)=(3.412𝑘𝐵𝑡𝑢/𝑘𝑊ℎ)∗0.5/〖𝐸𝐸𝑅〗_𝑅
〖𝑊𝐻〗_(𝑅,𝐸)=〖𝑊𝐻〗_(𝑅,𝐷)

## C_Light_Occupancy Sensor
COMMERCIAL: Light Occupancy Sensor
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. This update changes the default type of lighting controlled with an occupancy sensor from linear fluorescent lamps to linear LED lamps.
MEASURE DETAILS
Description
This measure is for wall switch sensors that control the use of lighting in areas around the facility with variable use.
Program Criteria
The savings approach for this measure assumes the occupancy sensors are installed in existing buildings that have not yet been required to comply with current ANSI/ASHRAE/IES Standard 90.1 requirements for occupancy sensors.
Ultrasonic and infrared sensors are eligible.
Unit of Measure
One sensor.
Baseline Equipment
Manual switch.
High Efficiency Equipment
Occupancy sensor installed.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description |  |  | Value | Unit | Source/Notes
Pctrl |  |  |  | Total wattage controlled by sensor |  |  | Actual (default = 32) | W | Default is a fixture with two (2) 4-foot LED linear (T8) lamps controlled by one sensor. Source of wattage is Table 2 in the C_Light_General tab.
Constant |  |  |  | Conversion factor from W to kW |  |  | 1000 | W/kW
RTR |  |  |  | Runtime reduction factor from sensor |  |  | 0.24 | - | AEG's Fall 2018 Benchmarking; median of 16 reviewed sources
ISR |  |  |  | Lifetime in-service rate |  |  | 0.98 | - | AEG's Fall 2018 Benchmarking
CF |  |  |  | Coincidence factor |  |  | See Table 1 | - | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period, adjusted to specific lighting types1
HRS |  |  |  | Hours of lighting operation |  |  | See Table 1 | hrs | DEER20202 hours of use with no occupancy sensors for San Diego (CA's southern-most latitude)
IEC,D |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting |  |  | See Table 1 | - | DEER20202 interactive effect factors for San Diego, adjusted to Hawai‘i's weather zone using LBNL simulation results;3 Assumes 50% of spaces with occupancy sensors are air conditioned
IEC,E |  |  |  | Factor reflecting impact of lighting savings on cooling load |  |  | See Table 1 | - | DEER20202 interactive effect factors for San Diego, adjusted to Hawai‘i's weather zone using LBNL simulation results;3 Assumes 50% of spaces with occupancy sensors are air conditioned
PF |  |  |  | Persistence factor |  |  | 1 | - | Assumes that savings persistence is accounted for in the EUL
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of occupancy sensor measure |  |  | 8 | yrs | AEG's Fall 2018 Benchmarking; median of 16 reviewed sources
1 This approach assumes that the occupancy pattern during 5-9 pm is consistent with rest of day, which may not be the case for some building types (e.g., offices). Overall, this is likely to yield conservative values for CF.
2 The DEER interactive effect factors and hours of use were developed for DEER2016 and they are still applicable to DEER2020.
3 "Lighting/HVAC Interactions and Their Effects on Annual and Peak HVAC Requirements in Commercial Buildings," Sezgen, A. O., Y. J. Huang, Lawrence Berkeley Laboratory, ACEEE Summer Study, 1994.
Table 1. Key Parameters for Occupancy Sensor Measure (Applicable to Counties of Oahu, Maui, and Hawai‘i)
Building Type |  |  |  | CF | HRS | IEC,D | IEC,E | Weights |  | Source
Avg. Commercial |  |  |  | 0.34348 | 2427.7497 | 1.0994 | 1.1332 | - |  | Weighted averages based on kWh savings by building type associated with actual PY17 occupancy sensor projects.
Cold Storage |  |  |  | 0.2 | 4700 | 1.125 | 1.31 | 0% |  | Values tie back to C_Light_General tab, Tables 3, 4, and 5.
Education |  |  |  | 0.32 | 1702 | 1.155 | 1.125 | 1.861%
Grocery |  |  |  | 0.68 | 4770 | 1.045 | 1.07 | 2.171%
Health |  |  |  | 0.63 | 5100 | 1.12 | 1.075 | 20.78%
Hotel/Motel |  |  |  | 0.23 | 1130 | 1.135 | 1.18 | 38.14%
Industrial |  |  |  | 0.59 | 2305 | 1.1 | 1.065 | 0.7754%
Office |  |  |  | 0.25 | 1980 | 1.035 | 1.13 | 31.93%
Restaurant |  |  |  | 0.49 | 3500 | 1.12 | 1.14 | 0.3102%
Retail |  |  |  | 0.5 | 3690 | 1.18 | 1.075 | 3.566%
Warehouse |  |  |  | 0.08 | 1970 | 1.08 | 1.005 | 0.4652%
Notes:
a. Assumes linear, U-bend, or troffer lamps are controlled. (Values would be different for omni-directional, directional, decorative, or high bay lighting.)
b. The CF values were derived using the three step process described in the C_Light_General tab.
c. Baseline HRS are from DEER2020 hours of use for San Diego IOU for no occupancy sensor case.
d. The IE values were derived using the four step process described in the C_Light_General tab.
SAVINGS
Deemed Savings (based on default value for Pctrl)
Building Type |  |  |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Avg. Commercial |  |  |  |  | 0.003 |  | 20.71 |  |  | 165.68
Cold Storage |  |  |  |  | 0.002 |  | 46.34 |  |  | 370.72
Education |  |  |  |  | 0.003 |  | 14.41 |  |  | 115.28
Grocery |  |  |  |  | 0.005 |  | 38.41 |  |  | 307.28
Health |  |  |  |  | 0.005 |  | 41.26 |  |  | 330.08
Hotel/Motel |  |  |  |  | 0.002 |  | 10.04 |  |  | 80.32
Industrial |  |  |  |  | 0.005 |  | 18.48 |  |  | 147.84
Office |  |  |  |  | 0.002 |  | 16.84 |  |  | 134.72
Restaurant |  |  |  |  | 0.004 |  | 30.03 |  |  | 240.24
Retail |  |  |  |  | 0.004 |  | 29.86 |  |  | 238.88
Warehouse |  |  |  |  | 0.001 |  | 14.9 |  |  | 119.2
Semi-Prescriptive Savings Calculator (based on user input of Pctrl)
Enter total wattage controlled by sensor, Pctrl
32
Building Type |  |  |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Avg. Commercial |  |  |  |  | 0.003 |  | 20.71 |  |  | 165.68
Cold Storage |  |  |  |  | 0.002 |  | 46.34 |  |  | 370.72
Education |  |  |  |  | 0.003 |  | 14.41 |  |  | 115.28
Grocery |  |  |  |  | 0.005 |  | 38.41 |  |  | 307.28
Health |  |  |  |  | 0.005 |  | 41.26 |  |  | 330.08
Hotel/Motel |  |  |  |  | 0.002 |  | 10.04 |  |  | 80.32
Industrial |  |  |  |  | 0.005 |  | 18.48 |  |  | 147.84
Office |  |  |  |  | 0.002 |  | 16.84 |  |  | 134.72
Restaurant |  |  |  |  | 0.004 |  | 30.03 |  |  | 240.24
Retail |  |  |  |  | 0.004 |  | 29.86 |  |  | 238.88
Warehouse |  |  |  |  | 0.001 |  | 14.9 |  |  | 119.2
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Multiple Lighting Measures - Analysis File."
• | ACEEE, "Lighting/HVAC Interactions and Their Effects on Annual and Peak HVAC Requirements in Commercial Buildings," Sezgen, A. O., Y. J. Huang, Lawrence Berkeley Laboratory, ACEEE Summer Study, 1994.
• | AEG's 2018 Analysis File titled "AEG HPUC Update of Com-Lighting Measures - Analysis file."
• | AEG's 2018 Analysis of U.S. Department of Energy's OpenEI Commercial Hourly Load Profiles using Hawai‘i-specific data. OpenEI data files available here: https://openei.org/doe-opendata/dataset/commercial-and-residential-hourly-load-profiles-for-all-tmy3-locations-in-the-united-states.
• | Arkansas Technical Reference Manual, Version 7.0, Arkansas Public Service Commission, 2017.
• | California Public Utilities Commission (CPUC), DEER2016, Interior Lighting Hours-of-Use (HOU), Peak Period Coincident Demand (CDF), and HVAC Interactive Effects (IE) for San Diego, CA, Updated May 27, 2015, available here: http://www.deeresources.com. (There were no additional updates to interior lighting HOU, CDF, and IE factors in DEER2020.)
• | Connecticut's 2018 Program Savings Document, 13th Edition, filed December 15, 2017. https://www.energizect.com/sites/default/files/2018-PSD-FINAL-121217.pdf.
• | DNV KEMA, Retrofit Lighting Controls Measures Summary of Findings, FINAL REPORT, 2014.
• | Easy Lighting Calculator, Version 3, eLC_V3, Southern California Edison, Custom Lighting Tool, updated 12/07/2016.
• | Efficiency Vermont Technical Reference User Manual, Measure Savings Algorithms and Cost Assumptions, 2015.
• | Hawai‘i Energy PY17 Program Data for Commercial Occupancy Sensor Projects. Filename: "EMV Extract UPDATED 20181015". Spreadsheet.
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0, Volume 2: Commercial and Industrial Measures, FINAL, Feb. 8, 2017.
• | Maniccia, D., B. Von Neida, and A. Tweed. An analysis of the energy and cost savings potential of occupancy sensors for commercial lighting systems, Illuminating Engineering Society of North America 2000 Annual Conference: Proceedings. IESNA: New York, NY, pp. 433-459.
• | Massachusetts Technical Reference Manual, 2016-2018 Program Years, October 2015.
• | Mid-Atlantic Technical Reference Manual, Version 8, Final, May 2018.
• | New Mexico Technical Resource Manual for the Calculation of Energy Efficiency Savings, 2016, Section 3.5. p.31.
• | Northwest Power Conservation Council (NWPCC). Commercial Interior Lighting Controls, Version 10 - Seventh Power Plan Conservation Supply Workbooks. February 25, 2016. Spreadsheet.
• | Program Year 2017 (PY17) Program Tracking Data for Hawai‘i Energy's business programs, occupancy sensor projects.
• | Public Service Company of Colorado. 2019/2020 Demand-Side Management Plan. Colorado Public Utilities Commission. Aug 31, 2018.
• | Public Utility Commission of Texas, Texas Technical Reference Manual, Version 5.0, Volume 2: Residential Measures, Program Year (PY) 2018, October 2017.
• | State of Minnesota, Technical Reference Manual for Energy Conservation Improvement Programs, Version 2.2, May 2, 2018.
• | State of Pennsylvania Technical Reference Manual, Pennsylvania Public Utilities Commission, June 2016.
• | Tennessee Valley Authority Technical Reference Manual, Version 6.0, Oct. 1, 2017.
• | Vermont Energy Investment Corporation. Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 5.0. Illinois Energy Efficiency Stakeholder Advisory Group. February 11, 2016.
∆𝑘𝑊=(𝑃_𝑐𝑡𝑟𝑙∕1000)∗𝑅𝑇𝑅∗𝐼𝑆𝑅∗〖𝐶𝐹∗𝐼𝐸〗_(𝐶,𝐷)∗𝑃𝐹
∆𝑘𝑊ℎ=(𝑃_𝑐𝑡𝑟𝑙∕1000)∗𝑅𝑇𝑅∗𝐼𝑆𝑅∗〖𝐻𝑅𝑆∗𝐼𝐸〗_(𝐶,𝐸)∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## C_Light_Stairwell Bi-Level
COMMERCIAL: Stairwell Bi-level Dimming Controls
Return to TOC
UPDATE STATUS
Updated in Fall 2018 for PY19 TRM.
MEASURE DETAILS
Description
Stairwell lighting typically operates continuously at full output despite very low, intermittent use. Bi-level stairwell dimming lights utilize either an ultrasonic or infrared motion sensor to detect motion in stairwells. Solid state controls are used to dim fixtures to lower light levels when a space is unoccupied. This measure may also include the installation of a new efficient fixture along with bi-level dimming controls.
Program Criteria
This measure applies to existing buildings. New construction is not eligible because the current ANSI/ASHRAE/IES Standard 90.1 requires that stairwell lighting be controlled so that lighting power can be reduced by at least 50% within 30 minutes of the stairwell space becoming unoccupied.
Ultrasonic and infrared sensors are eligible. Lighting must be ENERGY STAR labeled or Design Lights Consortium (DLC) listed and UL compliant.
Unit of Measure
Varies with scale of project.
Baseline Equipment
No bi-level dimming lights with occupancy sensors.
High Efficiency Equipment
Bi-level dimming lights with occupancy sensors.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description |  |  |  | Value |  | Unit | Source/Notes
kWbase | kW_b | kW_b | kW_b | Baseline kW load of continuous operation stairwell fixtures |  |  |  | User Input |  | kW | This is calculated based on user input of fixture wattages and fixture quantities
kWEE,dim | kW_led | kW_led | kW_led | kW load of stairwell fixtures in dim or low level mode when unoccupied |  |  |  | User Input |  | kW | This is calculated based on user input of fixture wattages in low power mode and fixture quantities
kWEE,full | kW_led | kW_led | kW_led | kW load of stairwell fixture in full power mode when occupied |  |  |  | User Input |  | kW | This is calculated based on user input of fixture wattages in full power mode and fixture quantities
%time,dim | kW_led | kW_led | kW_led | Fraction of time stairwell fixture is in dim or low level mode when unoccupied |  |  |  | 80% |  | % | AEG's Fall 2018 Benchmarking1
%time,full | kW_led | kW_led | kW_led | Fraction of time stairwell fixture is in full power mode when occupied |  |  |  | 20% |  | % | AEG's Fall 2018 Benchmarking1
IEC,D |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting |  |  |  | 1 |  | - | Assumes negligible interaction with cooling equipment; conservative assumption, but reasonable since not all stairwells are conditioned
IEC,E |  |  |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting |  |  |  | 1 |  | - | Assumes negligible interaction with cooling equipment; conservative assumption, but reasonable since not all stairwells are conditioned
ISR |  |  |  | Lifetime in-service rate |  |  |  | 1 |  |  | Assumes installations will be verified
CF |  |  |  | Coincidence factor |  |  |  | 1 |  | - | Assumes that occupancy patterns during peak hours of 5-9 PM are consistent (on average) with occupancy during the rest of the day
HOUyear |  |  |  | Hours of use per year |  |  |  | 8760 |  | hrs | Assumes stairwell lighting must remain on 24 hr/day, 365 day/yr; value is consistent with AEG's Fall 2018 Benchmarking results
PF |  |  |  | Persistence factor |  |  |  | 1 |  | - | Assumes that savings persistence is accounted for in the EUL
EULEE |  |  |  | Effective useful life of measure |  |  |  | 8 |  | yrs | AEG's Fall 2018 Benchmarking
1 Benchmarking yielded a median value of 79% for the percentage of time stairwells with bi-level occupancy control are in low power mode, and 21% for the percentage of time they are in full power mode. Values for low power mode varied from 62% to 97%, depending on the day of the week, building type, and stairwell type. AEG rounded to 80% and 20%.
SAVINGS
Semi-Prescriptive Savings Calculator (based on user input of fixture wattages and quantities)
1. Enter Baseline Fixture Wattage and Quantity (up to 3 types of fixtures)
|  | Fixture Type |  |  | Full Power Mode Wattage, kW |  | Quantity
|  | F32T8 |  |  | 0.031 |  | 10
|  | F17T8 |  |  | 0.016 |  | 2 |  |  |  |  | kWbase = | 0.342 | kW
Note: Entries in red are for illustrative purposes only
2. Enter Energy Efficient Fixture Wattages and Quantity (up to 3 types of fixtures)
|  | Fixture Type |  |  | Full Power Mode Wattage, kW |  | Low Power Mode Wattage, kW |  | Quantity
|  | F32T8 |  |  | 0.031 |  | 0.015 |  | 10 |  |  | kWEE,full = | 0.342 | kW
|  | F17T8 |  |  | 0.016 |  | 0.008 |  | 2
[12 empty] | kWEE,dim = | 0.166 | kW
Note: Entries in red are for illustrative purposes only
Measure Name | [5 empty] | Peak Demand Savings |  | Annual Energy Savings |  |  |  | Lifetime Energy Savings
Stairwell Bi-Level Dimming | [5 empty] | 0.141 |  | 1233.408 |  |  |  | 9867.26
Note: Savings in blue result from sample entries above. They are for illustrative purposes only.
RESOURCES
• | AEG's 2018 Analysis File titled "AEG HPUC Update of Com-Lighting Measures - Analysis file."
• | Connecticut's 2018 Program Savings Document, 13th Edition, filed December 15, 2017.
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0, Volume 2: Commercial and Industrial Measures, FINAL, Feb. 8, 2017.
• | Lighting Research Program, Project 5.1 Bi-Level Stairwell Fixture Performance, Final Report, prepared for California Energy Commission, Public Interest Energy Research Program, October 2015, CEC-500-2005-141-A16, Tables 2 and 3, https://www.energy.ca.gov/2005publications/CEC-500-2005-141/CEC-500-2005-141-A16.PDF
• | Massachusetts Technical Reference Manual, 2013-2015 Program Years, October 2012.
• | Michigan Energy Measure Database, v. 2018, https://www.michigan.gov/mpsc/0,4639,7-159-52495_55129---,00.html, filename: "mi_master_measure_database_2018-112917_609672_7"
• | Public Service Company of Colorado. Xcel Energy. 2019/2020 Demand-Side Management Plan. Colorado Public Utilities Commission. August 31, 2018.
• | Tennessee Valley Authority Technical Reference Manual, Version 6.0, Oct. 1, 2017.
∆𝑘𝑊=
(〖𝑘𝑊〗_𝑏𝑎𝑠𝑒−(〖𝑘𝑊〗_(𝐸𝐸,𝑑𝑖𝑚)∗%_(𝑡𝑖𝑚𝑒,𝑑𝑖𝑚)+〖𝑘𝑊〗_(𝐸𝐸,𝑓𝑢𝑙𝑙)∗%_(𝑡𝑖𝑚𝑒,𝑓𝑢𝑙𝑙) ))∗〖𝐼𝐸〗_(𝐶,𝐷)∗𝐼𝑆𝑅∗𝐶𝐹∗𝑃𝐹
∆𝑘𝑊ℎ=
(〖𝑘𝑊〗_𝑏𝑎𝑠𝑒−(〖𝑘𝑊〗_(𝐸𝐸,𝑑𝑖𝑚)∗%_(𝑡𝑖𝑚𝑒,𝑑𝑖𝑚)+〖𝑘𝑊〗_(𝐸𝐸,𝑓𝑢𝑙𝑙)∗%_(𝑡𝑖𝑚𝑒,𝑓𝑢𝑙𝑙) ))∗〖𝐼𝐸〗_(𝐶,𝐸)∗𝐼𝑆𝑅∗〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## C_Light_Horticulture
COMMERCIAL: Horticulture Lighting
Return to TOC
UPDATE STATUS
This new measure was added in Winter 2023-2024 for the PY24 TRM V1.
MEASURE DETAILS
Description
The increasing demand for locally produced and organic food combined with the legalization of cannabis is fueling the growth of controlled environment agriculture (CEA). Several horticulture customers have recently approached Hawai'i Energy regarding incentives for energy efficiency measures. As such, Hawai'i Energy is interested in offering rebates for energy-efficient horticulture lighting measures. The horticulture lighting measure applies to non-stack, single-layer indoor grow facilities and greenhouses. Horticultural lighting provides 100% artificial lighting for the required plant growth in indoor grow facilities. In greenhouses, horticulture lighting supplements natural sunlight.
Program Criteria
Horticultural LED lighting products must be listed on the DesignLights Consortium (DLC) Horticultural Lighting Qualified Products List (Horticultural QPL, Hort QPL). Products eligible for DLC qualification must be UL listed, have a power factor of least 0.90, a photosynthetic photon efficacy (PPE) of no less than 2.3 µmole/J, a minimum rated lifetime of 50,000 hours, and a minimum warranty of 5 years. They must be electromagnetic radiation-generating devices analogous to luminaires (or fixtures) or LED lamps (integrated or non-integrated) as defined by ANSI/IES LS-1-22.
Unit of Measure
One light fixture or lamp.
Baseline Equipment
The baseline equipment includes T5 High Output (T5HO), ceramic metal halides (CMH), and high-pressure sodium (HPS) lamps and fixtures, depending on the crop and the growing stage. Only non-stack, single-layer applications in indoor grow facilities and greenhouses are eligible. Vertical (stacked with multiple layers) applications must use a custom project approach.
High Efficiency Equipment
The high-efficiency equipment is LED fixtures that meet the DLC technical requirement of a PPE of no less than 2.3 µmole/J.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr (PPF Equivalence Method)
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  |  | Source/Notes
PPFEE,i | kW_b | kW_b | kW_b | Photosynthetic Photon Flux (PPF) output of the efficient LED fixture for a specific growth phase, i. | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | User input | see Table 1 | see Table 1 | see Table 1 | µmol/s |  |  | DLC QPL1
PPEBL,i | kW_b | kW_b | kW_b | Photosynthetic Photon Efficacy (PPE) of the baseline fixture for a specific growth phase, i. | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | See Table 1 | see Table 1 | see Table 1 | see Table 1 | µmol/J |  |  | 2024 IL TRM2
CF |  |  |  | Peak demand coincidence factor | [11 empty] | 1 | [6 empty] | 2024 IL TRM2 and AEG analysis3
WHFD |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting | [11 empty] | See Table 3 | [6 empty] | 2024 IL TRM2
kWEE | kW_led | kW_led | kW_led | Wattage of the efficient LED fixture | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | User input |  |  |  | kW |  |  | DLC HORT QPL1
Qtyi | kW_led | kW_led | kW_led | Quantity of the efficient LED fixtures | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | User input
HRSyear |  |  |  | Average hours of use of horticulture lighting per year | [11 empty] | See Table 2 |  |  |  | hr/yr |  |  | 2024 IL TRM2, CPUC4, and AEG analysis5
WHFE |  |  |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting | [11 empty] | See Table 3 | [6 empty] | 2024 IL TRM2
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of LED horticulture lighting | [11 empty] | 10 |  |  |  | yrs |  |  | AEG's benchmarking of other states' and utilities' TRMs.
1 DesignLights Consortium (DLC), Qualified Product List for Horticulture Lighting. HORT QPL. <https://qpl.designlights.org/qpl/horticulture>
2 2024 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 12.0, Volume 2: Commercial and Industrial Measures, FINAL, 2023. <https://icc.illinois.gov/api/web-management/documents/downloads/public/il-trm-12/IL-TRM-Version-12.0-Volumes-1-4-Compiled-Final.pdf>
3 Hawaii sunsets range from around 5:45 pm in winter to 7:15 pm in summer. Hawaii's peak demand period is non-holiday weekdays from 5 pm to 9 pm. AEG has assumed supplemental horticulture lighting in greenhouses will primarily operate around sunrise and sunset, which coincides with evening peak demand period. Therefore, the CF equals 1 for both greenhouses and indoor grow facilities.
4 California Public Utilities Commission. 2025 Title 24, Part 6 Final CASE Report - Controlled Environment Horticulture. Revised October 2023. < https://title24stakeholders.com/wp-content/uploads/2023/10/Revised-Oct-2023-2025_T24_CASE-Report-CEH.pdf>
5 AEG has assumed the daily supplemental lighting hours in greenhouses equal the difference between the required lighting hours in indoor grow facilities, which require 100% artificial lighting, and the natural lighting hours in greenhouses.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
Table 1. Baseline Horticulture Lighting Technology and PPE
Primary Indoor Crop Practices | [6 empty] | Baseline Technology Type | [5 empty] | Baseline PPE (µmol/J) |  |  |  | Typical Baseline Wattage Range (W)
Cannabis - Propagation Stage | [6 empty] | T5HO Fixture | [5 empty] | 1.2 |  |  |  | 120-460
Cannabis - Vegetative Stage | [6 empty] | Ceramic Metal Halide | [5 empty] | 1.5 |  |  |  | 400-1,000
Cannabis - Flowering Stage | [6 empty] | High-Pressure Sodium, Double-ended | [5 empty] | 1.7 |  |  |  | 400-1,100
Leafy Greens (e.g., lettuce, spinach, kale, chard, arugula, basil) | [6 empty] | High-Pressure Sodium, Double-ended | [5 empty] | 1.7 |  |  |  | 400-1,100
Vine Crops (e.g., tomatoes, peppers, cucumbers) | [6 empty] | High-Pressure Sodium, Double-ended | [5 empty] | 1.7 |  |  |  | 400-1,100
Sources:
1. 2024 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 12.0, Volume 2: Commercial and Industrial Measures, FINAL, 2023. <https://icc.illinois.gov/api/web-management/documents/downloads/public/il-trm-12/IL-TRM-Version-12.0-Volumes-1-4-Compiled-Final.pdf>
2. Erik Runkle. Lighting Greenhouse Vegetables. December 2021, www.GPNMAG.COM. <https://www.canr.msu.edu/uploads/resources/pdfs/lightingvegetables.pdf>
3. Resource Innovation Institute. Best Practices Guide Lighting for Controlled Environmental Agriculture (CEA) Operations. March 2022. <https://resourceinnovation.org/wp-content/uploads/2022/03/RII-Lighting-BPG-2022.pdf?utm_source=CE21>
4. US Department of Energy, Energy Savings Potential of SSL in Horticulture Applications. December 2017. <https://www.energy.gov/eere/ssl/articles/energy-savings-potential-ssl-horticultural-applications>
5. California Public Utilities Commission. Market-Based Industry Standard Practice (ISP) Study of Cannabis Grow Lighting. December 21, 2021. <https://pda.energydataweb.com/api/downloads/2573/Market-Based%20ISP%20Study_Cannabis%20Lighting_Report_20211221.docx>
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28
Table 2. Annual Hours of Horticulture Lighting Use, HRSyear
Crop Type and Stage1 | [6 empty] | Harvests per Year2 |  |  |  |  | Daily Hours of Operation (hrs) | [9 empty] | Annual Hours of Operation (hrs)5
[12 empty] | Indoor grow facility 2,3 |  |  |  |  | Greenhouse 4 |  |  |  |  | Indoor grow facility |  |  |  |  | Greenhouse
Cannabis - Propagation Stage | [6 empty] | 5 |  |  |  |  | 24 |  |  |  |  | 16 |  |  |  |  | 8400 |  |  |  |  | 5600
Cannabis - Vegetative Stage | [6 empty] | 5 |  |  |  |  | 18 |  |  |  |  | 10 |  |  |  |  | 6300 |  |  |  |  | 3500
Cannabis - Flowering Stage | [6 empty] | 5 |  |  |  |  | 12 |  |  |  |  | 4 |  |  |  |  | 4200 |  |  |  |  | 1400
Leafy Greens (e.g., lettuce, spinach, kale, chard, arugula, basil) | [6 empty] | 8 |  |  |  |  | 18 |  |  |  |  | 10 |  |  |  |  | 6140 |  |  |  |  | 3410
Vine Crops (e.g., tomatoes, peppers, cucumbers) | [6 empty] | 4 |  |  |  |  | 12 |  |  |  |  | 4 |  |  |  |  | 4240 |  |  |  |  | 1410
1 AEG's analysis indicates cannabis, leafy greens, and vine crops are popular crops grown in non-stack, single-layer indoor growth facilities and greenhouses.
2 California Public Utilities Commission. 2025 Title 24, Part 6 Final CASE Report - Controlled Environment Horticulture. Revised October 2023. https://title24stakeholders.com/wp-content/uploads/2023/10/Revised-Oct-2023-2025_T24_CASE-Report-CEH.pdf
3 2024 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 12.0, Volume 2: Commercial and Industrial Measures, FINAL, 2023. <https://icc.illinois.gov/api/web-management/documents/downloads/public/il-trm-12/IL-TRM-Version-12.0-Volumes-1-4-Compiled-Final.pdf
4 Hawaii's sunrise ranges from about 5:45 am in summer to about 7 am in winter, while Hawaii's sunsets range from around 5:45 pm in winter to 7:15 pm in summer. AEG has assumed that natural daylight is 8 hours in greenhouses in Hawaii, which requires supplementing with artificial lighting to achieve the necessary photoperiod for plant growth.
5 AEG determined the annual hours of operation by multiplying daily operational hours by 350 days per year for cannabis, 340 days for leafy greens, and 355 days per year for tomatoes, assuming three downtime days between each harvest cycle.
Table 3. Interactive Cooling Effects, WHFD and WHFE
Facility Type | [6 empty] | WHDD | [5 empty] | WHFE
Indoor grow facility or greenhouse with cooling | [6 empty] | 1.22 | [5 empty] | 1.21
Indoor grow facility or greenhouse without cooling | [6 empty] | 1 | [5 empty] | 1
Source: Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 12.0, Volume 2: Commercial and Industrial Measures, FINAL, 2023. <https://icc.illinois.gov/api/web-management/documents/downloads/public/il-trm-12/IL-TRM-Version-12.0-Volumes-1-4-Compiled-Final.pdf>
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
Type of Non-Stack (Single Layer) Facility
Greenhouse
Is Grow Space Cooled?
No
Enter Crop Type and Stage
Vine Crops (e.g., tomatoes, peppers, cucumbers)
[5 empty] | PPEBL = |  |  | 1.7 | [5 empty] | HRSyear = | 1410 |  |  |  |  | WHDD= | 1 |  |  |  |  | WHDE= | 1
Enter PPF of energy-efficient LED horticulture lighting fixture
[5 empty] | 1828 | [5 empty] | µmol/s
Enter wattage of energy-efficient LED horticulture lighting fixture
[5 empty] | 1000 | [5 empty] | W
Enter quantity of energy-efficient LED horticulture lighting fixture
110
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Vine Crops (e.g., tomatoes, peppers, cucumbers) | [7 empty] | 8.282 | [7 empty] | 11678.12 | [7 empty] | 116781.2
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | AEG's 2024 Analysis File named "PY24 TRM - Commercial Horticulture Lighting - Analysis File."
• | California Public Utilities Commission. Market-Based Industry Standard Practice (ISP) Study of Cannabis Grow Lighting. December 21, 2021. <https://pda.energydataweb.com/api/downloads/2573/Market-Based%20ISP%20Study_Cannabis%20Lighting_Report_20211221.docx>
• | California Statewide Codes and Standards Enhancement (CASE) Program. 2025 California Energy Code. Controlled Environment Horticulture. Final CASE Report. Revised October 2023. <https://title24stakeholders.com/wp-content/uploads/2023/10/Revised-Oct-2023-2025_T24_CASE-Report-CEH.pdf>
• | DesignLights Consortium (DLC), Technical Requirements for LED-Based Horticulture Lighting Version 3.0. Effective date: March 31, 2023. <https://www.designlights.org/dlc_hort-technical-requirements-v3-0_03312023/>
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 12.0, Volume 2: Commercial and Industrial Measures, FINAL, 2023. <https://icc.illinois.gov/api/web-management/documents/downloads/public/il-trm-12/IL-TRM-Version-12.0-Volumes-1-4-Compiled-Final.pdf>
• | New Jersey Board of Utilities. New Jersey 2023 Triennial Technical Reference Manual For 2024 Filings. 5/22/2023. <https://njcepfiles.s3.amazonaws.com/QO23030150-+Tri2+EE1+%2B+EE2-+Order+Attch+C-+TRM.pdf>
• | Resource Innovation Institute. Best Practices Guide Lighting for Controlled Environment Agriculture (CEA) Operations. March 2022. <https://resourceinnovation.org/wp-content/uploads/2022/03/RII-Lighting-BPG-2022.pdf?utm_source=CE21>
• | US Department of Energy, Energy Savings Potential of SSL in Horticulture Applications. December 2017. <https://www.energy.gov/eere/ssl/articles/energy-savings-potential-ssl-horticultural-applications>
• | Wisconsin Focus on Energy. 2023 Energy Technical Reference Manual. January 3, 2023. <https://assets.focusonenergy.com/production/inline-files/Focus_on_Energy_2023_TRM.pdf >
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒= ∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
∆𝑘𝑊ℎ=〖𝑄𝑡𝑦〗_𝑖∗(( (𝑃𝑃𝐹𝐸𝐸,𝑖)/(𝑃𝑃𝐸𝐵𝐿,𝑖 𝑥 1000))−"kWEE,i " )∗〖𝐻𝑅𝑆〗_𝑦𝑒𝑎𝑟∗〖𝑊𝐻𝐹〗_𝐸
∆𝑘𝑊=(( (𝑃𝑃𝐹𝐸𝐸,𝑖)/(𝑃𝑃𝐸𝐵𝐿,𝑖 𝑥 1000))−"kWEE,i " )∗𝐶𝐹∗〖𝑊𝐻𝐹〗_𝐷

## C_Light_Energy Advantage
COMMERCIAL: Energy Advantage
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. This update revises the language and algorithms to reflect Hawaii state requirements, such as the fluorescent lighting ban.
MEASURE DETAILS
Description
The Energy Advantage program provides qualifying participants with lighting upgrades at significantly reduced prices. This program falls under Hawai'i Energy's Business Hard to Reach (BHTR) program and is sometimes referred to as the Small Business Direct Install Lighting (SBDIL) program. It uses a software tool referred to as "Amplify" for tracking projects and calculating energy and demand savings.
Program Criteria
Qualifying participants are as follows:
| • | Restaurants.
| • | Small businesses receiving electric service under a commercial rate schedule with demand less than or equal to 30 kilowatts (kW) per month. Master-metered businesses must receive sign-off from the utility account holder.
| • | Common areas located in an eligible multi-tenant affordable housing property. Eligible multi-tenant affordable housing projects are owned by private, non-profit or government entities, developed with funding or support from federal, state or county resources (Source: Affordable Housing Inventory). This may include Elderly Housing, Public Housing, or Section 8 voucher approved housing.
| • | A 501(c)(3) nonprofit organization.
See <https://hawaiienergy.com/for-businesses/energy-advantage-program> for more information.
The replacement lighting must be on the Consortium for Energy Efficiency's (CEE's) most recent Commercial Lighting Qualifying Products List, have an ENERGY STAR label, or be on DesignLights Consortium's Qualified Product List (DLC QPL).
In the case of the delamping measure, the replacement lamp (with an added reflector as needed) must be of sufficient brightness to meet the requirements of the space. For delamping, the lamp and lamp holder ("tombstone") must be permanently removed.
Prior to installation of the lighting upgrades, participants must sign an Energy Advantage Program Project Commitment Letter, which states the following: “I have been given an on-site demonstration by (Contractor) of the replacement lighting that I will be receiving, and it appears that the lighting level, intensity, and color will be a suitable replacement for the lighting currently in place.”
Unit of Measure
Custom number of lamps/fixtures.
Baseline Equipment
All early retirement projects require a dual baseline. The first baseline is the pre-existing lighting fixtures and controls. The pre-existing equipment is assumed to have a remaining useful life (RUL) of one-third of the Effective Useful Life (EUL) of the pre-existing lamp fixtures and controls. The second baseline must comply with the federal and state requirements in effect at the end of the pre-existing equipment's RUL. Only lighting systems that are in working order at the time of the replacement qualify for early retirement. If the pre-existing lighting cannot be verified to be in working order, a replace on burnout (ROB) baseline must be used.
Note: Early retirement of fluorescent lighting represents a special dual baseline case since fluorescent lighting is now banned in Hawaii. The lifetime savings still use the RUL of the pre-existing fluorescent lighting for the first baseline. However, after the RUL, the baseline would transition to LED lighting, so there would be no savings during the second baseline period.
High Efficiency Equipment
The high efficiency case is an upgraded lighting system that meets program criteria and exceeds minimum federal and state requirements.
SAVINGS DESCRIPTION
The following documents how savings are calculated for the Energy Advantage projects within Amplify.
Each Energy Advantage application contains one or more Spaces, which represent different parts of a building affected by a project. Within each space the user selects the existing lighting equipment (e.g. base case) and the new lighting equipment (e.g. enhanced case) from the Amplify database, which has wattage values sourced from the product’s specification. Direct install or other early retirement projects that use pre-existing equipment for the baseline must use a dual baseline approach for lifetime savings to account for recent and forthcoming changes in federal and state requirements.
In addition, Amplify does allow for the possibility that each space may have its own unique operating schedule.
The Hours of Use per year (HOUyear)--which has also been referred to as Equivalent Full Load Hours (EFLH) for the Energy Advantage program--for each Space is calculated based on a user-entered start time and end time for each day of the week, modified by a user-entered set of holidays during which the building is assumed to be inactive. The specific holidays do not matter since they are a quantity (# Holidays * Hours/Day) used to adjust an annual total. The annual hours of use value can vary for different measures within the same Energy Advantage application due to various operating schedules entered per space.
When a user does not enter values for hours of operation, the savings calculation should use the operational hours from the Commercial General Lighting measure. (See Table 5 in the "C_Light_General" sheet.)
ALGORITHMS
Hours of Use per Year, hr/yr
(1)
Where: Hoursday of week is evaluated for each day of the week and is equal to:
WHEN End Hours > Start Hours THEN End Hours - Start Hours
WHEN End Hours < Start Hours THEN End Hours - Start Hours + 24
WHEN End Hours = Start Hours THEN 24
First Baseline Peak Demand Reduction, kW
(2)
Second Baseline Peak Demand Reduction, kW
(3)
First Baseline Annual Energy Savings, kWh/yr
(4)
Second Baseline Annual Energy Savings, kWh/yr
(5)
Lifetime Energy Savings, kWh
(6)
Remaining Useful Life
(7)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit | Source/Notes
HOUyear |  |  |  | Average hours of use per year | [11 empty] | Calculated. See Eq. 1. |  |  |  | hr/yr | Calculated with Equation 1 based on user inputs for operating hours and holidays. For default HOUyear values, see Table 5 of "C_Light_General" sheet.
kWpre | kW_b | kW_b | kW_b | Wattage of pre-existing lighting fixture | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | wattage of the baseline lamp | User input | see Table 1 | see Table 1 | see Table 1 | kW
kWFed/State | kW_b | kW_b | kW_b | Wattage of a comparable lighting fixture that meets minimum federal and state requirements | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | User input | see Table 1 | see Table 1 | see Table 1 | kW | Must meet federal and state requirements in effect as of end of the pre-existing fixture's RUL.
kWEE | kW_led | kW_led | kW_led | Wattage of installed energy efficient lighting fixture | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | wattage of the proposed efficient lamp | User input | see Table 1 | see Table 1 | see Table 1 | kW | Must meet program criteria.
#fixturepre |  |  |  | Number of pre-existing fixtures | [11 empty] | User input | see Table 1 | see Table 1 | see Table 1 | -
#fixturepost |  |  |  | Number of installed efficient fixtures | [11 empty] | User input | see Table 1 | see Table 1 | see Table 1 | -
RTRpre |  |  |  | Runtime reduction factor from pre-existing lighting controls | [11 empty] | User input | see Table 1 | see Table 1 | see Table 1 | - | Default for occupancy sensors is RTR = 0.24. (See "C_Light_Occupancy Sensor" sheet.)
RTRFed/State |  |  |  | Runtime reduction factor from lighting controls that meet minimum federal and state requirements | [11 empty] | User input | see Table 1 | see Table 1 | see Table 1 | - | Default for occupancy sensors is RTR = 0.24. (See "C_Light_Occupancy Sensor" sheet.)
RTRpost |  |  |  | Runtime reduction factor from installed lighting controls | [11 empty] | User input | see Table 1 | see Table 1 | see Table 1 | - | Default for occupancy sensors is RTR = 0.24. (See "C_Light_Occupancy Sensor" sheet.)
CF |  |  |  | Peak demand coincidence factor | [11 empty] | User input | see Table 1 | see Table 1 | see Table 1 | - | For default CF values, see Table 3 of "C_Light_General" sheet.
IEC,D |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting | [11 empty] | User input |  |  |  | - | For default IEC,D values, see Table 4 of "C_Light_General" sheet.
IEC,E |  |  |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting | [11 empty] | User input |  |  |  | - | For default IEC,D values, see Table 4 of "C_Light_General" sheet.
EULpre-existing | Measure Life | Measure Life | Measure Life | Effective useful life of pre-existing lighting | [11 empty] | User input |  |  |  | yrs | Calculated by dividing rated lamp life by HOUyear and setting upper bound EUL = 25 yr and lower bound EUL = 1 yr.
RUL | Measure Life | Measure Life | Measure Life | Remaining useful life of pre-existing lighting | [11 empty] | Calculated |  |  |  | yrs | Calculated with Equation 7 based on EULpre-existing.
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of efficient lighting | [11 empty] | User input |  |  |  | yrs | Calculated by dividing rated lamp life by HOUyear and setting upper bound EUL = 25 yr and lower bound EUL = 1 yr.
KEY VARIABLES FROM AMPLIFY TOOL
A number of variables are tracked in the Amplify database. As of PY18, the key variables used to estimate demand and energy savings for a given Rebate ID are listed below:
Amplify Variable | [12 empty] | Description
RebateId | [12 empty] | Rebate ID
Equipment_Id | [12 empty] | Equipment ID; there may be more than one equipment ID per rebate
predominant_space_type | [12 empty] | The predominant space type, which generally maps to building types
Application_Status__c | [12 empty] | Status of the application (e.g., check mailed, cancelled)
Is_Exterior | [12 empty] | Indicator for exterior lighting
area_cooling_description | [12 empty] | Description of type of cooling in the space
pre_control_factor_type | [12 empty] | Type of pre-existing controls
post_control_factor_type | [12 empty] | Type of installed controls
pre_fixture_wattage | [12 empty] | Pre-existing fixture wattage, kWpre/1000
pre_fixture_quantity | [12 empty] | Pre-existing fixture quantity, #fixturepre
post_fixture_wattage | [12 empty] | Installed fixture wattage, kWpost/1000
post_fixture_quantity | [12 empty] | Installed fixture quantity, #fixturepost
eflh | [12 empty] | Annual hours of use, HOUyear
Coincidence_factor | [12 empty] | Coincidence factor, CF
Interactive_Factor_Value_Demand | [12 empty] | Interactive effects factor for demand minus 1, IEC,D - 1
Interactive_Factor_Value_Energy | [12 empty] | Interactive effects factor for energy minus 1, IEC,E - 1
pre_control_factor | [12 empty] | Runtime reduction factor for pre-existing controls, RTRpre
post_control_factor | [12 empty] | Runtime reduction factor for installed controls, RTRpost
Additional variables will be needed to estimate savings using the dual baseline approach, including kWFed/State, RTRFed/State, EULpre-existing, and EULEE.
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Multiple Lighting Measures - Analysis File."
• | AEG's analysis files named "PY24 TRM - Commercial Energy Advantage - Analysis File." "Mid-year PY22 TRM - Energy Advantage - Analysis File," "AEG HPUC Energy Advantage - Analysis File" (developed for PY20 TRM), and "AEG HPUC Update of Com-Lighting Measures - Analysis file" (developed for PY19 TRM).
• | Tetra Tech's summary of the PY18 Energy Advantage verification process. Filename: "Energy Advantage Lighting Verification Methodology_30Dec2019 V1."
• | Hawai'i Energy's Energy Advantage webpage, <https://hawaiienergy.com/for-businesses/energy-advantage-program>, accessed Jan. 2, 2020.
〖∆𝑘𝑊〗_1𝑠𝑡=[(〖𝑘𝑊〗_𝑝𝑟𝑒∗〖# 𝑓𝑖𝑥𝑡𝑢𝑟𝑒〗_𝑝𝑟𝑒 )∗(1−〖𝑅𝑇𝑅〗_𝑝𝑟𝑒 )−
(𝑘𝑊_𝑝𝑜𝑠𝑡∗〖# 𝑓𝑖𝑥𝑡𝑢𝑟𝑒〗_𝑝𝑜𝑠𝑡 )∗(1−〖𝑅𝑇𝑅〗_𝑝𝑜𝑠𝑡 )]∗𝐶𝐹∗〖𝐼𝐸〗_(𝐶,𝐷)
𝑅𝑈𝐿=〖1∕3∗𝐸𝑈𝐿〗_(𝑝𝑟𝑒−𝑒𝑥𝑖𝑠𝑡𝑖𝑛𝑔)
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒,)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(〖𝐸𝑈𝐿〗_𝐸𝐸−𝑅𝑈𝐿)
〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟=
(∑_(𝑖=1)^7▒〖(〖𝐻𝑜𝑢𝑟𝑠〗_(𝑑𝑎𝑦 𝑜𝑓 𝑤𝑒𝑒𝑘))〗_𝑖 )∗(52.14 𝑤𝑒𝑒𝑘𝑠)/𝑦𝑒𝑎𝑟−#𝐻𝑜𝑙𝑖𝑑𝑎𝑦𝑠∗𝐴𝑣𝑔. 𝑂𝑝𝑒𝑟𝑎𝑡𝑖𝑛𝑔 〖𝐻𝑜𝑢𝑟𝑠〗_𝑑𝑎𝑦
〖∆𝑘𝑊〗_2𝑛𝑑=[(〖𝑘𝑊〗_(𝐹𝑒𝑑/𝑠𝑡𝑎𝑡𝑒)∗〖# 𝑓𝑖𝑥𝑡𝑢𝑟𝑒〗_𝑝𝑟𝑒 )∗(1−〖𝑅𝑇𝑅〗_(𝐹𝑒𝑑/𝑆𝑡𝑎𝑡𝑒) )−
(𝑘𝑊_𝑝𝑜𝑠𝑡∗〖# 𝑓𝑖𝑥𝑡𝑢𝑟𝑒〗_𝑝𝑜𝑠𝑡 )∗(1−〖𝑅𝑇𝑅〗_𝑝𝑜𝑠𝑡 )]∗𝐶𝐹∗〖𝐼𝐸〗_(𝐶,𝐷)
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=[(〖𝑘𝑊〗_𝑝𝑟𝑒∗〖# 𝑓𝑖𝑥𝑡𝑢𝑟𝑒〗_𝑝𝑟𝑒 )∗(1−〖𝑅𝑇𝑅〗_𝑝𝑟𝑒 )−
(𝑘𝑊_𝑝𝑜𝑠𝑡∗〖# 𝑓𝑖𝑥𝑡𝑢𝑟𝑒〗_𝑝𝑜𝑠𝑡 )∗(1−〖𝑅𝑇𝑅〗_𝑝𝑜𝑠𝑡 )]∗〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟∗〖𝐼𝐸〗_(𝐶,𝐸)
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=[(〖𝑘𝑊〗_(𝐹𝑒𝑑/𝑆𝑡𝑎𝑡𝑒)∗〖# 𝑓𝑖𝑥𝑡𝑢𝑟𝑒〗_𝑝𝑟𝑒 )∗(1−〖𝑅𝑇𝑅〗_(𝐹𝑒𝑑/𝑆𝑡𝑎𝑡𝑒) )−
(𝑘𝑊_𝑝𝑜𝑠𝑡∗〖# 𝑓𝑖𝑥𝑡𝑢𝑟𝑒〗_𝑝𝑜𝑠𝑡 )∗(1−〖𝑅𝑇𝑅〗_𝑝𝑜𝑠𝑡 )]∗〖𝐻𝑂𝑈〗_𝑦𝑒𝑎𝑟∗〖𝐼𝐸〗_(𝐶,𝐸)

## C_PlugProcess_ASH Control
COMMERCIAL: Anti-Sweat Heater Controls
Return to TOC
MEASURE DETAILS
Description
Anti-sweat heater controls sense the relative humidity in the air outside of a refrigerated display case and reduces or shuts off the glass door and/or frame anti-sweat heaters based on dew point temperature. Heat generated by an ASH is also load on the display case refrigeration system. Thus, reduction in ASH duty cycle will also have an interactive effect on the refrigeration energy. As a result, compressor run time and energy consumption are reduced.
Program Criteria
1. Pre-notification before project begins. 2. Controls must be installed on all doors of the refrigerator or freezer. 3. The following situations DO NOT qualify for this incentive: a. New refrigerators and freezers b. Refrigerators and freezers with existing controls being replaced with new controls c. Walk-in refrigerators and freezers manufactured after January 1, 2009 4. The rebate is awarded based on the total linear feet of the doors controlled by Anti-Sweat Heater Controls and incentivized at a rate of $40 per linear foot.
Unit of Measure
Linear feet
Baseline Equipment
No anti-sweat controls installed.
High Efficiency Equipment
Anti-sweat control installed.
ALGORITHMS
|  |  |  | annual Peak kW savings from ASH per door | =SVG_d,ash * W_b,door/1000 * CF
|  |  |  | annual kWh savings from ASH | =SVG_d,ash * W_b,door/1000 * HRS_ash
|  |  |  | annual kW savings from Compressor | =SVG_cooling / EER / 1000* CF
|  |  |  | annual kWh savings from Compressor | =SVG_cooling / EER / 1000 * HRS_comp
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Value |  |  | Unit | Notes
SVG_d,ash |  | ASH demand savings factor |  |  | 50% |  |  | - | SDG&E Statewide Express Efficiency Program - https://www.sdge.com/sites/default/files/regulatory/Express%20and%20SBS%20Workpapers.pdf
SVG_d,comp |  | Compressor demand savings factor |  |  | 17.5% |  |  | - | SDG&E Statewide Express Efficiency Program - https://www.sdge.com/sites/default/files/regulatory/Express%20and%20SBS%20Workpapers.pdf
SVG_cooling |  | =BaseWatts/door*SVG_d_Comp |  |  | - |  |  | W
Watt_b,door |  | Baseline door heater power |  |  | 200 |  |  | W | SDG&E Statewide Express Efficiency Program - https://www.sdge.com/sites/default/files/regulatory/Express%20and%20SBS%20Workpapers.pdf
Btu_b,door |  | Baseline door heater power (3.413 Btu/h per W) |  |  | 682.6 |  |  | Btu/hr | SDG&E Statewide Express Efficiency Program - https://www.sdge.com/sites/default/files/regulatory/Express%20and%20SBS%20Workpapers.pdf
EER |  | Compressor energy efficiency ratio |  |  | 5.43 |  |  | Btu/hr/W | SDG&E Statewide Express Efficiency Program - https://www.sdge.com/sites/default/files/regulatory/Express%20and%20SBS%20Workpapers.pdf
HRS_ash |  | Hours of base ASH operation per year |  |  | 8760 |  |  | hrs
HRS_comp |  | Compressor run time |  |  | 5700 |  |  | hrs | SDG&E Statewide Express Efficiency Program - https://www.sdge.com/sites/default/files/regulatory/Express%20and%20SBS%20Workpapers.pdf
RH_avg |  | Typical Store relative humidity |  |  | 45% |  |  | - | SDG&E Statewide Express Efficiency Program - https://www.sdge.com/sites/default/files/regulatory/Express%20and%20SBS%20Workpapers.pdf
CF |  | Coincidence factor |  |  | 0.85 |  |  | -
Measure Life |  | Expected duration of savings |  |  | 12 |  |  | yrs | SDG&E Statewide Express Efficiency Program - https://www.sdge.com/sites/default/files/regulatory/Express%20and%20SBS%20Workpapers.pdf
SAVINGS
Annual Peak kW savings from ASH |  |  |  | 0.085 |  |  | kW
Annual kWh savings from ASH |  |  |  | 876 |  |  | kWh
SVG_cooling |  |  |  | 119.455 |  |  | Btu/hr/door
Annual Peak kW savings from Compressor |  |  |  | 0.018699 |  |  | kW
Annual kWh savings from Compressor |  |  |  | 125.3948 |  |  | kWh
Total Cooling Savings: |  |  |  | 119.455 |  |  | Btu/hr/door
Total Peak Power Savings: |  |  |  | 0.1037 |  |  | kW/door
Total Annual Energy Savings: |  |  |  | 1001.3948 |  |  | kWh/door
Per Linear Foot calculation:
Door width |  |  |  | 35 |  |  | inches
|  |  |  | 12 |  |  | inches/ft
Bottom door length |  |  |  | 2.9167 |  |  | feet
Peak kW savings per linear foot |  |  |  | 0.036 |  |  | kW/ft
Annual kWh savings per linear foot |  |  |  | 343.34 |  |  | kWh/ft
Measure Name |  |  | Peak Demand Savings |  |  | Annual Energy Savings
ASH Control |  |  | 0.036 |  |  | 343.34

## C_PlugProcess_Vending Miser
COMMERCIAL: Vending Miser
Return to TOC
MEASURE DETAILS
Description
Controls can significantly reduce the energy consumption of vending machine lighting and refrigeration systems. Qualifying controls must power down these systems during periods of inactivity but, in the case of refrigerated machines, must always maintain a cool product that meets customer expectations. This measure applies to refrigerated beverage vending machines, non-refrigerated snack vending machines, and glass front refrigerated coolers. This measure should not be applied to ENERGY STAR® qualified vending machines, as they already have built-in controls.
Program Criteria
Vending machine must be refrigerated and/or employ an active lamp.
Unit of Measure
One control unit
Baseline Equipment
The baseline efficiency case is a standard efficiency refrigerated beverage vending machine, non-refrigerated snack vending machine, or glass front refrigerated cooler without a control system capable of powering down lighting and refrigeration systems during periods of inactivity.
High Efficiency Equipment
The high efficiency case is a standard efficiency refrigerated beverage vending machine, non-refrigerated snack vending machine, or glass front refrigerated cooler with a control system capable of powering down lighting and refrigeration systems during periods of inactivity.
ALGORITHMS
ΔE |  |  | = P * HRS * SVG
ΔP |  |  | = ΔE / HRS
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Value | Unit | Notes
ΔE |  | Annual energy reduction |  |  | Calculated | kWh
ΔP |  | Peak power demand reduction |  |  | Calculated | kW
P |  | Rated power of connected equipment |  |  | Table | kW
HRS |  | Annual operating hours |  |  | 8760 | hrs | 24 hrs/day, 7 days/wk
SVG |  | Savings factor for connected equipment |  |  | Table | %
Measure Life |  | Expected duration of savings |  |  | 8 | yrs
SAVINGS
Measure Name |  |  |  | Peak Demand Savings | Annual Energy Savings
Refrigerated beverage vending maching (cans or bottles) |  |  |  | 0.184 | 1612
Refrigerated |  |  |  | 0.124 | 1086
Non-refrigerated snack vending machine |  |  |  | 0.044 | 387
All (Average) |  |  |  | 0.117 | 1028.33

## C_PlugProcess_Water Cooler Tmr
COMMERCIAL: Water Cooler Timer
Return to TOC
UPDATE STATUS
This measure is designated "inactive" as of PY23. Before it can be reinstated for a future program year, a full update of the savings approach will be needed.
MEASURE DETAILS
Description
Similar to the timers you might use to control lights in your home, plug-in appliance timers allow you to pre-program the times that various appliances in your business are turned on and drawing electricity. So you could pre-program the water cooler so it turns on one hour before the office opens and turns off again after everyone leaves.
Program Criteria
Timers must be digital, include an internal rechargeable battery, and 7 day programmable on/off settings.
Unit of Measure
One timer unit
Baseline Equipment
No timer
High Efficiency Equipment
Timer installed
ALGORITHMS
SAVINGS
It is assumed that half of all water coolers are ENERGY STAR and half are not:
· 50% ENERGY STAR
· 50% Conventional
It is assumed that half of all water coolers are cold only and half are hot + cold dispenser:
· 50% Cold Only
· 50% Hot + Cold
The energy savings figure will be based on the average of the above-mentioned percentages.
Persistence Factor = 90%
Energy Savings = 225 x 90% = 202.5 kWh/year
Taking a conservative approach, the demand savings will based on the following calculation and methodology:
Demand Savings = 225 kWh/year divided by 8760 hrs/year = 0.026 kW
Coincidence Factor = 75%
Note: Based on utilization of 3 of the 4 peak hours (6PM-9PM). 5PM-6PM is not counted since most offices close at 5PM and the timer should be set to turn off cooler 1 hour after office closes which is 6PM.
Coincidence Demand Savings = 0.026 kW x .75 = 0.020 kW
Persistence = 90% (10% of people will disconnect)
Peak Demand Savings = 0.020 kW x .90 = 0.018 kW
Measure Name |  | Peak Demand Savings | Annual Energy Savings
Water Cooler Timer |  | 0.018 | 202.5

## C_PlugProcess_Case Night Cover
COMMERCIAL: Case Night Cover
Return to TOC
MEASURE DETAILS
Description
Installation of night covers on existing, open-type refrigerated display cases to reduce extra cooling load caused by infiltration and radiation. Unit of measure is 1 foot of case opening width to be covered.
Program Criteria
Project pre-approval required.
Unit of Measure
Linear foot of cooler space
Baseline Equipment
The baseline efficiency case is the annual operation of open-display cooler cases
High Efficiency Equipment
The high-efficiency case is the use of night covers to protect the exposed areas of display cooler cases during unoccupied store hours.
ALGORITHMS
|  |  | peak kW savings/ft | = 0*
|  |  | annual kWh savings/ft | = SVG_kW * HRS
* Assumes covers are used during off peak hours--midnight to 6 am
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  |  | Value | Unit | Notes
SVG_kW |  | Reduced power use of refrigerated display case |  |  |  | Table 1 | - | Original factors from Southern Cal Edison 1997 paper
HRS |  | Hours per year that cases are covered |  |  |  | 2407 | hrs | 8760 minus (average of 45 Hawai‘i supermarkets open hours)
Measure Life |  | Expected duration of savings |  |  |  | 5 | yrs | DEER 2014
Table 1. Power Savings Factor for Refrigerated Cases |  |  |  |  | kW/ft1
Low Temp (less than 0 F) |  |  |  |  | 0.03
Medium Temp (0F to 30 F) |  |  |  |  | 0.02
High Temp (35 F to 55 F) |  |  |  |  | 0.01
Average |  |  |  |  | 0.02
Source: Pennsylvania Technical Reference Manual, Errata Update February 2017, p.403,
http://www.puc.pa.gov/filing_resources/issues_laws_regulations/act_129_information/technical_reference_manual.aspx
1 Google search of refrigerated display cases yields a range of typical sizes--4', 5', 6', 6.5', 8'.
SAVINGS
Measure Name |  |  |  | Peak Demand Savings |  | Annual Energy Savings
Case Night Cover |  |  |  | 0 |  | 48.14

## C_PumpMotor_VFD Booster Pump
COMMERCIAL: VFD Booster Pump
Return to TOC
UPDATE STATUS
Updated in Fall 2018 for PY19 TRM.
MEASURE DETAILS
Description
The purpose of this measure is to reduce energy consumption through more efficient domestic water booster systems by installing a VFD with or without also reducing pump HP. Pump improvements can be done to optimize the design and control of water pumping systems.
Program Criteria
• Booster pump applications require pre-notification before equipment is purchased and installed. • The new Booster Pump System’s total horsepower must be equal to or less than that of the existing system. • The system horsepower reduction must be between 0 to 129 hp. For projects with greater than 129 hp, please contact the program. Booster pump applications do not apply to new construction.
Unit of Measure
One pump.
Baseline Equipment
Assumed to be a non-optimized existing pumping system with a constant speed motor. Baseline pumps are assumed to run 60% of the time.
High Efficiency Equipment
Assumed to be an optimized pumping system meeting applicable program efficiency requirements. The proposed booster pump system must be a more efficient design than the existing system (i.e. Installed with VFD controls). All pump motors must meet NEMA Premium Efficiency standards. As in the base case, enhanced pumps are assumed to run 60% of the time. Savings result from two aspects: (1) reduced horsepower and (2) reduced speed on the motor due to VFD controls.
ALGORITHMS
Pump Horsepower Reduction
Annual Energy Savings, kWh/yr per hp
(1)
Peak Demand Reduction, kW per hp
(2)
Lifetime Energy Savings, kWh per hp
(3)
VFD Installation
Annual Energy Savings, kWh/yr per hp
(4)
Peak Demand Reduction, kW per hp
(5)
Lifetime Energy Savings, kWh per hp
(6)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  | Value | Unit | Source/Notes
ΔkWh per hp |  |  | Annual energy savings per horsepower |  | Calculated | kWh/yr/hp
ΔkW per hp |  |  | Peak demand reduction per horsepower |  | Calculated | kW/hp
Constant |  |  | Conversion from horsepower to kW |  | 0.746 | kW/hp
Hours |  |  | Operating hours |  | 8760 | hrs | No change from PY18 TRM
LF |  |  | Loading factor - % of time pump actually operates |  | 60% | - | No change from PY18 TRM
CF |  |  | Coincidence factor |  | 0.5 | - | No change from PY18 TRM
AFCS |  |  | Adjustment factor for constant-speed pump - accounts for pumping system efficiency and load profile |  | 0.89852 | - | AEG derived the value from the Regional Technical Forum's (RTF) original analysis contained in the unit energy savings measure workbook for Efficient Pumps
AFVS |  |  | Adjustment factor for variable-speed pump - accounts for pumping system efficiency and load profile |  | 0.67123 | - | AEG derived the value from the Regional Technical Forum's (RTF) original analysis contained in the unit energy savings measure workbook for Efficient Pumps
EUL |  |  | Effective useful life of measure |  | 15 | yrs | No change from PY18 TRM; EUL was verified during AEG's 2018 benchmarking
SAVINGS
Source of Savings |  |  |  | Peak Demand Savings | Annual Energy Savings |  |  | Lifetime Energy Savings
HP Reduction |  |  |  | 0.335 | 3523.08 |  |  | 52846.2
VFD Installation |  |  |  | 0.085 | 891.2 |  |  | 13368
RESOURCES
• | AEG's 2018 Analysis File titled "AEG HPUC Update of Com Booster Pump VFD - Analysis File."
• | DOE, Technical Support Document: Energy Efficiency Program for Consumer Products and Commercial and Industrial Equipment: Pumps, U.S. Department of Energy, Washington DC: December 2015. Available for download here: https://www.regulations.gov/document?D=EERE-2011-BT-STD-0031-0056.
• | Regional Technical Forum. Efficient Pumps - Unit Energy Savings Measure Workbook, Version 1.1. Northwest Power and Conservation Council. June 14, 2017. Spreadsheet. Available online at: https://rtf.nwcouncil.org/measure/efficient-pumps.
∆𝑘𝑊ℎ 𝑝𝑒𝑟 ℎ𝑝=0.746 𝑘𝑊/ℎ𝑝∗𝐻𝑜𝑢𝑟𝑠∗𝐿𝐹∗〖𝐴𝐹〗_𝐶𝑆
∆𝑘𝑊 𝑝𝑒𝑟 ℎ𝑝=0.746 𝑘𝑊/ℎ𝑝∗𝐶𝐹∗〖𝐴𝐹〗_𝐶𝑆
∆𝑘𝑊ℎ 𝑝𝑒𝑟 ℎ𝑝=0.746 𝑘𝑊/ℎ𝑝∗𝐻𝑜𝑢𝑟𝑠∗𝐿𝐹∗(〖𝐴𝐹〗_𝐶𝑆−〖𝐴𝐹〗_𝑉𝑆 )
∆𝑘𝑊 𝑝𝑒𝑟 ℎ𝑝=0.746 𝑘𝑊/ℎ𝑝∗𝐶𝐹∗(〖𝐴𝐹〗_𝐶𝑆−〖𝐴𝐹〗_𝑉𝑆 )
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒 𝑝𝑒𝑟 ℎ𝑝=∆𝑘𝑊ℎ 𝑝𝑒𝑟 ℎ𝑝∗𝐸𝑈𝐿
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒 𝑝𝑒𝑟 ℎ𝑝=∆𝑘𝑊ℎ 𝑝𝑒𝑟 ℎ𝑝∗𝐸𝑈𝐿

## C_PumpMotor_ECM
COMMERCIAL: Electronically Commutated Motor
Return to TOC
UPDATE STATUS
Updated in Winter 2023-2024 for the PY24 TRM. The update included a complete review of the commercial electronically commutated motor (ECM) measure, clarifying the measure's scope, clarifying eligibility criteria, removing the requirement for integrated controls, updating the savings estimation approaches, and adding deemed savings tables for multiple ECM applications.
MEASURE DETAILS
Description
This measure is the replacement of a fractional horsepower (≤1 hp) standard efficiency shaded pole (SP) motor with a high efficiency electronically commutated motor (ECM) in commercial refrigeration and commercial HVAC applications. This measure covers the following applications:
| • | Evaporator fan motors for walk-in coolers and freezers, with and without motor control
| • | Evaporator fan motors for reach-in cooler and freezer display cases
| • | Compressor and condenser / condensing unit fan motors in refrigeration applications
| • | Motors in fan coil units (FCUs) in HVAC applications
Program Criteria
| 1. | Evaporator fan motor replacements for walk-in cooler and freezer systems manufactured after January 1, 2009 do NOT qualify. Federal standards (10 CFR 431.306) mandate factory-installed ECMs or 3-phase motors on these models. Retrofit ECMs installed on evaporator fans in walk-in coolers and freezers manufactured prior to 2009 are eligible.
| 2. | Condenser fan motor replacements for walk-in cooler and freezer systems manufactured after January 1, 2009 do NOT qualify. Federal standards (10 CFR 431.306) mandate factory-installed ECMs, permanent split capacitor motors, or 3-phase motors on these models. Retrofit ECMs installed on condenser fans in walk-in coolers and freezers manufactured prior to 2009 are eligible.
| 3. | HVAC FCU motor replacements in the capacity range of ≥1/12 hp and < 1 hp are only applicable for savings during the remaining useful life (RUL) of the pre-existing SP motor; this is because 2018 IECC standards require ECMs for this size range. Replacement of motors with capacities of <1/12 hp are eligible for savings for the full effective useful life (EUL).
| 4. | ECM motors in new construction and retrofits are eligible for these motor types: a) evaporator fan motors for reach-in coolers and display cases; b) compressor fan motors for refrigeration applications; and c) motors for FCUs with capacities <1/12 hp.
Unit of Measure
One motor.
Baseline Equipment
A standard efficiency shaded pole (SP) motor, up to 1 hp in capacity. (Deemed savings are provided for standard motor capacities up to 1/3 hp.)
High Efficiency Equipment
A high efficiency direct current electronically commutated motor (ECM), with the same capacity (hp) as the baseline motor.
ALGORITHMS
Baseline Motor Input Wattage
(1)
Energy Efficient Motor Input Wattage
(2)
Peak Demand Reduction, kW
Evaporator fan motors for walk-in and reach-in cases and motors for HVAC FCU fans:
(3)
Evaporator fan motors coupled with controls for walk-ins:
(4)
Compressor and condenser / condensing unit fan motors:
(5)
Annual Energy Savings, kWh/yr
Evaporator fan motors for walk-in and reach-in cases and motors for HVAC FCU fans:
(6)
Evaporator fan motors coupled with controls for walk-ins:
(7)
Compressor and condenser / condensing unit fan motors:
(8)
Lifetime Energy Savings, kWh
HVAC FCU fans, ≥1/12 hp and < 1hp
(9)
Evaporator fan motors and controls for walk-ins
(10)
Rest of measures
(11)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  | Sources/Notes
hp |  |  |  | Horsepower rating of motor (output power) | [11 empty] | Table 1 |  |  |  | hp |  | Selected based on site specific conditions.
746 |  |  |  | Conversion factor | [11 empty] | 746 |  |  |  | W/hp
ηBL |  |  |  | Efficiency of baseline motor (SP) | [11 empty] | Table 2 |  |  |  | - |  | AEG benchmarking 1
ηEE |  |  |  | Efficiency of efficient motor (ECM) | [11 empty] | Table 2 |  |  |  | - |  | AEG benchmarking 1
WBL |  |  |  | Baseline motor input wattage | [11 empty] | Eq'n 1 |  |  |  | W
WEE |  |  |  | Efficient motor input wattage | [11 empty] | Eq'n 2 |  |  |  | W
COP |  |  |  | Coefficient of performance | [11 empty] | Table 3 |  |  |  | - |  | AEG benchmarking 1
CF |  |  |  | Coincidence factor | [11 empty] | Table 4 |  |  |  | - |  | AEG benchmarking 1
HRS |  |  |  | Annual hours of operation | [11 empty] | Table 4 |  |  |  | hrs |  | AEG benchmarking 1
∆kWControl |  |  |  | Peak demand savings from Evaporator Motor Control measure | [11 empty] | Refer to measure |  |  |  | kW |  | See Table 2 of the Evaporator Motor Control measure
∆kWhControl |  |  |  | Energy savings from Evaporator Motor Control measure | [11 empty] | Refer to measure |  |  |  | kWh |  | See Table 2 of the Evaporator Motor Control measure
RUL |  |  |  | Remaining useful life of SP motor | [11 empty] | 5 |  |  |  | yrs |  | AEG benchmarking 1
EUL |  |  |  | Effective useful life of measure | [11 empty] | 15 |  |  |  | yrs |  | AEG benchmarking 1
Footnotes:
1. Refer to AEG's 2024 analysis file named "PY24 TRM - Commercial ECM - Analysis File."
Table 1: Horsepower Ratings and Output Power in Watts
Motor HP |  |  |  | Output Power in W (hp*746)
1/47 |  |  |  | 15.8723
1/25 |  |  |  | 29.84
1/20 |  |  |  | 37.3
1/15 |  |  |  | 49.7333
1/8 |  |  |  | 93.25
1/3 |  |  |  | 248.6667
Table 2: Motor Efficiencies
Application | [11 empty] | Motor Type
[12 empty] | SP |  |  |  |  | ECM
Walk-in Evaporator Fan Motor 1 | [11 empty] | 35% |  |  |  |  | 70%
Case Evaporator Fan Motor 2 | [11 empty] | 27% |  |  |  |  | 71%
Compressor/Condenser Fan Motor 3 | [11 empty] | 32.5% |  |  |  |  | 73%
HVAC FCU Fan Motor 4 | [11 empty] | 30% |  |  |  |  | 70%
Footnotes:
1. The efficiencies match the Evaporator Motor Control measure's efficiencies, which were derived from benchmarking.
2. The efficiencies are the average of high and low values in the RTF workbook: ComGroceryDisplayCaseEvapFanMotorRetrofit_v6_1.
3. The efficiencies are the average of high and low values in the RTF workbook: ComGroceryCompressorECM_v5_2.
4. See DOE 2013. SP efficiency is the average of high and low in Table 2.1 and ECM efficiency is the fractional horsepower efficiency of 70% listed in Section 2.4.3.
Table 3: Coefficients of Performance
Application | [11 empty] | COP
Medium Temperature (Cooler) 1 | [11 empty] | 2.2766
Low Temperature (Freezer) 2 | [11 empty] | 1.4329
Air Conditioning 3 | [11 empty] | 3.29
Footnotes:
1. Calculated for a typical reciprocating compressor, medium temperature refrigeration system using values of 769,000 Btu/h capacity and 99 kW power from DOE 2009, Table 3-7: Supermarket Compressor Energy Consumption. (769,000/3412)/99=2.28.
2. Calculated for a typical reciprocating compressor, low temperature refrigeration system using values of 308,000 Btu/h capacity and 63 kW power from DOE 2009, Table 3-7: Supermarket Compressor Energy Consumption. (308,000/3412)/63=1.43.
3. U.S. Department of Energy, Energy Efficiency & Renewable Energy, "Commercial Reference Buildings," <https://www.energy.gov/eere/buildings/commercial-reference-buildings>. Reference case for supermarket in Climate Zone 1A: "RefBldgSuperMarketNew2004_v1.3_5.0.xlsx."
Table 4: Hours of Operation and Coincidence Factors
Application | [11 empty] | Med. Temp. (Cooler) | [5 empty] | Low Temp. (Freezer) | [5 empty] | Air Conditioning
[12 empty] | HRS |  |  | CF |  |  | HRS |  |  | CF |  |  | HRS |  |  | CF
Walk-in Evaporator Fan Motor | [11 empty] | 8760 |  |  | 1 |  |  | 8234.4 |  |  | 0.94
Case Evaporator Fan Motor | [11 empty] | 8760 |  |  | 1 |  |  | 8234.4 |  |  | 0.94
Compressor/Condenser Fan Motor 1 | [11 empty] | 4380 |  |  | 0.5 |  |  | 6132 |  |  | 0.7
HVAC FCU Fan Motor 2 | [23 empty] | 2594 |  |  | 0.38
Footnotes:
1. Assumes duty cycle of 50% for cooler and 70% for freezer based on benchmarking; this is consistent with the Evaporator Motor Controls measure.
2. Uses EFLH and CF for average commercial building type from Table 2 of the EFLH & CF sheet.
Table 5: Demand and Energy Savings for Walk-In Evaporator Fan Motors (NO Controls)
Motor HP |  |  | For Coolers | [14 empty] | For Freezers
|  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings |  |  |  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings
1/47 |  |  | 0.033 |  |  |  |  | 285.88 |  |  |  |  | 4288.2 |  |  |  |  | 0.036 |  |  |  |  | 317.02 |  |  |  |  | 4755.3
1/25 |  |  | 0.061 |  |  |  |  | 537.46 |  |  |  |  | 8061.9 |  |  |  |  | 0.068 |  |  |  |  | 596 |  |  |  |  | 8940
1/20 |  |  | 0.077 |  |  |  |  | 671.82 |  |  |  |  | 10077.3 |  |  |  |  | 0.085 |  |  |  |  | 745 |  |  |  |  | 11175
1/15 |  |  | 0.102 |  |  |  |  | 895.76 |  |  |  |  | 13436.4 |  |  |  |  | 0.113 |  |  |  |  | 993.34 |  |  |  |  | 14900.1
1/8 |  |  | 0.192 |  |  |  |  | 1679.55 |  |  |  |  | 25193.25 |  |  |  |  | 0.213 |  |  |  |  | 1862.5 |  |  |  |  | 27937.5
1/3 |  |  | 0.511 |  |  |  |  | 4478.8 |  |  |  |  | 67182 |  |  |  |  | 0.567 |  |  |  |  | 4966.68 |  |  |  |  | 74500.2
Table 6: Demand and Energy Savings for Walk-In Evaporator Fan Motors (WITH Controls)
Motor HP |  |  | For Coolers | [14 empty] | For Freezers
|  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings |  |  |  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings
1/47 |  |  | 0.048 |  |  |  |  | 414.99 |  |  |  |  | 6224.85 |  |  |  |  | 0.046 |  |  |  |  | 401.04 |  |  |  |  | 6015.61
1/25 |  |  | 0.089 |  |  |  |  | 780.19 |  |  |  |  | 11702.81 |  |  |  |  | 0.086 |  |  |  |  | 753.96 |  |  |  |  | 11309.39
1/20 |  |  | 0.112 |  |  |  |  | 975.23 |  |  |  |  | 14628.43 |  |  |  |  | 0.108 |  |  |  |  | 942.45 |  |  |  |  | 14136.74
1/15 |  |  | 0.148 |  |  |  |  | 1300.31 |  |  |  |  | 19504.58 |  |  |  |  | 0.143 |  |  |  |  | 1256.61 |  |  |  |  | 18849.08
1/8 |  |  | 0.279 |  |  |  |  | 2438.07 |  |  |  |  | 36571.08 |  |  |  |  | 0.269 |  |  |  |  | 2356.12 |  |  |  |  | 35341.84
1/3 |  |  | 0.742 |  |  |  |  | 6501.53 |  |  |  |  | 97522.89 |  |  |  |  | 0.717 |  |  |  |  | 6283.01 |  |  |  |  | 94245.11
Table 7: Demand and Energy Savings for Reach-In Display Case Evaporator Fan Motors
Motor HP |  |  | For Coolers | [14 empty] | For Freezers
|  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings |  |  |  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings
1/47 |  |  | 0.052 |  |  |  |  | 459.32 |  |  |  |  | 6889.8 |  |  |  |  | 0.058 |  |  |  |  | 509.35 |  |  |  |  | 7640.25
1/25 |  |  | 0.099 |  |  |  |  | 863.52 |  |  |  |  | 12952.8 |  |  |  |  | 0.109 |  |  |  |  | 957.58 |  |  |  |  | 14363.7
1/20 |  |  | 0.123 |  |  |  |  | 1079.4 |  |  |  |  | 16191 |  |  |  |  | 0.137 |  |  |  |  | 1196.98 |  |  |  |  | 17954.7
1/15 |  |  | 0.164 |  |  |  |  | 1439.2 |  |  |  |  | 21588 |  |  |  |  | 0.182 |  |  |  |  | 1595.97 |  |  |  |  | 23939.55
1/8 |  |  | 0.308 |  |  |  |  | 2698.49 |  |  |  |  | 40477.35 |  |  |  |  | 0.342 |  |  |  |  | 2992.44 |  |  |  |  | 44886.6
1/3 |  |  | 0.821 |  |  |  |  | 7195.99 |  |  |  |  | 107939.85 |  |  |  |  | 0.911 |  |  |  |  | 7979.85 |  |  |  |  | 119697.75
Table 8: Demand and Energy Savings for Compressor/Condenser Fan Motors
Motor HP |  |  | For Coolers | [14 empty] | For Freezers
|  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings |  |  |  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings
1/47 |  |  | 0.014 |  |  |  |  | 118.68 |  |  |  |  | 1780.2 |  |  |  |  | 0.019 |  |  |  |  | 166.15 |  |  |  |  | 2492.25
1/25 |  |  | 0.025 |  |  |  |  | 223.11 |  |  |  |  | 3346.65 |  |  |  |  | 0.036 |  |  |  |  | 312.36 |  |  |  |  | 4685.4
1/20 |  |  | 0.032 |  |  |  |  | 278.89 |  |  |  |  | 4183.35 |  |  |  |  | 0.045 |  |  |  |  | 390.44 |  |  |  |  | 5856.6
1/15 |  |  | 0.042 |  |  |  |  | 371.85 |  |  |  |  | 5577.75 |  |  |  |  | 0.059 |  |  |  |  | 520.59 |  |  |  |  | 7808.85
1/8 |  |  | 0.08 |  |  |  |  | 697.22 |  |  |  |  | 10458.3 |  |  |  |  | 0.111 |  |  |  |  | 976.11 |  |  |  |  | 14641.65
1/3 |  |  | 0.212 |  |  |  |  | 1859.26 |  |  |  |  | 27888.9 |  |  |  |  | 0.297 |  |  |  |  | 2602.97 |  |  |  |  | 39044.55
Table 9: Demand and Energy Savings for HVAC FCU Fans
Motor HP |  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings
1/47 |  |  | 0.015 |  |  |  |  | 102.26 |  |  |  |  | 1533.9
1/25 |  |  | 0.028 |  |  |  |  | 192.25 |  |  |  |  | 2883.75
1/20 |  |  | 0.035 |  |  |  |  | 240.32 |  |  |  |  | 3604.8
1/15 |  |  | 0.047 |  |  |  |  | 320.42 |  |  |  |  | 4806.3
1/8 |  |  | 0.088 |  |  |  |  | 600.79 |  |  |  |  | 3003.95
1/3 |  |  | 0.235 |  |  |  |  | 1602.1 |  |  |  |  | 8010.5
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Select Type of Application (Walk-in, Case, Compressor/Condenser, HVAC)
Walk-in
Select Temperature of Application (Cooler, Freezer, FCU)
Freezer
Does Walk-in Evaporator Fan Motor Have Controls? (with, without)
[5 empty] | without |  |  | only applicable to evaporator fan motors in walk-in refrigeration systems
Select Horsepower of Motor
1/15
Enter Number of Motors of Given Horsepower
1
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Walk-in Freezer, 1/15 hp, without controls, 1 motor(s) | [7 empty] | 0.113 | [7 empty] | 993.34 | [7 empty] | 14900.1
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | AEG's 2024 analysis file named "PY24 TRM - Commercial ECM - Analysis File."
• | AEG's 2020 Analysis File titled "AEG HPUC - New Com Refrig Measures - Analysis File."
• | Arkansas Technical Reference Manual, Version 9.1, Volume 2, Aug. 31, 2022.
• | Code of Federal Regulations, 10 CFR 431.306, <https://www.ecfr.gov/current/title-10/section-431.306>.
• | Illinois 2024 Statewide Technical Reference Manual for Energy Efficiency, Version 12.0, Volume 2: Commercial and Industrial Measures, Sep. 22, 2023.
• | International Energy Conservation Code (IECC) 2018, <https://codes.iccsafe.org/content/IECC2018P5>.
• | Mid-Atlantic Technical Reference Manual, Version 10, May 2020.
• | Public Service Commission of Wisconsin, Wisconsin Focus on Energy 2023 Technical Reference Manual, Jan. 3, 2023.
• | Regional Technical Forum, "Compressor Head Fan Motor Retrofit to ECM," UES Workbook, Version 5.2." Northwest Power and Conservation Council. Jul. 18, 2023. Spreadsheet: "ComGroceryCompressorECM_v5_2.xlsm."
• | Regional Technical Forum, "Display Case Evaporator Fan Motor Retrofit," UES Workbook, Version 6.1." Northwest Power and Conservation Council. Jul. 18, 2023. Spreadsheet: "ComGroceryDisplayCaseEvapFanMotorRetrofit_v6_1.xlsm."
• | Regional Technical Forum, "Walk-In Evaporator Fan Motor Retrofit," UES Workbook, Version 5.1." Northwest Power and Conservation Council. Jul. 18, 2023. Spreadsheet: "ComGroceryWalkinECM_v5_1.xlsm."
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Programs, Version 4.0, Jan. 31, 2023.
• | Texas Technical Reference Manual, Version 11.0, Volume 3: Nonresidential Measures, Oct. 2023.
• | U.S. Department of Energy, Energy Efficiency & Renewable Energy, "Commercial Reference Buildings," <https://www.energy.gov/eere/buildings/commercial-reference-buildings>.
• | U.S. Department of Energy, Energy Efficiency & Renewable Energy, (DOE 2013), “Energy Savings Potential and Opportunities for High-Efficiency Electric Motors in Residential and Commercial Equipment,” Dec. 2013.
• | U.S. Department of Energy, Energy Efficiency & Renewable Energy, (DOE 2009), “Energy Savings Potential and Research & Development Opportunities for Commercial Refrigeration,” Sep. 2009.
∆𝑘𝑊=((𝑊_𝐵𝐿−𝑊_𝐸𝐸 ))/1000∗(1+1/𝐶𝑂𝑃)∗𝐶𝐹
∆𝑘𝑊=((𝑊_𝐵𝐿−𝑊_𝐸𝐸 ))/1000∗𝐶𝐹
∆𝑘𝑊ℎ=((𝑊_𝐵𝐿−𝑊_𝐸𝐸 ))/1000∗(1+1/𝐶𝑂𝑃)∗𝐻𝑅𝑆
∆𝑘𝑊ℎ=((𝑊_𝐵𝐿−𝑊_𝐸𝐸 ))/1000∗𝐻𝑅𝑆
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
𝑊_𝐵𝐿=(ℎ𝑝∗746)/𝜂_𝐵𝐿
𝑊_𝐸𝐸=(ℎ𝑝∗746)/𝜂_𝐸𝐸
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝑅𝑈𝐿
∆𝑘𝑊=((𝑊_𝐵𝐿−𝑊_𝐸𝐸 ))/1000∗(1+1/𝐶𝑂𝑃)∗𝐶𝐹+〖∆𝑘𝑊〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙
∆𝑘𝑊ℎ=((𝑊_𝐵𝐿−𝑊_𝐸𝐸 ))/1000∗(1+1/𝐶𝑂𝑃)∗𝐻𝑅𝑆+〖∆𝑘𝑊ℎ〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=(∆𝑘𝑊ℎ+〖∆𝑘𝑊ℎ〗_𝐶𝑜𝑛𝑡𝑟𝑜𝑙)∗𝐸𝑈𝐿

## C_PumpMotor_PE Motor
COMMERCIAL: Premium Efficiency Motor
Return to TOC
MEASURE DETAILS
Description
This measure relates to the installation of premium efficiency three phase Open Drip Proof (ODP) and Totally Enclosed Fan-Cooled (TEFC) motors less than or equal to 200 HP, meeting minimum qualifying efficiency for the following HVAC applications: supply fans, return fans, exhaust fans, chilled water pumps, and boiler feed water pumps.
Program Criteria
• Incentives apply to both ODP and TEFC enclosures with 1200 RPM, 1800 RPM or 3600 RPM motors. • Motors must meet minimum efficiency requirements as shown in the Table below. • Motors greater than 200 hp will be given consideration under the Hawai‘i Energy Customized Program. • If motors are not listed, submit manufacturer specifications, motor curve and performance data to Hawai‘i Energy for consideration
Unit of Measure
Per horse power
Baseline Equipment
2007 EISA nominal efficiency (as defined in NEMA MG1 Table 12-12) motors.
High Efficiency Equipment
The qualified efficiency table includes motors that are 1-200 hp NEMA Design A/B, 460 volts, TEFC or ODP, and 1200 rpm, 1800 rpm, or 3600 rpm.
ALGORITHMS
peak kW savings per HP | [6 empty] | = kW_perHP * [(1 / η_base) - (1 / η_ee)]
annual kWh savings per HP | [6 empty] | = kW_perHP * [(1 / η_base) - (1 / η_ee)] * LF * HRS
DEFINITIONS & ASSUMPTIONS
Variable |  | Description | [11 empty] | Value |  |  | Unit |  |  | Notes
kW_perHP |  | kW equivalent of 1 horse power | [11 empty] | 0.746 |  |  | kW/HP
η_base |  | Efficiency of baseline motor | [11 empty] | 81.67% |  |  | - |  |  | EISA 2007, avg 1 HP
η_ee |  | Efficiency of energy efficient motor | [11 empty] | 84.28% |  |  | - |  |  | HE requirement, avg 1 HP
LF |  | Loading factor--% of time pump actually operates | [11 empty] | 75% |  |  | - |  |  | Hawai‘i Energy PY15 TRM
HRS |  | Annual operating hours | [11 empty] | 2190 |  |  | hrs |  |  | Hawai‘i Energy PY15 TRM, 6 hours per day
Measure Life |  | Expected duration of savings | [11 empty] | 15 |  |  | yrs
Table 1: Qualifying Motor Efficiency Table
Motor Size (hp) |  | 3600 RPM (2-pole) | [7 empty] | 1800 RPM (4-pole) | [7 empty] | 1200 RPM (6-pole)
|  | ODP |  |  |  | TEFC |  |  |  | ODP |  |  |  | TEFC |  |  |  | ODP |  |  |  | TEFC
1 |  | 80 |  |  |  | 84 |  |  |  | 86.4 |  |  |  | 87.5 |  |  |  | 83.8 |  |  |  | 84
1.5 |  | 86.5 | 86.5 | 86.5 | 86.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.3 | 86.5 | 86.5 | 86.5 | 88.5 | 88.5 | 88.5 | 88.5 | 87.5 | 87.5 | 87.5 | 87.5 | 89.2 | 87.5 | 87.5 | 87.5
2 |  | 86.5 | 86.5 | 86.5 | 86.5 | 88.5 | 88.5 | 88.5 | 88.5 | 87.3 | 86.5 | 86.5 | 86.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 90.1 | 88.5 | 88.5 | 88.5
3 |  | 86.5 | 86.5 | 86.5 | 86.5 | 89.5 | 89.5 | 89.5 | 89.5 | 90.3 | 89.5 | 89.5 | 89.5 | 91 | 91 | 91 | 91 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2
5 |  | 89.5 | 89.5 | 89.5 | 89.5 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 89.5 | 89.5 | 89.5 | 91 | 91 | 91 | 91 | 90.5 | 90.5 | 90.5 | 90.5 | 91 | 91 | 91 | 91
7.5 |  | 90.2 | 90.2 | 90.2 | 90.2 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 93 | 93 | 93 | 93 | 91.7 | 91.7 | 91.7 | 91.7 | 92.4 | 92.4 | 92.4 | 92.4
10 |  | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 92.3 | 91.7 | 91.7 | 91.7 | 93 | 93 | 93 | 93 | 92.4 | 92.4 | 92.4 | 92.4 | 92.4 | 92.4 | 92.4 | 92.4
15 |  | 91.6 | 91 | 91 | 91 | 92.4 | 92.4 | 92.4 | 92.4 | 93.6 | 93 | 93 | 93 | 93.6 | 93.6 | 93.6 | 93.6 | 92.4 | 92.4 | 92.4 | 92.4 | 93 | 93 | 93 | 93
20 |  | 92.4 | 92.4 | 92.4 | 92.4 | 93 | 93 | 93 | 93 | 93.6 | 93.6 | 93.6 | 93.6 | 94.1 | 94.1 | 94.1 | 94.1 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
25 |  | 93 | 93 | 93 | 93 | 93.6 | 93.6 | 93.6 | 93.6 | 94.1 | 94.1 | 94.1 | 94.1 | 94.5 | 94.5 | 94.5 | 94.5 | 93.6 | 93.6 | 93.6 | 93.6 | 94.1 | 94.1 | 94.1 | 94.1
30 |  | 92.4 | 92.4 | 92.4 | 92.4 | 93.6 | 93.6 | 93.6 | 93.6 | 94.6 | 94.1 | 94.1 | 94.1 | 94.5 | 94.5 | 94.5 | 94.5 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1
40 |  | 93.6 | 93.6 | 93.6 | 93.6 | 94.1 | 94.1 | 94.1 | 94.1 | 94.5 | 94.5 | 94.5 | 94.5 | 95 | 95 | 95 | 95 | 94.5 | 94.5 | 94.5 | 94.5 | 95 | 95 | 95 | 95
50 |  | 94.1 | 94.1 | 94.1 | 94.1 | 94.5 | 94.5 | 94.5 | 94.5 | 95 | 95 | 95 | 95 | 95.4 | 95.4 | 95.4 | 95.4 | 94.5 | 94.5 | 94.5 | 94.5 | 95 | 95 | 95 | 95
60 |  | 94.5 | 94.5 | 94.5 | 94.5 | 95 | 95 | 95 | 95 | 95.4 | 95.4 | 95.4 | 95.4 | 95.8 | 95.8 | 95.8 | 95.8 | 95 | 95 | 95 | 95 | 95.4 | 95.4 | 95.4 | 95.4
75 |  | 95 | 95 | 95 | 95 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.8 | 95.8 | 95.8 | 95.8 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
100 |  | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.8 | 95.4 | 95.4 | 95.4 | 96.2 | 96.2 | 96.2 | 96.2 | 95.4 | 95.4 | 95.4 | 95.4 | 95.8 | 95.8 | 95.8 | 95.8
125 |  | 95.4 | 95.4 | 95.4 | 95.4 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 96.2 | 96.2 | 96.2 | 96.2 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8
150 |  | 95.8 | 95.8 | 95.8 | 95.8 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.5 | 96.5 | 96.5 | 96.5 | 95.8 | 95.8 | 95.8 | 95.8 | 96.2 | 96.2 | 96.2 | 96.2
200 |  | 95.8 | 95.8 | 95.8 | 95.8 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.8 | 96.8 | 96.8 | 96.8 | 95.8 | 95.8 | 95.8 | 95.8 | 96.2 | 96.2 | 96.2 | 96.2
SAVINGS
Measure Name | [5 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings
Premium Efficiency Motor | [5 empty] | 0.028 | [7 empty] | 46.46

## C_PumpMotor_VFD Pool Pump
COMMERCIAL: VFD Pool Pump
Return to TOC
UPDATE STATUS
Updated in Winter 2023-2024 for the PY24 TRM. This update applies the federal standard for dedicated-purpose pool pumps, effective June 19, 2021. It also applies the most recent Energy STAR 3.1 specifications for dedicated-purpose pool pumps.
MEASURE DETAILS
Description
This measure involves replacing a single-speed or dual-speed pool filter pump with a variable-speed pump of equivalent horsepower. This measure only applies to self-priming pool filter pumps, typically used with permanent, in-ground pools in multi-family and commercial buildings (there is a separate measure for single-family residential settings). Non-self-priming pool filter pumps, typically used with rigid, above-ground pools, are not applicable.
Program Criteria
Qualifying pumps are variable speed pumps with built-in controllers or purchased and installed as a pair.
The installed variable-speed self-priming pool filter pump's rated Weighted Energy Factor (WEF) must meet or exceed the ENERGY STAR specifications. Any high-speed override capability should be temporary, not to exceed one 24-hour cycle without reverting to default settings.
A pool pump greater than 4 hp may be handled as a custom measure.
Unit of Measure
One pump.
Baseline Equipment
The baseline efficiency equipment is a single-speed or dual-speed self-priming pool filter pump.
High Efficiency Equipment
The high efficiency equipment is an ENERGY STAR-certified variable-speed self-priming pool filter pump.
The sunset date for this measure is September 29, 2025, for pool pumps greater or equal to 1.15 but less than 5 total horsepower (THP).
The sunset date for this measure is September 28, 2027, for pool pumps greater or equal to 0.5 but less than 1.15 total horsepower (THP).
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  | Value | Unit | Sources/Notes
ΔkWh |  | Annual energy savings |  | Calculated | kWh/yr
ΔkW |  | Peak demand reduction |  | Calculated | kW
kWhDaily,Base |  | Daily energy consumption of baseline pump (depends on pump horsepower) |  |  |  | AEG derived the values from the Regional Technical Forum's (RTF) original analysis in the unit energy savings measure workbook for Efficient Pool Pumps but only included pool pumps meeting the federal code requirements.1
Single-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 14.6223 | kWh/day
|  | > 1 to ≤ 2 hp |  | 22.1854 | kWh/day
|  | > 2 to ≤ 3 hp |  | 31.5133 | kWh/day
|  | > 3 to ≤ 4 hp |  | 51.822 | kWh/day
Dual-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 18.9712 | kWh/day
|  | > 1 to ≤ 2 hp |  | 22.1854 | kWh/day
|  | > 2 to ≤ 3 hp |  | 31.5133 | kWh/day
|  | > 3 to ≤ 4 hp |  | 49.3825 | kWh/day
kWhDaily,Eff |  | Daily energy consumption of variable-speed pump (depends on pump horsepower) |  |  |  | AEG derived the values from the RTF's original analysis in the unit energy savings measure workbook for Efficient Pool Pumps but only included pool pumps meeting the Energy Star requirements.2
Variable-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 9.231 | kWh/day
|  | > 1 to ≤ 2 hp |  | 13.9266 | kWh/day
|  | > 2 to ≤ 3 hp |  | 18.3345 | kWh/day
|  | > 3 to ≤ 4 hp |  | 27.0497 | kWh/day
Days |  | Number of days the pump operates in a year |  | 365 | Days/yr | No change from PY18 TRM
HoursDaily,Base |  | Daily runtime of baseline pump (depends on pump horsepower) |  |  |  | AEG derived the values from the RTF's original analysis in the unit energy savings measure workbook for Efficient Pool Pumps but only included pool pumps meeting the federal code requirements.1
Single-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 17.637 | Hrs/day
|  | > 1 to ≤ 2 hp |  | 24 | Hrs/day
|  | > 2 to ≤ 3 hp |  | 24 | Hrs/day
|  | > 3 to ≤ 4 hp |  | 18.8782 | Hrs/day
Dual-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 24 | Hrs/day
|  | > 1 to ≤ 2 hp |  | 24 | Hrs/day
|  | > 2 to ≤ 3 hp |  | 24 | Hrs/day
|  | > 3 to ≤ 4 hp |  | 24 | Hrs/day
HoursDaily,Eff |  | Daily runtime of variable-speed pump (depends on pump horsepower) |  |  |  | AEG derived the values from the RTF's original analysis in the unit energy savings measure workbook for Efficient Pool Pumps but only included pool pumps meeting the Energy Star requirements.2
Variable-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 22.692 | Hrs/day
|  | > 1 to ≤ 2 hp |  | 22.692 | Hrs/day
|  | > 2 to ≤ 3 hp |  | 22.692 | Hrs/day
|  | > 3 to ≤ 4 hp |  | 23.51 | Hrs/day
CFBase |  | Coincidence factor of baseline pump (depends on pump horsepower) |  |  |  | AEG's estimate, obtained by dividing the number of daily operation hours of pump by 24 hours
Single-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 0.73488
|  | > 1 to ≤ 2 hp |  | 1
|  | > 2 to ≤ 3 hp |  | 1
|  | > 3 to ≤ 4 hp |  | 0.78659
Dual-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 1
|  | > 1 to ≤ 2 hp |  | 1
|  | > 2 to ≤ 3 hp |  | 1
|  | > 3 to ≤ 4 hp |  | 1
CFEff |  | Coincidence factor of variable-speed pump (depends on pump horsepower) |  |  |  | AEG's estimate, obtained by dividing the number of daily operation hours of pump by 24 hours
Variable-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 0.9455
|  | > 1 to ≤ 2 hp |  | 0.9455
|  | > 2 to ≤ 3 hp |  | 0.9455
|  | > 3 to ≤ 4 hp |  | 0.97958
EUL |  | Effective useful life of measure |  | 10 | yrs | AEG's Fall 2018 Benchmarking
Sources:
1 Federal Code. Title 10, Subchapter D. Part 431. Subpart Z. § 431.465. Accessible at: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-Y/section-431.465.
2 ENERGY STAR Program Requirements Product Specification for Pool Pumps Version 3.1. Accessible at: https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Version%203.1%20Pool%20Pumps%20Final%20Specification.pdf.
SAVINGS
Measure Name |  |  | Peak Demand Savings | Annual Energy Savings |  |  | Lifetime Energy Savings
Com. VFD Pool Pump
Single-speed to variable speed: > 0 to ≤ 1 hp |  |  | 0.225 | 1967.83 |  |  | 19678.3
Single-speed to variable speed: > 1 to ≤ 2 hp |  |  | 0.344 | 3014.48 |  |  | 30144.8
Single-speed to variable speed: > 2 to ≤ 3 hp |  |  | 0.549 | 4810.24 |  |  | 48102.4
Single-speed to variable speed: > 3 to ≤ 4 hp |  |  | 1.032 | 9041.89 |  |  | 90418.9
Dual-speed to variable speed: > 0 to ≤ 1 hp |  |  | 0.406 | 3555.14 |  |  | 35551.4
Dual-speed to variable speed: > 1 to ≤ 2 hp |  |  | 0.344 | 3014.48 |  |  | 30144.8
Dual-speed to variable speed: > 2 to ≤ 3 hp |  |  | 0.549 | 4810.24 |  |  | 48102.4
Dual-speed to variable speed: > 3 to ≤ 4 hp |  |  | 0.931 | 8151.47 |  |  | 81514.7
RESOURCES
• | AEG's 2024 Analysis File titled "PY24 TRM - Commercial Variable Frequency Drive (VFD) Pool Pump - Analysis File."
• | AEG's 2018 Analysis File titled "AEG HPUC Update of Com Pool Pump VFD - Analysis File."
• | Code of Federal Regulation, Title 10, Subchapter D. Part 431. Subpart Z. § 431.465. Available online at: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-Y/section-431.465.
• | Code of Federal Regulation, Title 10, Subchapter D. Part 431. Subpart Z. § 431.485 Available online at: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-Z/section-431.485.
• | DOE National Impact Analysis (NIA) for Dedicated Purpose Pool Pumps ("NIA_PoolPumps_2016-12-19_ForPublication_v2.xlsm"), available online at: https://www.regulations.gov/document?D=EERE-2015-BT-STD-0008-0107.
• | ENERGY STAR Product Specifications for Pool Pumps, Version 2.0, available online at: https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Final%20Version%202.0%20Pool%20Pumps%20Specification.pdf.
• | Regional Technical Forum. Efficient Pool Pumps - Unit Energy Savings Workbook, Version 2.1. Northwest Power and Conservation Council. February 27, 2018. Spreadsheet. Available online at: https://rtf.nwcouncil.org/measure/efficient-pool-pumps.
∆𝑘𝑊ℎ=(〖𝑘𝑊ℎ〗_(𝐷𝑎𝑖𝑙𝑦,𝐵𝑎𝑠𝑒)−〖𝑘𝑊ℎ〗_(𝐷𝑎𝑖𝑙𝑦,𝐸𝑓𝑓) )∗𝐷𝑎𝑦𝑠
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊=[(〖𝑘𝑊ℎ〗_(𝐷𝑎𝑖𝑙𝑦,𝐵𝑎𝑠𝑒)/〖𝐻𝑜𝑢𝑟𝑠〗_(𝐷𝑎𝑖𝑙𝑦,𝐵𝑎𝑠𝑒) )∗〖𝐶𝐹〗_𝐵𝑎𝑠𝑒 ]−[(〖𝑘𝑊ℎ〗_(𝐷𝑎𝑖𝑙𝑦,𝐸𝑓𝑓)/〖𝐻𝑜𝑢𝑟𝑠〗_(𝐷𝑎𝑖𝑙𝑦,𝐸𝑓𝑓) )∗〖𝐶𝐹〗_𝐸𝑓𝑓 ]

## C_Refrig_Evap Motor Control
COMMERCIAL: Evaporator Motor Controls
Return to TOC
UPDATE STATUS
Introduced in Fall 2020 for PY20 TRM v2.0.
MEASURE DETAILS
Description
By installing evaporator fan motor controls on existing evaporator fans, the continuous full speed operation of cooler and freezer evaporator fans can be avoided. This measure assumes the motor controls will cycle the evaporator fans on and off to meet the current need of the refrigeration system, thus conserving energy.
Program Criteria
| 1. | Equipping already existing shaded pole (SP) motors or electronically commutated motors (ECMs) on evaporator fans with fan motor controls.
| 2. | Walk-in coolers and freezers and refrigerated warehouse applications are eligible.
Unit of Measure
Per evaporator fan motor controlled, where the total number of controlled evaporator fans with a given motor horsepower is a custom entry.
Baseline Equipment
Evaporator fans with no motor controls.
High Efficiency Equipment
Evaporator fans with motor controls equipped.
ALGORITHMS
Peak Demand Reduction, kW
[16 empty] | where | [14 empty] | (1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [8 empty] | Value | [5 empty] | Unit |  |  | Source/Notes
[13 empty] | SP |  |  | ECM
Nfans |  |  |  | Number of evaporator fans | [8 empty] | User entry | [5 empty] | Fans |  |  | Custom entry based on number of evaporator fans of a given horsepower rating.
hp |  |  |  | Horsepower rating of evaporator fan | [8 empty] | Table 1 |  |  | Table 2 |  |  | hp |  |  | Selected based on site specific conditions.
0.746 |  |  |  | Conversion factor | [8 empty] | 0.746 | [5 empty] | kW/hp
η |  |  |  | Motor efficiency | [8 empty] | 35% |  |  | 70% |  |  | - |  |  | Benchmarking review of typical SP and ECM products. 1
DCcomp |  |  |  | Duty cycle of compressor used in Coolers (medium temperature refrigeration) | [8 empty] | 50% | [5 empty] | - |  |  | Assumes on/off cycling. Value is based on benchmarking review of typical compressor operation for Coolers. 1
|  |  |  | Duty cycle of compressor used in Freezers (low temperature refrigeration) | [8 empty] | 70% | [5 empty] | - |  |  | Assumes on/off cycling. Value is based on benchmarking review of typical compressor operation for Freezers. 1
DCevap |  |  |  | Duty cycle of evaporator fan used in Coolers (base case) | [8 empty] | 100% | [5 empty] | - |  |  | Without controls, evaporator fans in coolers run continuously at full speed.
|  |  |  | Duty cycle of evaporator fan used in Freezers (base case) | [8 empty] | 94% | [5 empty] | - |  |  | Even without evaporator fan motor controls, evaporator fans in freezers do not run 100% of the time because of defrost control settings. The assumed value of 94% is based on benchmarking review. 1
BF |  |  |  | Bonus factor for reduced thermal load in Coolers, due to reduced fan usage | [8 empty] | 1.3 | [5 empty] | - |  |  | Bonus factor (1+1/COP) assumes 2.0 COP for low temperature and 3.5 COP for medium temperature refrigeration, based on the average of standard reciprocating and discus compressor efficiencies with Saturated Suction Temperatures of -20°F and 20°F, respectively, and a condensing temperature of 90°F. 2
|  |  |  | Bonus factor for reduced thermal load in Freezers, due to reduced fan usage | [8 empty] | 1.5 | [5 empty] | -
CF |  |  |  | Coincidence factor | [8 empty] | (1-DCcomp)*DCevap | [5 empty] | - |  |  | Assumes the controlled fan will cycle consistently throughout the day, including during the peak demand period.
HRS |  |  |  | Annual hours of operation | [8 empty] | 8760 | [5 empty] | hrs |  |  | Assumes refrigeration space operates 24 hr/day, 365 day/yr.
EULEE |  |  |  | Effective useful life of measure | [8 empty] | 5 |  |  | 15 |  |  | yrs |  |  | EUL for SP is based on remaining useful life of the SP motor since it is likely the SP motor would be replaced with a more efficient motor upon the end of its useful life (and, therefore, the savings would diminish). 3 EUL for ECM assumes most of existing ECMs would be replaced with ECMs upon the end of the motor's useful life (and, therefore, the savings would continue), but sets a limit equal to the EUL of the ECM, which is 15 years for a high efficiency evaporator fan motor per DEER 2020.
1 AEG's 2020 Analysis File titled "AEG HPUC - New Com Refrig Measures - Analysis File_Dec 2020." See sheet named "Evaporator motor controls_Notes." Note that efficiency will also be a function of motor size, but we have assumed an average efficiency across all motor sizes in Tables 1 and 2 for simplicity.
2 Arkansas Technical Reference Manual, Version 8.1, Volume 2: Deemed Savings, Aug. 31, 2019, p. 475, footnote 648. The 1.2 and 1.5 values are also cited in Texas TRM v7.0.
3 Note that future replacement of an SP motor with a new ECM + same controller could be claimed in the TRM's other ECM measure.
Table 1: Demand and Energy Savings for Motor Controls (Having Shaded Pole Motor)
Motor HP |  |  | For Coolers | [14 empty] | For Freezers
|  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings |  |  |  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings
1/47 |  |  | 0.029477 |  |  |  |  | 258.2203 |  |  |  |  | 1291.1015 |  |  |  |  | 0.019183 |  |  |  |  | 168.0418 |  |  |  |  | 840.2091
1/25 |  |  | 0.055417 |  |  |  |  | 485.4542 |  |  |  |  | 2427.2709 |  |  |  |  | 0.036064 |  |  |  |  | 315.9186 |  |  |  |  | 1579.5932
1/20 |  |  | 0.069271 |  |  |  |  | 606.8177 |  |  |  |  | 3034.0886 |  |  |  |  | 0.04508 |  |  |  |  | 394.8983 |  |  |  |  | 1974.4915
1/15 |  |  | 0.092362 |  |  |  |  | 809.0903 |  |  |  |  | 4045.4514 |  |  |  |  | 0.060106 |  |  |  |  | 526.5311 |  |  |  |  | 2632.6553
1/8 |  |  | 0.17318 |  |  |  |  | 1517.0443 |  |  |  |  | 7585.2214 |  |  |  |  | 0.1127 |  |  |  |  | 987.2457 |  |  |  |  | 4936.2287
1/3 |  |  | 0.46181 |  |  |  |  | 4045.4514 |  |  |  |  | 20227.2571 |  |  |  |  | 0.30053 |  |  |  |  | 2632.6553 |  |  |  |  | 13163.2766
Table 2: Demand and Energy Savings for Motor Controls (Having ECM)
Motor HP |  |  | For Coolers | [14 empty] | For Freezers
|  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings |  |  |  |  | Peak kW Savings |  |  |  |  | Annual kWh Savings |  |  |  |  | Lifetime kWh Savings
1/47 |  |  | 0.014739 |  |  |  |  | 129.1102 |  |  |  |  | 1936.6523 |  |  |  |  | 0.0095914 |  |  |  |  | 84.0209 |  |  |  |  | 1260.3137
1/25 |  |  | 0.027709 |  |  |  |  | 242.7271 |  |  |  |  | 3640.9063 |  |  |  |  | 0.018032 |  |  |  |  | 157.9593 |  |  |  |  | 2369.3898
1/20 |  |  | 0.034636 |  |  |  |  | 303.4089 |  |  |  |  | 4551.1329 |  |  |  |  | 0.02254 |  |  |  |  | 197.4491 |  |  |  |  | 2961.7372
1/15 |  |  | 0.046181 |  |  |  |  | 404.5451 |  |  |  |  | 6068.1771 |  |  |  |  | 0.030053 |  |  |  |  | 263.2655 |  |  |  |  | 3948.983
1/8 |  |  | 0.086589 |  |  |  |  | 758.5221 |  |  |  |  | 11377.8321 |  |  |  |  | 0.05635 |  |  |  |  | 493.6229 |  |  |  |  | 7404.3431
1/3 |  |  | 0.2309 |  |  |  |  | 2022.7257 |  |  |  |  | 30340.8857 |  |  |  |  | 0.15027 |  |  |  |  | 1316.3277 |  |  |  |  | 19744.9149
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Select Type of Refrigerated Space (Cooler or Freezer)
Cooler
Select Type of Evaporator Fan Motor
ECM
Select Horsepower of Evaporator Fan Motor
1/47
Enter Number of Motors of Given Horsepower
1
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Cooler Evaporator Fan Motor Controls, 1/47 hp, ECM, 1 motor(s) | [7 empty] | 0.015 | [7 empty] | 129.11 | [7 empty] | 1936.65
RESOURCES
• | AEG's 2020 Analysis File titled "AEG HPUC - New Com Refrig Measures - Analysis File."
• | Arkansas Technical Reference Manual, Version 8.1, Volume 2: Deemed Savings, Aug. 31, 2019.
• | Connecticut's 2018 Program Savings Document, 13th Edition, filed Dec. 15, 2017.
• | Illinois 2020 Statewide Technical Reference Manual for Energy Efficiency, Version 8.0, Volume 2: Commercial and Industrial Measures, Oct. 17, 2019.
• | Mid-Atlantic Technical Reference Manual, Version 8, May 2018.
• | Public Service Commission of Wisconsin, Wisconsin Focus on Energy 2020 Technical Reference Manual, pp. 794-797.
• | Regional Technical Forum. "Walk-In Evaporator Fan ECMotor Controllers - Unit Energy Savings Workbook, Version 3.1." Northwest Power and Conservation Council. December 7, 2018. Spreadsheet: "ComGroceryWalkinEvapFanECMContoller_v3_1.xlsm."
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Programs, Version 2.2, May 2, 2018.
• | Tennessee Valley Authority Technical Reference Manual, Version 6.0, October 1, 2017.
• | Texas Technical Reference Manual, Version 7.0, Volume 3: Nonresidential Measures, November 2019, pp. 247-249.
∆𝑘𝑊=𝑁_𝑓𝑎𝑛𝑠∗(ℎ𝑝∗0.746)/𝜂∗𝐵𝐹∗𝐶𝐹
∆𝑘𝑊ℎ=𝑁_𝑓𝑎𝑛𝑠∗(ℎ𝑝∗0.746)/𝜂∗(1−〖𝐷𝐶〗_𝑐𝑜𝑚𝑝 )∗〖𝐷𝐶〗_𝑒𝑣𝑎𝑝∗𝐵𝐹∗𝐻𝑅𝑆=∆𝑘𝑊∗𝐻𝑅𝑆
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
𝐶𝐹=(1−〖𝐷𝐶〗_𝑐𝑜𝑚𝑝 )∗〖𝐷𝐶〗_𝑒𝑣𝑎𝑝

## C_Refrig_Add Case Doors
COMMERCIAL: Adding Doors to Refrigerated Cases
Return to TOC
UPDATE STATUS
Introduced in Fall 2020 for PY20 TRM v2.0.
MEASURE DETAILS
Description
Doors can be retrofitted onto existing medium temperature open cases to reduce the energy usage by compressor due to reduced spillage of cold air.
Program Criteria
| 1. | Equipping already existing medium temperature (10-35°F) open refrigerated cases with doors.
| 2. | Refrigeration system must be reevaluated after adding doors since the load reduction (and change in load profile) will affect the operation and performance of the overall system. Specifically, reconfiguration of the compressor rack and controls will be needed to align compressor operation with the new load profile of the cases. Refer to DOE 2013 reference listed in "Resources" section below for more information.
Unit of Measure
Per refrigerated case, where the length of the case in linear feet is a custom entry.
Baseline Equipment
Case with no doors.
High Efficiency Equipment
Case with doors equipped.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  | Value | Unit | Source/Notes
LT |  |  | Total load of refrigerated case |  |  | 1727.5 | Btu/hr-ft | The thermal load is based on the value for a typical 12 ft "vertical open medium temperature" supermarket display case from DOE 2009. 1
LRNet |  |  | Overall net reduction in thermal load due to adding doors |  |  | 73% | - | DOE 2009, Table 3-4. 2
DCcomp |  |  | Duty cycle for refrigeration compressor |  |  | 60% | - | The duty cycle is dependent on the configuration and controls of the compressor racks, which generally include several compressors to allow for optimizing capacity loading and duty cycles. AEG's 2020 benchmarking yielded a typical range of 50-70%, so 60% is assumed to reflect the midpoint of that range.
3412 |  |  | Conversion factor from Btu to kWh |  |  | 3412 | Btu/kWh
COPR |  |  | Coefficient of performance for refrigeration system |  |  | 2.28 | - | Estimated for a typical reciprocating compressor, medium temperature refrigeration system, DOE 2009, Table 3-7. 3
COPAC |  |  | Coefficient of performance for the AC system cooling the space |  |  | 3.29 | - | Weighted average value used in DOE's reference case prototype for supermarkets, climate zone 1A: Miami (same as Hawaii), used in simulation models. 4
24 |  |  | Conversion factor from hours to days |  |  | 24 | hrs/day
CDD |  |  | Cooling degree days |  |  | 4560 | degree day | For Honolulu, HI based on TMY3 data and base temperature of 65°F. 5
Ts |  |  | Temperature of the space |  |  | 75 | °F | Temperature of space (i.e., supermarket) based on set-point used in DOE's reference case prototype for supermarkets. 4
TR |  |  | Temperature of the refrigerated case |  |  | 25 | °F | Temperature that refrigerated case needs to be maintained. Typical range for medium temperature coolers is 10-35°F, so 25°F is assumed to reflect the midpoint of that range. Source: DOE 2009, Table 3-1. 6
HRS |  |  | Annual hours of operation |  |  | 8760 | hrs/yr | Assumes refrigerated case operates 24 hr/day, 365 day/yr.
Length |  |  | Length of the refrigerated case |  |  | User entry | linear foot | Custom entry based on refrigerated case.
EULEE |  |  | Effective useful life of measure |  |  | 8 | yrs | According to DOE 2009 and the Food Marketing Institute, refrigerated display cases are often replaced before the end of their functional life during store renovations. Store renovations typically occur every 6 to 10 years, so 8 years is assumed to reflect the midpoint of that range. 7
1 U.S. Department of Energy, Energy Efficiency & Renewable Energy, Building Technologies Office, "Energy Savings Potential and Research & Development Opportunities for Commercial Refrigeration," September 2009. <https://www1.eere.energy.gov/buildings/pdfs/commercial_refrigeration_equipment_research_opportunities.pdf>. Table 3-4: Supermarket Display Case Thermal Load Breakdown (Btu/hr).
2 Used values in Table 3-4 of the DOE 2009 report to come up with a total reduction in thermal load from 20,730 Btu/hr without door to 5,507 Btu/hr with doors for a 12 ft case; this equates to a net reduction of 73% in thermal load by adding doors.
3 Calculated for a typical reciprocating compressor, medium temperature refrigeration system using values of 769,000 Btu/h capacity and 99 kW power from DOE 2009, Table 3-7: Supermarket Compressor Energy Consumption. (769,000/3412)/99=2.28.
4 U.S. Department of Energy, Energy Efficiency & Renewable Energy, "Commercial Reference Buildings," <https://www.energy.gov/eere/buildings/commercial-reference-buildings>. Reference case for supermarket in Climate Zone 1A: "RefBldgSuperMarketNew2004_v1.3_5.0.xlsx."
5 AEG analysis file titled "3 - Weather Analysis - EPW-HI Portland and CA - TMY.xlsx."
6 DOE 2009, Table 3-1: Evaporator Coil Temperature Ranges by Application.
7 DOE 2009 and Food Marketing Institute, "Marketing Costs," August 2008.
SAVINGS
Semi-Prescriptive Savings Calculator (based on length of refrigerated case in linear feet)
Enter Length of Refrigerated Case in Linear Feet
1
Measure Name |  |  |  |  | Peak Demand Savings | Annual Energy Savings |  |  | Lifetime Energy Savings
Adding Refrigerated Case Doors |  |  |  |  | 0.069 | 606.13 |  |  | 4849.04
RESOURCES
• | AEG's 2020 Analysis Files titled "AEG HPUC - New Com Refrig Measures - Analysis File" and "3 - Weather Analysis - EPW-HI Portland and CA - TMY.xlsx."
• | Faramarzi, R. T., B. A. Coburn, R. Sarhadian, "Performance and Energy Impact of Installing Glass Doors on an Open Vertical Deli/Dairy Display Case," AC-02-7-2, ASHRAE Transactions, 2002, 108, ProQuest SciTech Collection, pg. 673.
• | Food Marketing Institute, "Marketing Costs," August 2008.
• | U.S. Department of Energy, Energy Efficiency & Renewable Energy, Building Technologies Office, "Energy Savings Potential and Research & Development Opportunities for Commercial Refrigeration," September 2009. <https://www1.eere.energy.gov/buildings/pdfs/commercial_refrigeration_equipment_research_opportunities.pdf>.
• | U.S. Department of Energy Building Technology Program, "Advanced Energy Retrofit Guide: Practical Ways to Improve Energy Performance, Grocery Stores," National Renewable Energy Laboratory, June 2012. <http://www.nrel.gov/docs/fy13osti/54243.pdf>.
• | U.S. Department of Energy, Energy Efficiency & Renewable Energy, "Guide for the Retrofitting of Open Refrigeration Display Cases with Doors," Prepared for Better Buildings Alliance, Building Technologies Office, Prepared by Navigant Consulting, Inc., June 2013.
• | U.S. Department of Energy, Energy Efficiency & Renewable Energy, "Commercial Reference Buildings," <https://www.energy.gov/eere/buildings/commercial-reference-buildings>. Reference case for supermarket in Climate Zone 1A: "RefBldgSuperMarketNew2004_v1.3_5.0.xlsx."
• | Public Service Commission of Wisconsin, "Focus on Energy Evaluation, Business Programs: Deemed Savings Manual v1.0," March 2010.
• | Public Service Commission of Wisconsin. "Wisconsin Focus on Energy 2020 Technical Reference Manual." Pp. 816-819.
∆𝑘𝑊=[𝐿_𝑇∗〖𝐿𝑅〗_𝑁𝑒𝑡 ][〖𝐷𝐶〗_𝑐𝑜𝑚𝑝/(3412∗〖𝐶𝑂𝑃〗_𝑅 )−(24∗𝐶𝐷𝐷)/((𝑇_𝑠−𝑇_𝑅 )∗3412∗〖𝐶𝑂𝑃〗_𝐴𝐶∗𝐻𝑅𝑆)]∗𝐿𝑒𝑛𝑔𝑡ℎ
∆𝑘𝑊ℎ=∆𝑘𝑊∗𝐻𝑅𝑆
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## C_Refrig_FHP Control
COMMERCIAL: Floating Head Pressure Controls
Return to TOC
UPDATE STATUS
Introduced in Fall 2020 for PY20 TRM v2.0.
MEASURE DETAILS
Description
By allowing the head pressure to float instead of keeping it fixed, we can reduce the compressor pressure ratio and the compressor runtime would be reduced. By programming the head pressure to follow the ambient temperature, we can ensure efficient operation at all temperatures.
Program Criteria
| 1. | Adding a floating head pressure controller to a refrigeration system that initially has a fixed head pressure.
| 2. | Limited to single compressor systems.
Unit of Measure
Per compressor motor, where compressor motor horsepower is a custom entry.
Baseline Equipment
Refrigeration system with no head pressure controller.
High Efficiency Equipment
Refrigeration system equipped with head pressure controller.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  |  |  | Value |  |  |  | Unit |  |  | Source/Notes
m |  |  | Linear interpolation constant, slope of line |  |  |  |  | See Table 1 |  |  |  | kW/hp-°F |  |  | The Regional Technical Forum (RTF) used EnergyPlus building simulation modeling with climate data for Portland and other Pacific Northwest locations to estimate the impacts from floating head pressure controls for several types of refrigeration systems.1 The approach for Hawaii uses a comparison of annual dry bulb temperatures from typical meteorological year (TMY) data for Portland, OR and Honolulu, HI to adjusts the RTF's savings results for Hawaii's climate. The result is a set of linear regression models that estimate savings as a function of mean dry bulb temperatures (≤75°F).2
b |  |  | Linear interpolation constant, y-intercept |  |  |  |  | See Table 1 |  |  |  | kW/hp
hp |  |  | Compressor motor horsepower |  |  |  |  | User entry |  |  |  | hp |  |  | Custom entry based on refrigeration system
|  |  | Weighted average of annual outside dry bulb temperatures (DBi) across 10 temperature bins between 56°F and 75°F, ONLY during Hawaii's peak demand hours of 5-9 pm |  |  |  |  | 72.3385 |  |  |  | °F |  |  | Bin analysis of TMY data for Honolulu, Hawaii. Calculated with this approach:
|  |  | Weighted average of annual outside dry bulb temperatures (DBj) across 10 temperature bins between 56°F and 75°F, any time of day |  |  |  |  | 70.9013 |  |  |  | °F |  |  | Bin analysis of TMY data for Honolulu, Hawaii. Calculated with this approach:
|  |  | Annual number of hours the outside dry bulb temperature in Honolulu is ≤75°F |  |  |  |  | 2938 |  |  |  | hrs |  |  | Bin analysis of typical meteorological year (TMY) data for Honolulu, Hawaii
EULEE |  |  | Effective useful life of measure |  |  |  |  | 15 |  |  |  | yrs |  |  | DEER 2020
1 Regional Technical Forum. Floating Head Pressure Controls on Single Compressor Systems - Unit Energy Savings Workbook, Version 2.1. Northwest Power and Conservation Council. September 20, 2019. Spreadsheet: "ComGroceryFHPCSingleCompressor_v2_1.xlsm." See "Savings" sheet for assumptions about condenser fan controls, compressor COP, compressor oversize factor, suction temperature setpoints, etc. See "SavingsData&Analysis" sheet for modeling results. <https://nwcouncil.app.box.com/v/ComGroceryFHPCv2-1>.
2 AEG's 2020 Analysis File titled "AEG HPUC - New Com Refrig Measures - Analysis File." See sheets named "DB analysis for kWh - AEG" and "DB analysis for peak kW - AEG."
Table 1: Linear Interpolation Constants, by Refrigeration System Type
Type |  |  |  | Medium Temp |  |  |  |  | Low Temp
|  |  |  | m |  | b |  |  | m |  |  |  | b
Unitary Condenser |  |  |  | -0.0019629 |  | 0.14722 |  |  | -0.0038654 |  |  |  | 0.2899
Remote Condenser |  |  |  | -0.0064624 |  | 0.48468 |  |  | -0.008078 |  |  |  | 0.60585
Table 2: Assumed Distribution of Refrigeration Types in Hawaii Supermarkets
Type |  |  |  | Medium Temp |  |  |  | Low Temp
Unitary Condenser |  |  |  | 37.5% |  |  |  | 12.5%
Remote Condenser |  |  |  | 37.5% |  |  |  | 12.5%
Note: The distribution factors were estimated by Hawai'i Energy. They are used to determine default impacts for an "average" or "unknown" type of refrigeration system.
Table 3: Deemed Savings Per Unit of Compressor Motor Horsepower
Type | [6 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  |  | Lifetime Energy Savings |  |  | Estimated Fraction of Systems
[7 empty] | kW/hp |  |  |  | kWh/hp-yr |  |  | kWh/hp
Medium Temp with Unitary Condenser | [6 empty] | 0.0052242 |  |  |  | 23.637 |  |  | 354.5555 |  |  | 0.375
Medium Temp with Remote Condenser | [6 empty] | 0.0172 |  |  |  | 77.8204 |  |  | 1167.3058 |  |  | 0.375
Low Temp with Unitary Condenser | [6 empty] | 0.010288 |  |  |  | 46.5468 |  |  | 698.2016 |  |  | 0.125
Low Temp with Remote Condenser | [6 empty] | 0.0215 |  |  |  | 97.2755 |  |  | 1459.1322 |  |  | 0.125
Unknown | [6 empty] | 0.012382 |  |  |  | 56.0243 |  |  | 840.3647
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Select Type of Refrigeration System
Unknown
Enter Horsepower of Compressor Motor
1
Measure Name |  |  |  |  | Peak Demand Savings |  |  |  |  | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Floating Head Pressure Controls |  |  |  |  | 0.012 |  |  |  |  | 56.02 | [5 empty] | 840.36
RESOURCES
• | AEG's 2020 Analysis Files titled "AEG HPUC - New Com Refrig Measures - Analysis File" and "3 - Weather Analysis - EPW-HI Portland and CA - TMY.xlsx."
• | Efficiency Vermont. “Technical Reference User Manual (TRM): Measure Savings Algorithms and Cost Assumptions.” P. 68. Dec 31, 2018.
• | Public Service Commission of Wisconsin. "Wisconsin Focus on Energy 2020 Technical Reference Manual." Pp.781-784.
• | Regional Technical Forum. "Floating Head Pressure Controls on Single Compressor Systems - Unit Energy Savings Workbook, Version 2.1." Northwest Power and Conservation Council. September 20, 2019. Spreadsheet: "ComGroceryFHPCSingleCompressor_v2_1.xlsm."
∆𝑘𝑊ℎ=[(𝑚∗(𝐷𝐵) ̅_(≤75°𝐹)+𝑏)∗ℎ𝑝]∗〖𝐻𝑜𝑢𝑟𝑠〗_(𝐷𝐵≤75°𝐹)
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
∆𝑘𝑊=(𝑚∗(𝐷𝐵) ̅_(≤75°𝐹,5−9𝑝𝑚)+𝑏)∗ℎ𝑝
(𝐷𝐵) ̅_(≤75°𝐹,5−9𝑝𝑚)
(𝐷𝐵) ̅_(≤75°𝐹)
〖𝐻𝑜𝑢𝑟𝑠〗_(𝐷𝐵≤75°𝐹)
(∑_1^10▒〖〖𝐷𝐵〗_𝑖∗〖𝐻𝑜𝑢𝑟𝑠〗_𝑖 〗)/(∑_1^10▒〖𝐻𝑜𝑢𝑟𝑠〗_𝑖 ),5−9𝑝𝑚
(∑_1^10▒〖〖𝐷𝐵〗_𝑗∗〖𝐻𝑜𝑢𝑟𝑠〗_𝑗 〗)/(∑_1^10▒〖𝐻𝑜𝑢𝑟𝑠〗_𝑗 )

## C_SubMeter_Condominium
COMMERCIAL: Condominium Submetering
Return to TOC
MEASURE DETAILS
Description
This program is to assist master-metered condominiums and their Association of Apartment Owners (AOAO) efforts to reduce energy consumption and implement the current submetering proposal as one that will insure both equity and fairness in allocating energy costs as well as encouraging energy conservation through direct feedback of personal energy use to tenants. The combination of billing submeters, along with education, peer group comparisons and special equipment offerings, will assist the tenant achieve significant energy conservation and efficiency.
Program Criteria
The manufacturer’s submetering system model type to be installed (meter and CTs) must have been tested by an independent third party that is Nationally Rated Testing Laboratory certified for ANSI C12.1. The certification documentation must be provided to the Program prior to installation. Additionally, manufacturers must have a factory-quality compliance procedure in place to ensure meter accuracy. Documentation of this procedure must be available to the Program upon request. The submeter must be UL, CSA or ETL listed (Electrical Safety). Requirements: • The metering system must remain in place and billing to occur for a period of at least five (5) years or a pro-rated portion of the incentive will be recovered by Hawai‘i Energy. Provide Hawai‘i Energy with energy meter data for analysis purposes. • A joint educational and monitoring program will be undertaken with AOAO to assist in the verification of savings and development of an ongoing energy incentive offering for other condominiums in Hawai‘i.
Unit of Measure
Per tenant unit
Baseline Equipment
The base case is no submetering. Baseline Annual Energy Usage is the actual average usage (kWh/year) based on historical usage for past 24 months (or as appropriate) for entire condominium (master metered) divided by the number of condominium units. Baseline demand (kW) is the Average Historical Demand divided by the number of condominium units.
High Efficiency Equipment
The high efficiency case is with submetering. It is expected there will be a 10% reduction in energy usage and 8% reduction in peak demand during (5PM – 9PM).
ALGORITHMS
SAVINGS
Example Savings Calculation:

## C_SubMeter_Small Business
COMMERCIAL: Small Business Submetering
Return to TOC
MEASURE DETAILS
Description
This program is to assist master-metered small businesses to reduce energy consumption that will insure both equity and fairness in allocating energy costs as well as encouraging energy conservation through direct feedback of personal energy use to business tenants. The combination of billing submeters, along with education, peer group comparisons and special equipment offerings, will assist the tenant achieve significant energy conservation and efficiency.
Program Criteria
The manufacturer’s submetering system model type to be installed (meter and CTs) must have been tested by an independent third party that is Nationally Rated Testing Laboratory certified for ANSI C12.1. The certification documentation must be provided to the Program prior to installation. Additionally, manufacturers must have a factory-quality compliance procedure in place to ensure meter accuracy. Documentation of this procedure must be available to the Program upon request. The submeter must be UL, CSA or ETL listed (Electrical Safety). Requirements: • The metering system must remain in place and billing to occur for a period of at least five (5) years or a pro-rated portion of the incentive will be recovered by Hawai‘i Energy. Provide Hawai‘i Energy with energy meter data for analysis purposes. • A joint educational and monitoring program will be undertaken with the businesses to assist in the verification of savings and development of an ongoing energy incentive offering for other condominiums in Hawai‘i.
Unit of Measure
Baseline Equipment
The base case is no submetering.
High Efficiency Equipment
The high efficiency case is with submetering.
ALGORITHMS
| Building Type | Demand Savings (kW) | Annual Energy Savings (kWh/year)
| Small Business | 0.24 | 1080
| Operational Factor | Adjustment Factor
| Persistence Factor (PF) | 1
| Coincidence Factor (CF) | 1
SAVINGS
Example Savings Calculation:

## Dropdown (hidden)
R_Light_LED | R_Light_Occupancy Sensor | C_WH_Solar | C_WH_Solar | C_WH_Solar | C_HVAC_VFD Water Pump |  | R_HVAC_AC_WKST
Incandescent Wattage | Are controlled lamps energy efficient | Building Type for Semi-Prescriptive Approach | Orientation (° to true North) | Collector Tilt (degrees) | Project type | Baseline controls | Pre-2006
40 | Yes | Avg. Commercial | 90-104 | 14-39 | Fan VFD | Constant Volume | 2006 and Later
60 | No | Education | 105-114 | 40-44 | Pump VFD | Inlet Guide Vane, FC | NA
75 |  | Grocery | 115-124 | 45-49 |  | Inlet Damper Box
100 |  | Health | 125-134 | 50-54 |  | Outlet Damper
|  | Hotel/Motel | 135-224 | 55-59 |  | Eddy Current Drive
|  | Office | 225-234 | 60 |  | Throttle Valve
|  | Restaurant | 235-244
245-254
255-270
R_WH_Solar
County
Unspecified
Honolulu
Maui
Hawai‘i

## C_WH_Solar
COMMERCIAL: Solar Water Heater
Return to TOC
UPDATE STATUS
Updated in January 2019 for PY19 TRM.
MEASURE DETAILS
Description
Replacement of an Electric Storage Water Heater with a Solar Water Heater for Service Water Heating in an existing commercial building. Solar Water Heating systems use solar thermal energy to meet most of the water heating load and continue to utilize electricity to operate the circulation pump and provide heating through an electric resistance element when needed.
The semi-prescriptive approach presented here is reserved for smaller, simpler systems where the baseline Electric Storage Water Heater has an input rating of 12 kW (40,950 Btu/hr) or less and the square footage of the building or area served by the solar water heating system is known. A fully custom approach should be used for larger or more complex installations, and/or when the water heating load served by the solar water heater is more accurately known.
Program Criteria
The Solar Water Heating collectors must meet the Solar Rating and Certification Corporation (SRCC™) OG-100 standard. OG-300 certification for the solar water heating system is not required.
Unit of Measure
One system.
Baseline Equipment
Baseline equipment for the semi-prescriptive approach is an Electric Storage Water Heater with an input rating of 12 kW (40,950 Btu/hr) or less that meets current Federal codes and standards, which were effective April 16, 2015. (Commercial water heaters with an input rating of ≤ 12 kW must meet the Residential standards per a ruling by the Department of Energy.)
High Efficiency Equipment
High efficiency equipment is a new Solar Water Heater with electric backup designed for a 90% Solar Fraction. The Solar Water Heating collectors must meet the Solar Rating and Certification Corporation (SRCC™) OG-100 standard. OG-300 certification for the solar water heating system is not required. Solar Water Heating systems use solar thermal energy to meet most of the water heating load and continue to utilize electricity to operate the circulation pump and provide heating through an electric resistance element when needed.
ALGORITHMS
Energy Factor of Baseline Equipment (Electric Storage Water Heater ≤ 55 gallons)
(1)
Energy Factor of Baseline Equipment (Electric Storage Water Heater > 55 gallons)
(2)
Baseline Annual Energy Use, kWh/hr
(3)
Efficient Case Annual Energy Use, kWh/hr
(4)
Annual Energy Savings, kWh/yr
(5)
Peak Demand Reduction, kW
(6)
Lifetime Energy Savings, kWh
(7)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [10 empty] | Value |  |  |  | Unit |  |  |  | Source/Notes
EFbase |  |  |  | Energy factor of the baseline equipment | [10 empty] | See Eq'ns 1 or 2 |  |  |  | - |  |  |  | Minimum federal requirements effective April 16, 20151
V |  |  |  | Rated Storage Volume of baseline Electric Storage Water Heater tank | [10 empty] | User input |  |  |  | gal |  |  |  | -
HWper SqFt |  |  |  | Average annual hot water use per square foot of building space | [10 empty] | See Table 1 |  |  |  | gal/SqFt |  |  |  | DEER 2015 "DEER-WaterHeater-Calculator-v1.1.xlsm"2
A |  |  |  | Square footage of area served by new Solar Water Heater | [10 empty] | User input |  |  |  | SqFt |  |  |  | -
ρ |  |  |  | Density of water | [10 empty] | 8.3 |  |  |  | lbm/gal |  |  |  | -
cp |  |  |  | Specific heat capacity of water | [10 empty] | 1 |  |  |  | Btu/lbm°F |  |  |  | -
Tout |  |  |  | Outlet temperature of the water heater | [10 empty] | User input |  |  |  | °F |  |  |  | -
Tin |  |  |  | Incoming water temperature from the water main | [10 empty] | User input |  |  |  | °F |  |  |  | -
SF |  |  |  | Solar fraction | [10 empty] | User input |  |  |  | - |  |  |  | Program requirement of 0.9
EFSWH |  |  |  | Energy factor of solar water heater when using back-up electric resistance heating | [10 empty] | 0.9 |  |  |  | - |  |  |  | Typical value for electric resistance water heating; equal to efficiency assumption of 0.9 from PY18 TRM
kWpump |  |  |  | Circulation pump demand | [10 empty] | 0.082 |  |  |  | kW |  |  |  | Source: KEMA 2005-2007; consistent with residential solar water heating measure3
HOUpump |  |  |  | Pump hours of operation | [10 empty] | 1292 |  |  |  | hr/yr |  |  |  | Source: KEMA 2005-2007; consistent with residential solar water heating measure3
PF | PF | PF | PF | Persistence factor | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | 0.93 | 0.93 | 0.93 | 0.93 | - |  |  |  | Source: KEMA 2005-2007; consistent with residential solar water heating measure3
M |  |  |  | Multiplier to scale circulation pump energy use for medium-sized systems | [10 empty] | 1.0 for small; 1.5 for medium |  |  |  | - |  |  |  | Assumes small commercial systems have same circulation pump energy requirements as residential systems and medium commercial systems have greater (1.5X) circulation pump energy requirements4
EFLH | HOURS | HOURS | HOURS | Equivalent full load hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | See Table 1 |  |  |  | hrs |  |  |  | AEG's Hawai‘i-specific analysis of U.S. DOE OpenEI Load shapes for Commercial Water Heating
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | See Table 1 |  |  |  | - |  |  |  | AEG's Hawai‘i-specific analysis of U.S. DOE OpenEI Load shapes for Commercial Water Heating; peak period defined as non-holiday weekdays from 5-9 pm
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 18 | 20 years | 20 years | 20 years | yrs |  |  |  | AEG's Fall 2018 Benchmarking
1 Federal Register, Energy Conservation Program for Consumer Products: Definitions for Residential Water Heaters, Table I.2, April 8, 2015, available here: https://www.federalregister.gov/documents/2015/04/08/2015-07956/energy-conservation-program-for-consumer-products-definitions-for-residential-water-heaters. Applies to residential and non-residential water heaters that are ≤12 kW.
2 AEG assumes average hot water use per square footage of commercial building space is similar in California and Hawai‘i.
3 See "R_WH_SWH" tab for more details. The kWpump, HOUpump, and PF values should be updated as better data specific to the commercial sector becomes available.
4 Small systems are defined as those with a baseline electric storage water heater of ≤ 55 gal. Medium systems are defined as those with a baseline electric storage water heater of >55 gal and input rating ≤ 12 kW. Larger systems are to be treated with a custom approach. The approach to estimate circulation pump energy use for commercial applications should be updated as better data specific to the commercial sector becomes available.
Table 1. Key Parameters for Semi-Prescriptive Approach
Building Type | [9 empty] | HWper SqFt (gal/ft2-yr) |  |  |  |  | EFLH |  |  |  |  | CF
Avg. Commercial | [9 empty] | 9.78 |  |  |  |  | 2322 |  |  |  |  | 0.29
Cold Storage | [9 empty] | 0.23 |  |  |  |  | Varies |  |  |  |  | Varies
Education | [9 empty] | 7.58 |  |  |  |  | 1916 |  |  |  |  | 0.25
Grocery | [9 empty] | 10.6 |  |  |  |  | 4406 |  |  |  |  | 0.6
Health | [9 empty] | 22.7 |  |  |  |  | 2247 |  |  |  |  | 0.2
Hotel/Motel | [9 empty] | 12.61 |  |  |  |  | 3008 |  |  |  |  | 0.35
Industrial | [9 empty] | 2.83 |  |  |  |  | Varies |  |  |  |  | Varies
Office | [9 empty] | 2.07 |  |  |  |  | 2632 |  |  |  |  | 0.3
Restaurant | [9 empty] | 74.91 |  |  |  |  | 3947 |  |  |  |  | 0.74
Retail | [9 empty] | 1.49 |  |  |  |  | Varies |  |  |  |  | Varies
Warehouse | [9 empty] | 0.23 |  |  |  |  | Varies |  |  |  |  | Varies
Use custom approach for entries noted as "Varies."
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
Enter Equivalent Rated Storage Volume in gallons for Electric Storage Water Heater, V
|  |  | 50 | [5 empty] | EF= |  | 0.945 |  |  |  |  | M= |  | 1
Enter Solar Fraction for new Solar Water Heater (default of 0.9), SF
0.9
Select Building Type from Dropdown List
|  |  | Grocery | [8 empty] | HWper SqFt = |  |  |  | 10.6 |  |  |  | EFLH = |  |  | 4406 |  | CF = | 0.6
Enter Square Footage of Area Served by Solar Water Heater, A
|  |  | 1800 |  |  | SqFt
Enter inlet temperature of the water heater, Tin
(default of 75°F for Honolulu and Hawai‘i Counties, and 71°F for Maui County)
|  |  | 75 |  |  | °F
Enter outlet temperature of the water heater (default of 130°F), Tout
|  |  | 130 |  |  | °F
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Commercial Solar Water Heater | [7 empty] | 0.293 | [7 empty] | 2149.93 | [7 empty] | 38698.74
Note: Savings in blue result from sample entries above. They are for illustrative purposes only.
RESOURCES
• | 2015 International Energy Conservation Code, Chapter 4: Commercial Energy Efficiency, Section C404: Service Water Heating (Mandatory), https://codes.iccsafe.org/content/IECC2015/chapter-4-ce-commercial-energy-efficiency.
• | AEG's 2018 Analysis Files titled 1) "AEG HPUC Update of Com-Solar Water Heater - Analysis file" and 2) "R&C Solar Water Heater - v2 Solar Fraction."
• | AEG's 2018 Analysis of U.S. DOE OpenEI Load shapes for Commercial Water Heating. Analyzed 16 commercial building types (based off the DOE commercial reference building models) for IECC Zone 1A and Hawai‘i weather stations (Keahole-Kona.Intl.AP, Honolulu.Intl.AP, Kahului.AP). Prototype data available here: https://openei.org/doe-opendata/dataset/commercial-and-residential-hourly-load-profiles-for-all-tmy3-locations-in-the-united-states.
• | A.O. Smith responses to ENERGY STAR 2.0 framework specification for water heaters, ENERGY STAR Water Heaters Product Specification Framework May 2011, Questions for Discussion, Q9: "9. How does the SEF metric compare to EF metric? Could they be considered equivalent compared?..." https://www.energystar.gov/sites/default/files/specs/AOSmith%20Comments_0.pdf.
• | Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, November 6, 2013, With errata February 26, 2014, Evergreen Economics, Figure 87.
• | DEER 2015 Small Storage and Small Instantaneous Water Heater Energy Use Calculator. Filename: "DEER-WaterHeater-Calculator-v1.1.xlsm," "TechCalc" sheet. Spreadsheet dated 11/29/2014. AEG used for analysis of hot water usage (Gal/SqFt-yr) by building type.
• | Energy and Peak Demand Impact Evaluation Report of the 2005-2007 Demand Management Programs – (KEMA 2005-07)
• | ENERGY STAR Program Requirement for Residential Water Heaters, v3.0, April 2015. https://www.energystar.gov/products/water_heaters/residential_water_heaters_key_product_criteria.
• | Federal Register, Energy Conservation Program for Consumer Products: Definitions for Residential Water Heaters, April 8, 2015, available here: https://www.federalregister.gov/documents/2015/04/08/2015-07956/energy-conservation-program-for-consumer-products-definitions-for-residential-water-heaters.
• | Hawai‘i Energy PY17 Program Data for BEEM. Filename: "EMV Extract UPDATED 20181015." Spreadsheet. AEG used data to develop shares of participant energy savings (kWh) by building type. The shares were then used to estimate weighted averages of key parameters (HWper SQFT, EFLH, and CF) for the average commercial building type ("Avg. Commercial").
• | Hawai‘i Energy Solar Water Heating Program Handbook: Design Guidelines, Volume 5, October 2018, available for download here: <https://hawaiienergy.com/files/for-homes/swh_handbook.pdf>.
• | International Code Council (ICC) and Solar Rating & Certification Corporation (SRCC), 2015 ICC 900/SRCC 300-2015 Solar, Thermal System Standard, https://codes.iccsafe.org/content/ICC9002015/toc.
• | Technical Reference Manual, State of Pennsylvania, Act 129 Energy Efficiency and Conservation Program & Act 213 Alternative Energy Portfolio Standards, June 2016.
• | Title 10: Energy, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart B—Test Procedures, Appendix E to Subpart B of Part 430—Uniform Test Method for Measuring the Energy Consumption of Water Heaters, https://www.ecfr.gov/cgi-bin/text-idx?SID=80dfa785ea350ebeee184bb0ae03e7f0&mc=true&node=ap10.3.430_127.e&rgn=div9.
• | Title 10: Energy, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates, (d) Water heaters.
∆𝑘𝑊=∆𝑘𝑊ℎ/𝐸𝐹𝐿𝐻∗𝐶𝐹
〖𝐸𝐹〗_(𝑏𝑎𝑠𝑒,≤55)=0.960−(0.0003∗𝑉)
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
〖𝐸𝐹〗_(𝑏𝑎𝑠𝑒,>55)=2.057−(0.00113∗𝑉)
〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒=(1/〖𝐸𝐹〗_𝑏𝑎𝑠𝑒 )∗(〖𝐻𝑊〗_(𝑝𝑒𝑟 𝑆𝑞𝐹𝑡)∗𝐴∗𝜌∗𝑐_𝑝∗(𝑇_𝑜𝑢𝑡−𝑇_𝑖𝑛 ))/(3412 𝐵𝑡𝑢/𝑘𝑊ℎ)
〖𝑘𝑊ℎ〗_𝐸𝐸=(1−𝑆𝐹)(1/〖𝐸𝐹〗_𝑆𝑊𝐻 )∗(〖𝐻𝑊〗_(𝑝𝑒𝑟 𝑆𝑞𝐹𝑡)∗𝐴∗𝜌∗𝑐_𝑝∗(𝑇_𝑜𝑢𝑡−𝑇_𝑖𝑛 ))/(3412 𝐵𝑡𝑢/𝑘𝑊ℎ)+〖(𝑘𝑊〗_𝑝𝑢𝑚𝑝∗〖𝐻𝑂𝑈〗_𝑝𝑢𝑚𝑝)∗𝑀
∆𝑘𝑊ℎ=(〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊ℎ〗_𝐸𝐸 )∗𝑃𝐹

## C_WH_Heat Pump
COMMERCIAL: Heat Pump Water Heater
Return to TOC
UPDATE STATUS
Added in Winter 2021-2022 for PY22 TRM.
MEASURE DETAILS
Description
Replacement of a Light Duty Electric Resistance Storage Water Heater with an ENERGY STAR-certified Heat Pump Water Heater with a tank size of up to 120 gallons. The water heater is to be used for service water heating in an existing commercial building.
The deemed and semi-prescriptive approaches presented here are reserved for light duty, smaller, simpler systems installed in offices, grocery stores, or restaurants where the baseline Electric Storage Water Heater has an input rating of 12 kW (40,950 Btu/hr) or less. A fully custom approach should be used for different commercial building types and for larger or more complex installations.
Program Criteria
Rebate applications for water heaters are provided by the retailers at the time of purchase or a customer can visit our website and download the form. Rebate applications must include an original purchase receipt showing brand and model number.
Unit of Measure
One water heater
Baseline Equipment
Baseline equipment for the deemed and semi-prescriptive approach is a Light Duty Electric Storage Water Heater with an input rating of 12 kW (40,950 Btu/hr) or less that meets current Federal standards listed in Table 1 below, which were effective April 16, 2015. (Commercial water heaters with an input rating of ≤ 12 kW must meet the Residential standards per a ruling by the Department of Energy.)
High Efficiency Equipment
To qualify for this measure, the installed equipment must be an ENERGY STAR Heat Pump water heater with a tank size of up to 120 gallons. ENERGY STAR qualifying equipment must reach the requirements outlined below in Table 2.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [10 empty] | Value |  |  |  | Unit |  | Source/Notes
UEFbase |  |  |  | Uniform Energy Factor of the baseline | [10 empty] | User input or Table 1 |  |  |  | - |  | Must meet Federal Regulations.1
DP |  |  |  | Draw Pattern | [10 empty] | See Table 3 |  |  |  | - |  | Default values in Table 3 are based on AEG's engineering judgement.
Vr |  |  |  | Rated Storage Volume of Water Heater Tank | [10 empty] | See Table 3 |  |  |  | gal |  | Default values in Table 3 are from Evergreen Economics' 2014 Baseline Study,2 Section E.2.1, Mean Storage Volume. Rounded to nearest gallon.
UEFEff for ≤ 55 gal |  |  |  | Uniform Energy Factor of the most common Heat Pump Water Heaters sized less than or equal to 55 gallons according to the ENERGY STAR database | [10 empty] | 3.45 |  |  |  | - |  | ENERGY STAR Product Finder (Jan 2022): <https://www.energystar.gov/productfinder/product/certified-water-heaters/results>.
UEFEff for > 55 gal |  |  |  | Uniform Energy Factor of the most common Heat Pump Water Heaters sized above 55 gallons according to the ENERGY STAR database | [10 empty] | 3.45 |  |  |  | - |  | ENERGY STAR Product Finder (Jan 2022): <https://www.energystar.gov/productfinder/product/certified-water-heaters/results>.
HWper SqFt |  |  |  | Average annual hot water use per square foot of building space | [10 empty] | See Table 3 |  |  |  | gal/SqFt |  | DEER 2015 "DEER-WaterHeater-Calculator-v1.1.xlsm."3
A |  |  |  | Square footage of area served by new Solar Water Heater | [10 empty] | User input or Table 3 |  |  |  | SqFt |  | Default values in Table 3 from Evergreen Economics' 2014 Baseline Study,2 Section E.2.1, Mean Building Area.
ρ |  |  |  | Density of water | [10 empty] | 8.3 |  |  |  | lbm/gal |  | -
cp |  |  |  | Specific heat capacity of water | [10 empty] | 1 |  |  |  | Btu/lbm°F |  | -
Tout |  |  |  | Outlet temperature of the water heater | [10 empty] | 125 |  |  |  | °F |  | Outlet water temperatures typically range from 120 to 140°F. 125 ± 5°F is the temperature prescribed in Uniform Test Method for Measuring the Energy Consumption of Water Heaters.4
Tin |  |  |  | Incoming water temperature from the water main | [10 empty] | 75 | 8760 | 8760 | 8760 | °F |  | Hawai‘i Energy.5
EFLH | HOURS | HOURS | HOURS | Equivalent full load hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | See Table 3 |  |  |  | hrs |  | AEG's 2018 Hawaii-specific analysis of U.S. DOE OpenEI Load shapes for Commercial Water Heating.
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | See Table 3 |  |  |  | - |  | AEG's 2018 Hawaii-specific analysis of U.S. DOE OpenEI Load shapes for Commercial Water Heating; peak period defined as non-holiday weekdays from 5-9 pm.
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 10 |  |  |  | yrs |  | DEER 2020
1. Source for UEF equation: Electronic Code of Federal Regulations, <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>. (See Table 1 below.)
2. Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, Prepared by Evergreen Economics, February 26, 2014. Appendix E.
3. AEG assumes average hot water use per square footage of commercial building space is similar in California and Hawaii.
4. Source for Tout: Electronic Code of Federal Regulations, Appendix E to Subpart B of Part 430 <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-B>.
5. Hawai‘i Energy's Solar Water Heating Program Handbook, Table 2.
Table 1. Federal Standards for Electric Storage Water Heaters
Source: Electronic Code of Federal Regulations, <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>. Has been collapsed to show just electric storage water heaters.
Table 1. Criteria for Certified Electric Water Heaters
Criteria | [17 empty] | ENERGY STAR Version 4.0 Requirements, Effective Jan. 5, 2022
Uniform Energy Factor | [7 empty] | Integrated HPWH | [9 empty] | UEF ≥ 3.30
[8 empty] | Integrated HPWH, 120 Volt / 15 Amp Circuit | [9 empty] | UEF ≥ 2.20
[8 empty] | Split-system HPWH | [9 empty] | UEF ≥ 2.20
First-Hour Rating | [17 empty] | FHR ≥ 45 gallons per hour
Warranty | [17 empty] | Warranty ≥ 6 years on sealed system
Safety | [17 empty] | UL 174 and UL 1995
Lower Compressor Cut-Off Temperature (Reporting Requirement Only) | [17 empty] | Report ambient temperature below which the compressor cuts off and electric resistance only operation begins
Source: ENERGY STAR Program Requirements, Product Specification for Residential Water Heaters, V4.0, <https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Version%204.0%20Water%20Heaters%20Final%20Specification%20and%20Partner%20Commitments_0.pdf>.
Table 3. Default Values for Key Parameters
Building Type |  |  |  | Vr (gal) |  |  |  | Draw Pattern |  |  |  | Baseline UEF |  |  |  | HWper SqFt (gal/ft2-yr) |  |  |  | Building Area, A (ft2) |  | EFLH | CF
Office |  |  |  | 48 |  |  |  | Very Small |  |  |  | 0.8424 |  |  |  | 2.07 |  |  |  | 2690 |  | 2632 | 0.3
Grocery |  |  |  | 50 |  |  |  | Low |  |  |  | 0.9104 |  |  |  | 10.6 |  |  |  | 1980 |  | 4406 | 0.6
Restaurant |  |  |  | 65 |  |  |  | High |  |  |  | 2.1703 |  |  |  | 74.91 |  |  |  | 2060 |  | 3947 | 0.74
SAVINGS
Deemed Savings (based on default values for key parameters)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Office | [7 empty] | 0.069 | [7 empty] | 607.67 | [5 empty] | 6076.7
Grocery | [7 empty] | 0.281 | [7 empty] | 2064.07 | [5 empty] | 20640.7
Restaurant | [7 empty] | 0.601 | [7 empty] | 3207.86 | [5 empty] | 32078.6
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
|  | Enter Building Type | [12 empty] | Enter Building Floor Area Served by Water Heater
[5 empty] | Office | [14 empty] | 2690
|  | Enter Baseline UEF | [12 empty] | Enter ENERGY STAR UEF
[5 empty] | 0.8424 | [14 empty] | 3.45
|  | HWper SqFt = |  |  |  | 2.07 |  |  |  | EFLH = |  |  | 2632 |  |  |  | CF = |  |  | 0.3
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Office | [7 empty] | 0.069 | [7 empty] | 607.67 | [5 empty] | 6076.7
Note: Savings in blue result from sample entries above. They are for illustrative purposes only.
RESOURCES
• | AEG's 2022 Analysis File titled "PY22 C_WH_Heat Pump - Analysis File."
• | AEG's 2018 Analysis of U.S. DOE OpenEI Load shapes for Commercial Water Heating. Analyzed 16 commercial building types (based off the DOE commercial reference building models) for IECC Zone 1A and Hawai‘i weather stations (Keahole-Kona.Intl.AP, Honolulu.Intl.AP, Kahului.AP). Prototype data available here: <https://openei.org/doe-opendata/dataset/commercial-and-residential-hourly-load-profiles-for-all-tmy3-locations-in-the-united-states>.
• | Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, Prepared by Evergreen Economics, February 26, 2014. Appendix E. Section E.2.1 Means by Business Type.
• | DEER 2015 Small Storage and Small Instantaneous Water Heater Energy Use Calculator. Filename: "DEER-WaterHeater-Calculator-v1.1.xlsm," "TechCalc" sheet. Spreadsheet dated 11/29/2014. AEG used for analysis of hot water usage (Gal/SqFt-yr) by building type.
• | DEER 2020: <http://www.deeresources.com/index.php/deer-versions/deer2020#EUL>.
• | Electronic Code of Federal Regulations: Title 10: Energy, Part 430 - Energy Conservation Program for Consumer Products. Subpart C - Energy and Water Conservation Standards. Section 6d. <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>.
• | Electronic Code of Federal Regulations, Appendix E to Subpart B of Part 430 <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-B>.
• | ENERGY STAR Product Finder: <https://www.energystar.gov/productfinder/product/certified-water-heaters/results>.
• | ENERGY STAR Program Requirements, Product Specification for Residential Water Heaters, V4.0, effective Jan. 5, 2022, <https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Version%204.0%20Water%20Heaters%20Final%20Specification%20and%20Partner%20Commitments_0.pdf>.
∆𝑘𝑊=∆𝑘𝑊ℎ/𝐸𝐹𝐿𝐻∗𝐶𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
∆𝑘𝑊ℎ=(1/〖𝑈𝐸𝐹〗_𝑏𝑎𝑠𝑒 −1/〖𝑈𝐸𝐹〗_𝐸𝑓𝑓 )∗(〖𝐻𝑊〗_(𝑝𝑒𝑟 𝑆𝑞𝐹𝑡)∗𝐴∗𝜌∗𝑐_𝑝∗(𝑇_𝑜𝑢𝑡−𝑇_𝑖𝑛 ))/(3412 𝐵𝑡𝑢/𝑘𝑊ℎ)

## C_WH_Smart Circ Pump
COMMERCIAL: Smart Circulator Pump for Domestic Hot Water
Return to TOC
UPDATE STATUS
Introduced in Spring 2026 for the PY26 TRM.
MEASURE DETAILS
Description
This measure involves the commercial building installation of a smart circulator pump to optimize commercial domestic hot water (DHW) systems by adjusting flow based on real-time demand, utilizing an electronically commutated motor (ECM) and a variable frequency drive (VFD). These are typically fractional horse power motors, up to 2 HP.
Program Criteria
| • | A circulator pump is a specific type of in-line pump used to circulate liquids in a closed distribution system. This measure covers small circulator pumps (≤ 2 HP). 2 HP is the maximum eligible horsepower rating for Hawaii's climate zone because, above 2 HP, IECC 2018 requires all motors installed in climate zone 1 to have VFDs.
| • | A "smart" system will contain a VFD that can modulate the flow of the circulator pump according to the on-demand controls.
| • | This measure applies to retrofit projects only. This restriction is because code requires demand controls for new construction. See IECC 2018, section C404.7 Demand Recirculation Controls, which states the following for recirculation water systems: "1. The controls shall start the pump upon receiving a signal from the action of a user of a fixture or appliance, sensing the presence of a user of a fixture or sensing the flow of hot or tempered water to a fixture fitting or appliance. 2. The controls shall limit the temperature of the water entering the cold-water piping to not greater than 104°F".
Unit of Measure
Per pump.
Baseline Equipment
A circulator pump with a constant speed, induction motor and on/off timer controls.
High Efficiency Equipment
For retrofit projects, the efficient case is a smart circulator pump with an electronically commutated motor (ECM) and variable speed capability with on-demand controls strategy.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  |  | Value |  | Unit | Source/Notes
WBase |  |  | Average input wattage of baseline induction motor per nameplate rated HP |  |  |  | See Table 1 |  | W | Table 1 data is from Regional Technical Forum (RTF), Circulator Pump measure v4.1
WEff |  |  | Average input wattage of efficient ECM per nameplate rated HP, adjusted to reflect VFD control |  |  |  | See Table 1 |  | W | Table 1 data is from RTF, Circulator Pump measure v4.1
HOUBase |  |  | Baseline pump annual hours of use. If table lists "varies", then project must be submitted as Custom |  |  |  | See Table 2 |  | hrs | ICF's 2026 analysis 1
HOUEff |  |  | Efficient pump annual hours of use. If table lists "varies", then project must be submitted as Custom |  |  |  | See Table 2 |  | hrs | ICF's 2026 analysis 2
CFBase |  |  | Coincidence factor of baseline case. If table lists "varies", then project must be submitted as Custom |  |  |  | See Table 2; Actual if "Varies" |  |  | ICF's 2026 analysis 3
CFEff |  |  | Coincidence factor of efficient case. If table lists "varies", then project must be submitted as Custom |  |  |  | See Table 2; Actual if "Varies" |  |  | ICF's 2026 analysis 4
1000 |  |  | Conversion factor from Watts to kW |  |  |  | 1000 |  | W/kW
EUL |  |  | Effective useful life of measure |  |  |  | 10 |  | years | DOE Effective Useful Life 5
1 Combination of a) the Hawai'i Energy TRM values for commercial water heating from the "EFLH & CF" sheet and b) ICF mapping of NY TRM v13, page 488, DHW circulator operating hours (adjusted to reflect on/off timer controls using benchmarking analysis) to Hawai'i Energy TRM building types for the Industrial, Retail, and Warehouse building types. Refer to ICF's PY26 TRM - Smart Circulator Pumps - Analysis File for more detail.
2 Calculated by adjusting baseline hours (HOUBase) downward to reflect change from on/off timer controls to on-demand controls using benchmarking analysis. Refer to ICF's PY26 TRM - Smart Circulator Pumps - Analysis File for more detail.
3 Combination of a) the Hawai'i Energy TRM values for commercial water heating from the "EFLH & CF" sheet and b) estimated CF values for the Industrial, Retail, and Warehouse building types. Refer to ICF's PY26 TRM - Smart Circulator Pumps - Analysis File for more detail.
4 Calculated by adjusting baseline CF (CFBase) downward to reflect change from on/off timer controls to on-demand controls using benchmarking analysis. Refer to ICF's PY26 TRM - Smart Circulator Pumps - Analysis File for more detail.
5 U.S. Department of Energy, "Circulator Pump Technical Support Document." 2022 <https://www.regulations.gov/document/EERE-2016-BT-STD-0004-0121>.
Table 1: Horsepower Ratings and Input Power in Watts 6
Nominal Motor HP |  |  | Avg. Motor Power (W)
|  |  | Induction Motor | ECM, with VFD
1/40 |  |  | 34 | 13
1/25 |  |  | 62 | 30
1/12 |  |  | 94 | 48
1/6 |  |  | 156 | 81
1/4 |  |  | 196 | 96
1/2 |  |  | 316 | 141
3/4 |  |  | 435 | 185
1 |  |  | 555 | 230
1.5 |  |  | 833 | 345
2 |  |  | 1110 | 460
6 RTF's Circulator Pump measure presentation from 12/05/2023, slide 29, Average Motor Power table. <https://nwcouncil.app.box.com/s/mmjilitbr8cics45euw7938rvp2dp6t9>
Table 2: Hours of Use & CF by Building Type
Building Type |  |  |  | Timer (On/Off) 7 |  | On Demand 8
|  |  |  | HoursBase | CFBase | HoursEff |  | CFEff
Misc./Avg. Commercial |  |  |  | 2880 | 0.37 | 53 |  | 0.01
Cold Storage 9 |  |  |  | Varies | Varies | Varies |  | Varies
Education |  |  |  | 1916 | 0.25 | 36 |  | 0
Grocery |  |  |  | 4406 | 0.6 | 82 |  | 0.01
Health |  |  |  | 2247 | 0.2 | 42 |  | 0
Hotel/Motel |  |  |  | 3008 | 0.35 | 56 |  | 0.01
Industrial |  |  |  | 2340 | 0.27 | 43 |  | 0
Office |  |  |  | 2632 | 0.3 | 49 |  | 0.01
Restaurant |  |  |  | 3947 | 0.74 | 73 |  | 0.01
Retail |  |  |  | 3211 | 0.37 | 60 |  | 0.01
Warehouse |  |  |  | 2145 | 0.24 | 40 |  | 0
7 ICF used the Hawai'i Energy TRM's "EFLH & CF" sheet's DHW values as the on/off timer baseline HOU and CF. Then replaced "Varies" values with mapped HOU values from the NY TRM v13 to Hawai'i building types where available (adjusted to reflect on/off timer controls using benchmarking analysis) using the assumption that DHW use is not going to vary by climate zone. The "Misc./Avg. Commercial" category was created as a weighted average based on Hawaii Energy's PY24 share of program level kWh savings by building type.
8 HOU and CF were determined through ICF's analysis of the change in hours between control types provided by U.S. Department of Energy, "Circulator Pump Technical Support Document." 2022 <https://www.regulations.gov/document/EERE-2016-BT-STD-0004-0121>. The percent change between control types was applied to the baseline HOU and CF to determine efficient case values.
9 Cold Storage did not have enough information to created deemed values. All Cold Storage projects will be submitted as a Custom project and use custom values for circulator pump HOU and CF.
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Select Building Type
Restaurant
Select Horsepower of Motor
1.5
Measure Name |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  |  | Lifetime Energy Savings
Smart Circulator Pumps - DHW |  |  |  | 0.613 |  |  | 3262.67 |  |  |  | 32626.7
Note: Savings in blue result from sample entries above. They are for illustrative purposes only.
RESOURCES
• | ICF's Analysis File titled "PY26 TRM - Smart Circulator Pumps - Analysis File.xlsx"
• | Northwest Council Regional Technical Forum, Circulator Pumps measure, updated Feb 2, 2024 <https://rtf.nwcouncil.org/measure/circulator-pumps/>
• | Regional Technical Forum's Circulator Pump measure presentation, 12/05/2023 <https://nwcouncil.app.box.com/s/mmjilitbr8cics45euw7938rvp2dp6t9>
• | Regional Technical Forum's Circulator Pump measure workbook v4.1, Feb 2, 2024 <https://nwcouncil.box.com/v/circpumps-4-1>
• | New York TRM v13, Section ELECTRONICALLY COMMUTATED (EC) MOTOR – HYDRONIC CIRCULATOR PUMPS, published December 12, 2025 <https://dps.ny.gov/system/files/documents/2026/01/nys-trm-v13_consolidated_clean.pdf>
• | 2026 Illinois TRM v14.0, Volume2, Section 4.3.8 Controls for Central Domestic Hot Water <https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010126_v14.0_Vol_2_C_and_I_09192025_FINAL.pdf>
• | State of Pennsylvania – Technical Reference Manual, Vol. 3: Commercial & Industrial Measures, Rev Date: Sept 2024, Section 3.3.5. ECM CIRCULATOR PUMP <https://www.puc.pa.gov/pcdocs/1848580.pdf>
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Programs, Version 4.0, ECM Circulators measure, published January 31, 2023 <https://mn.gov/commerce-stat/trm/releases/4.0.pdf>
• | California Electronic Technical Reference Manual. “CPUC Support Tables”. “Effective Useful Life and Remaining Useful Life”. Effective Useful Life ID: HiEff Motors. Accessed April 2026. <https://www.caetrm.com/cpuc/table/effusefullife/>
• | U.S. Department of Energy, "Circulator Pump Technical Support Document." 2022 <https://www.regulations.gov/document/EERE-2016-BT-STD-0004-0121>.
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊ℎ=〖[(𝑊〗_𝐵𝑎𝑠𝑒 〖∗〖𝐻𝑂𝑈〗_𝐵𝑎𝑠𝑒)−(𝑊〗_𝐸𝑓𝑓 〖∗𝐻𝑂𝑈〗_𝐸𝑓𝑓)]/1000
∆𝑘𝑊=〖[(𝑊〗_𝐵𝑎𝑠𝑒 〖∗〖𝐶𝐹〗_𝐵𝑎𝑠𝑒)−(𝑊〗_𝐸𝑓𝑓 〖∗𝐶𝐹〗_𝐸𝑓𝑓)]/1000

## C_CA_Receiver Tank
COMMERCIAL: Receiver Tank
Return to TOC
UPDATE STATUS
This new measure was added in Spring 2025 for the Mid-Year PY24 TRM V2. Its effective date is July 1, 2025.
MEASURE DETAILS
Description
Using an air receiver or storage tank will buffer the air demands of the system on the compressor, thus eliminating short cycling. Although a load/unload compressor unloads in response to lowered demand, it does so over a period of time to prevent lubrication oil from foaming. Therefore, reducing the number of cycles reduces the number of transition times from load to unload and saves energy.
Program Criteria
Compressed air systems between 10-75 HP are eligible. Systems greater than 75 HP should be evaluated using a custom approach.
Must meet or exceed a minimum size of 5 gal/CFM rated capacity of all active compressors.
Compressed air system must be operational and operate at least 1,500 hours annually.
Unit of Measure
One air receiver tank.
Baseline Equipment
The baseline equipment is a compressed air system with either inlet modulating and blowdown or load/unload controls.
High Efficiency Equipment
The efficient equipment is a compressed air system with load/unload controls and a minimum of 5 gal/CFM rated capacity of all active compressors. If that value cannot be determined, compressor power can be converted to capacity using the rule-of-thumb of 4.5 CFM/HP. The 4.5 CFM/HP rule of thumb is based on a rotary screw compressor delivering 4 to 5 CFM per HP. See “The Relationship Between Pressure and Flow,” Compressed Air System Best Practices, Industrial Utility Efficiency, 2015. <https://www.airbestpractices.com/system-assessments/pressure/relationship-between-pressure-and-flow-compressed-air-system>.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  |  | Sources/Notes
HP |  |  |  | System nominal horse power | [11 empty] | User Input |  |  |  | HP |  |  | ≥ 10 to ≤ 75 HP
Constant |  |  |  | Compressor motor nominal horse power to full load kW conversion factor | [11 empty] | 0.9 |  |  |  | kW/HP |  |  | 2025 IL TRM1, Compressed Air Analysis2
HRSyear |  |  |  | System total annual hours of operation depending on shift | [11 empty] | See Table 1 |  |  |  | hr/yr |  |  | 2018 VT TRM3, 2025 IL TRM1
CompFBase |  |  |  | Baseline compressor factor for ≥ 10 to ≤ 75 HP compressors depending on control type | [11 empty] | See Table 2 |  |  |  | - |  |  | 2025 IL TRM1, Compressed Air Analysis4
CompFEff |  |  |  | Efficient compressor factor for ≥ 10 to ≤ 75 HP compressors | [11 empty] | See Table 2 |  |  |  | - |  |  | 2025 IL TRM1, Compressed Air Analysis4
CF |  |  |  | Peak demand coincidence factor | [11 empty] | See Table 1 |  |  |  | - |  |  | Estimated based on the overlap of compressor operation with Hawaii's current peak demand period, which is weekdays, 5-9 pm.
EUL |  |  |  | Effective useful life of measure | [11 empty] | 15 |  |  |  | yrs |  |  | Benchmarking of other states' & utilities' TRMs
Sources:
1 2025 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 13.0, Volume 2: Commercial and Industrial Measures, FINAL, 2024. <https://icc.illinois.gov/api/web-management/documents/downloads/public/IL-TRM-Version-13.0-Volumes-1-4-Compiled-Final.pdf>
2 Conversion factor based on Survey of CAGI data sheets from 200 compressors. The underlying data are from a spreadsheet named "IL TRM VSD Air Compressor - Supporting Information v2.xlsx," sheet named "Conversion Factor Analysis." The 0.9 factor represents the average across 85 fixed speed compressors of ≥ 10 to ≤ 75 HP. Refer to "Mid-Year PY24 TRM - Commercial Air Receiver Tank - Analysis File" for Hawaii-specific analysis.
3 Efficiency Vermont Technical Reference User Manual (TRM), Measure Savings Algorithms and Cost Assumptions, 2018. <https://puc.vermont.gov/sites/psbnew/files/doc_library/Vermont%20TRM%20Savings%20Verification%202018%20Version_FINAL.pdf>
4 The underlying data are from a spreadsheet named "IL TRM VSD Air Compressor - Supporting Information v2.xlsx," sheets named "Comp. Factor (Previous, ≤40hp)" and "Compressor Factors (>40 hp)." The factors in Table 2 represent the averages across 77 compressors of ≥ 10 to ≤ 75 HP. Refer to "Mid-Year PY24 TRM - Commercial Air Receiver Tank - Analysis File" for Hawaii-specific analysis.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Table 1. Annual Hours of Operation and Coincidence Factors by Shift
Shift | [6 empty] | Description | [14 empty] | HRSyear |  |  |  |  | CF1
One Shift | [6 empty] | 8 hours per day on weekdays, minus holidays and scheduled down time | [14 empty] | 1976 |  |  |  |  | 0.25
Two Shifts | [6 empty] | 16 hours per day on weekdays, minus holidays and scheduled down time | [14 empty] | 3952 |  |  |  |  | 0.95
Three Shifts | [6 empty] | 24 hours per day on weekdays, minus holidays and scheduled down time | [14 empty] | 5928 |  |  |  |  | 0.95
Continual Operation | [6 empty] | 24 hours per day, 7 days per week, minus holidays and scheduled down time | [14 empty] | 8320 |  |  |  |  | 0.95
Unknown | [6 empty] | Weighted average of the above shifts2 | [14 empty] | 5702 |  |  |  |  | 0.84
1 Coincidence factor for one shift is an initial estimate until Hawaii-specific operational data becomes available; it currently assumes an average of one hour of one-shift operation is coincident with Hawaii's peak demand period of 5-9 PM. Coincidence factor for two shifts, three shifts, and continual operation assumed to be 0.95 to account for shift changes or downtime.
2 Weighting of 16% one shift, 23% two shifts, 25% three shifts and 36% continual operation based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.
Table 2. Compressor Factors by System Control Type and Size
Baseline or EE Case | [8 empty] | System Control Type | [13 empty] | Compressor Factor1 ≥ 10 to ≤ 75 HP
Baseline Options | [8 empty] | Inlet Modulating with Blowdown | [13 empty] | 0.829
[9 empty] | Load/Unload with 1 gal/CFM storage | [13 empty] | 0.851
[9 empty] | Load/Unload with 2 gal/CFM storage | [13 empty] | 0.809
[9 empty] | Load/Unload with 3 gal/CFM storage | [13 empty] | 0.78
[9 empty] | Load/Unload with 4 gal/CFM storage | [13 empty] | 0.762
Energy Efficient Case | [8 empty] | Load/Unload with 5 gal/CFM storage | [13 empty] | 0.757
1 Compressor factors for ≥ 10 to ≤ 75 HP were developed using DOE part load data for different compressor control types as well as load profiles from New York facilities employing air compressors ≥ 10 to ≤ 75 HP. Refer to "IL TRM VSD Air Compressor - Supporting Information v2.xlsx," sheet named "Introduction" for information on underlying data. Refer to "Mid-Year PY24 TRM - Commercial Air Receiver Tank - Analysis File" for Hawaii-specific analysis of the data.
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
Enter system nominal horse power
[5 empty] | 25 |  |  | HP
Shift Type
Unknown
[5 empty] | HRSyear = |  |  | 5702 |  |  |  | CF = |  | 0.84
Baseline System Control Type
Load/Unload with 1 gal/CFM storage
|  |  |  | CompFBase = |  |  |  | 0.851
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Upgrading to 5gal/CFM storage from Load/Unload with 1 gal/CFM storage | [7 empty] | 1.777 | [7 empty] | 12059.73 | [7 empty] | 180895.95
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | 2025 Analysis File titled "Mid-Year PY24 TRM - Commercial Air Receiver Tank - Analysis File."
• | 2025 Analysis File titled "Mid-Year PY24 TRM - Commercial VFD Compressor - Analysis File."
• | DOE evaluation of the Compressed Air Challenge, Section 2.1.5 Facility Operating Schedules. <https://www.energy.gov/sites/default/files/2014/05/f16/eval_cactp_cd.pdf>
• | Efficiency Vermont Technical Reference User Manual (TRM), Measure Savings Algorithms and Cost Assumptions, 2018. <https://puc.vermont.gov/sites/psbnew/files/doc_library/Vermont%20TRM%20Savings%20Verification%202018%20Version_FINAL.pdf>
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 13.0, Volume 2: Commercial and Industrial Measures, FINAL, 2024. <https://icc.illinois.gov/api/web-management/documents/downloads/public/IL-TRM-Version-13.0-Volumes-1-4-Compiled-Final.pdf>
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Supporting Analysis Files: "IL TRM VSD Air Compressor - Supporting Information v2.xlsx" and "compressed-air-analysis-xlsx.xlsx."
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Programs, Version 4.0, FINAL, 2023. <https://mn.gov/commerce-stat/pdfs/mn-trm-4.0.pdf>
• | “The Relationship Between Pressure and Flow”, Compressed Air System Best Practices, Industrial Utility Efficiency, 2015. <https://www.airbestpractices.com/system-assessments/pressure/relationship-between-pressure-and-flow-compressed-air-system>
• | Xcel Energy 2024-2026 Demand Side Management & Beneficial Electrification Plan <https://www.prod2.xcelenergy.com/staticfiles/xe-responsive/Company/Rates%20&%20Regulations/Regulatory%20Filings/CO-DSM/HE%20101_Attachment%20NCM-1,%202024-2026%20DSM%20BE%20Plan_without%20header.pdf>
∆𝑘𝑊ℎ=𝐻𝑃∗0.9 □(64&𝑘𝑊/𝐻𝑃)∗〖𝐻𝑅𝑆〗_𝑦𝑒𝑎𝑟∗(〖𝐶𝑜𝑚𝑝𝐹〗_𝐵𝑎𝑠𝑒−〖𝐶𝑜𝑚𝑝𝐹〗_𝐸𝑓𝑓 )
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊=∆𝑘𝑊ℎ/〖𝐻𝑅𝑆〗_𝑦𝑒𝑎𝑟 ∗𝐶𝐹

## C_CA_No-Loss Condensate Drain
COMMERCIAL: No-Loss Condensate Drain
Return to TOC
UPDATE STATUS
This new measure was added in Spring 2025 for the Mid-Year PY24 TRM V2. Its effective date is July 1, 2025.
MEASURE DETAILS
Description
When air is compressed, water in the form of condensation is squeezed out of the compressed air and collects in piping and storage tanks. The water must be drained so as not to interfere with the flow of compressed air and so it will not corrode the piping or tank. Many drains are controlled by a timer and open an orifice for a programmed amount of time, regardless of the level of the condensate. Thus compressed air is allowed to escape after the condensate has drained. Timed drains typically continue to operate even when the compressor is down, effectively bleeding off useful stored air that must be remade when the compressor is restarted. No-loss condensate drains are controlled by a sensor and only open when there is a need to drain condensate, and close before compressed air can escape.
Program Criteria
Timed drains are not eligible.
Replacement or upgrades of existing no-loss drains are not eligible.
Compressed air system must be operational and operate at least 1,500 hours annually.
Unit of Measure
One drain.
Baseline Equipment
The baseline equipment is a standard condensate drain (open valve, timer, or both).
High Efficiency Equipment
The high efficiency equipment is a no-loss condensate drain.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  |  | Sources/Notes
CFMreduced |  |  |  | Reduced air consumption per drain | [11 empty] | 3 |  |  |  | CFM |  |  | 2025 IL TRM1, Industrial System Analysis2
kWCFM |  |  |  | System power reduction per reduced air demand depending on the compressor and control type | [11 empty] | See Table 1 |  |  |  | kW/CFM |  |  | 2025 IL TRM1, Industrial System Analysis2
HRSyear |  |  |  | Compressor total annual hours of operation depending on shift | [11 empty] | 6136 |  |  |  | hr/yr |  |  | US DOE3
CF |  |  |  | Peak demand coincidence factor | [11 empty] | 0.84 |  |  |  | - |  |  | Weighted average across different numbers of shifts4
EUL |  |  |  | Effective useful life of measure | [11 empty] | 10 |  |  |  | yrs |  |  | Benchmarking of other states' & utilities' TRMs
Sources:
1 2025 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 12.0, Volume 2: Commercial and Industrial Measures, FINAL, 2024. <https://icc.illinois.gov/api/web-management/documents/downloads/public/IL-TRM-Version-13.0-Volumes-1-4-Compiled-Final.pdf>
2 Reduced CFM consumption is based on a timer drain opening for 10 seconds every 300 seconds as the baseline. Refer to spreadsheet named "Industrial System Standard Deemed Saving Analysis 20130113.xlsx," sheet named "Install NoLoss CondDrainValves." This information is also in "Mid-Year PY24 TRM - Commercial No-Loss Condensate Drain - Analysis File."
3 US DOE, Evaluation of the Compressed Air Challenge® Training Program. <https://www.energy.gov/sites/prod/files/2014/05/f16/eval_cactp_cd.pdf>
4 Weighting of 16% one shift (CF=0.25), 23% two shifts (CF=0.95), 25% three shifts (CF=0.95) and 36% continual operation (CF=0.95). Weighting is based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules. Refer to the C_CA_VFD Compressor and C_CA_Receiver Tank measure for more information.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Table 1. System Power Reduction per Reduced Air Demand1
Compressor Type | [5 empty] | Control Type | [10 empty] | kW/CFM
Reciprocating | [5 empty] | On/Off | [10 empty] | 0.184
[6 empty] | Load/Unload | [10 empty] | 0.136
Screw | [5 empty] | Load/Unload | [10 empty] | 0.152
[6 empty] | Inlet Modulating | [10 empty] | 0.055
[6 empty] | Inlet Modulating with Unloading | [10 empty] | 0.055
[6 empty] | Variable Displacement | [10 empty] | 0.153
[6 empty] | Variable Frequency Drive | [10 empty] | 0.178
Unknown2 | [5 empty] | - | [10 empty] | 0.107
1 Calculated based on the type of compressor control. This assumes the compressor will be between 40% and 100% capacity before and after the changes to the system demand. Refer to spreadsheet named "Industrial System Standard Deemed Saving Analysis 20130113.xlsx," sheet named "Install NoLoss CondDrainValves." This information is also in "Mid-Year PY24 TRM - Commercial No-Loss Condensate Drain - Analysis File."
2 Weighted average based on market share from the 2025 Illinois TRM.
SAVINGS
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Reciprocating, On/Off Control | [7 empty] | 0.464 | [7 empty] | 3387.07 | [7 empty] | 33870.7
Reciprocating, Load/Unload Control | [7 empty] | 0.343 | [7 empty] | 2503.49 | [7 empty] | 25034.9
Screw, Load/Unload Control | [7 empty] | 0.383 | [7 empty] | 2798.02 | [7 empty] | 27980.2
Screw, Inlet Modulating | [7 empty] | 0.139 | [7 empty] | 1012.44 | [7 empty] | 10124.4
Screw, Inlet Modulating with Unloading | [7 empty] | 0.139 | [7 empty] | 1012.44 | [7 empty] | 10124.4
Screw, Variable Displacement | [7 empty] | 0.386 | [7 empty] | 2816.42 | [7 empty] | 28164.2
Screw, Variable Frequency Drive | [7 empty] | 0.449 | [7 empty] | 3276.62 | [7 empty] | 32766.2
Unknown | [7 empty] | 0.27 | [7 empty] | 1969.66 | [7 empty] | 19696.6
RESOURCES
• | 2025 Analysis File titled "Mid-Year PY24 TRM - Commercial No-Loss Condensate Drain - Analysis File."
• | Efficiency Vermont Technical Reference User Manual (TRM), Measure Savings Algorithms and Cost Assumptions, 2018. <https://puc.vermont.gov/sites/psbnew/files/doc_library/Vermont%20TRM%20Savings%20Verification%202018%20Version_FINAL.pdf>
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 13.0, Volume 2: Commercial and Industrial Measures, FINAL, 2024. <https://icc.illinois.gov/api/web-management/documents/downloads/public/IL-TRM-Version-13.0-Volumes-1-4-Compiled-Final.pdf>
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Supporting Analysis File: "Industrial System Standard Deemed Saving Analysis 20130113.xlsx."
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Programs, Version 4.0, FINAL, 2023. <https://mn.gov/commerce-stat/pdfs/mn-trm-4.0.pdf>
• | US DOE, Evaluation of the Compressed Air Challenge® Training Program. <https://www.energy.gov/sites/prod/files/2014/05/f16/eval_cactp_cd.pdf>
• | Wisconsin Focus on Energy, 2025 Technical Reference Manual, January 29, 2025. <https://assets.focusonenergy.com/production/inline-files/Focus-on-Energy-2025-TRM.pdf>
• | Xcel Energy 2024-2026 Demand Side Management & Beneficial Electrification Plan <https://www.prod2.xcelenergy.com/staticfiles/xe-responsive/Company/Rates%20&%20Regulations/Regulatory%20Filings/CO-DSM/HE%20101_Attachment%20NCM-1,%202024-2026%20DSM%20BE%20Plan_without%20header.pdf>
• | Pennsylvania Pubic Utilities Commission, Technical Reference Manual, Volume 3: Commercial & Industrial Measures, Issued September 2024. <https://www.puc.pa.gov/pcdocs/1848580.pdf>
• | Technical Reference Manual. Prepared for Idaho Power Company. November 24, 2021. <https://docs.idahopower.com/pdfs/EnergyEfficiency/Reports/2020TRM.pdf>
∆𝑘𝑊ℎ=〖𝐶𝐹𝑀〗_𝑟𝑒𝑑𝑢𝑐𝑒𝑑∗〖𝑘𝑊〗_𝐶𝐹𝑀∗〖𝐻𝑅𝑆〗_𝑦𝑒𝑎𝑟
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊=∆𝑘𝑊ℎ/〖𝐻𝑅𝑆〗_𝑦𝑒𝑎𝑟 ∗𝐶𝐹

## C_CA_VFD Compressor
COMMERCIAL: VFD Compressor
Return to TOC
UPDATE STATUS
This new measure was added in Spring 2025 for the Mid-Year PY24 TRM V2. Its effective date is July 1, 2025.
MEASURE DETAILS
Description
This measure relates to the installation of an air compressor with a variable frequency drive, replacing either inlet modulating and blowdown or load/unload controls. Baseline compressors choke off the inlet air to modulate the compressor output, which is not efficient. Efficient compressors use a variable speed drive on the motor to match output to the load.
Program Criteria
Compressors between 10-75 HP are eligible. Compressors greater than 75 HP should be evaluated using a custom approach.
Only one compressor per compressed air distribution system is eligible and must operate under 90% load capacity.
Compressed air system must be operational and operate at least 1,500 hours annually.
Unit of Measure
One air compressor.
Baseline Equipment
The baseline equipment is an air compressor with either inlet modulating and blowdown or load/unload controls.
High Efficiency Equipment
The efficient equipment is an air compressor with variable speed control.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  |  | Sources/Notes
HP |  |  |  | Compressor motor nominal horse power | [11 empty] | User Input |  |  |  | HP |  |  | ≥ 10 to ≤ 75 HP
Constant |  |  |  | Compressor motor nominal horse power to full load kW conversion factor | [11 empty] | 0.9 |  |  |  | kW/HP |  |  | 2025 IL TRM1, Compressed Air Analysis2
HRSyear |  |  |  | Compressor total annual hours of operation depending on shift | [11 empty] | See Table 1 |  |  |  | hr/yr |  |  | 2018 VT TRM3, 2025 IL TRM1
CompFBase |  |  |  | Baseline compressor factor for ≥ 10 to ≤ 75 HP compressors depending on control type | [11 empty] | See Table 2 |  |  |  | - |  |  | 2025 IL TRM1, Compressed Air Analysis4
CompFEff |  |  |  | Efficient compressor factor for ≥ 10 to ≤ 75 HP compressors | [11 empty] | 0.657 | [6 empty] | 2025 IL TRM1, Compressed Air Analysis4
CF |  |  |  | Peak demand coincidence factor | [11 empty] | See Table 1 |  |  |  | -
EUL |  |  |  | Effective useful life of measure | [11 empty] | 13 |  |  |  | yrs |  |  | Benchmarking of other states' & utilities' TRMs
Sources:
1 2025 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 13.0, Volume 2: Commercial and Industrial Measures, FINAL, 2024. <https://icc.illinois.gov/api/web-management/documents/downloads/public/IL-TRM-Version-13.0-Volumes-1-4-Compiled-Final.pdf>
2 Conversion factor based on Survey of CAGI data sheets from 200 compressors. The underlying data are from a spreadsheet named "IL TRM VSD Air Compressor - Supporting Information v2.xlsx," sheet named "Conversion Factor Analysis." The 0.9 factor represents the average across 85 fixed speed compressors of ≥ 10 to ≤ 75 HP. Refer to "Mid-Year PY24 TRM - Commercial VFD Compressor - Analysis File" for Hawaii-specific analysis.
3 Efficiency Vermont Technical Reference User Manual (TRM), Measure Savings Algorithms and Cost Assumptions, 2018. <https://puc.vermont.gov/sites/psbnew/files/doc_library/Vermont%20TRM%20Savings%20Verification%202018%20Version_FINAL.pdf>
4 The underlying data are from a spreadsheet named "IL TRM VSD Air Compressor - Supporting Information v2.xlsx," sheets named "Comp. Factor (Previous, ≤40hp)" and "Compressor Factors (>40 hp)." The compressor factors represent the averages across 77 compressors of ≥ 10 to ≤ 75 HP. Refer to "Mid-Year PY24 TRM - Commercial VFD Compressor - Analysis File" for Hawaii-specific analysis. The factor for the efficient case (a VFD compressor) has been adjusted up from 0.632 presented in the analysis to 0.657 to account for the additional power draw of the VFD. (The adjustment uses a 4% adder. Typical power loss of a VFD is assumed to be 3-5%, depending on speed and application.)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
Table 1. Annual Hours of Operation and Coincidence Factors by Shift
Shift | [6 empty] | Description | [14 empty] | HRSyear |  |  |  |  | CF1
One Shift | [6 empty] | 8 hours per day on weekdays, minus holidays and scheduled down time | [14 empty] | 1976 |  |  |  |  | 0.25
Two Shifts | [6 empty] | 16 hours per day on weekdays, minus holidays and scheduled down time | [14 empty] | 3952 |  |  |  |  | 0.95
Three Shifts | [6 empty] | 24 hours per day on weekdays, minus holidays and scheduled down time | [14 empty] | 5928 |  |  |  |  | 0.95
Continual Operation | [6 empty] | 24 hours per day, 7 days per week, minus holidays and scheduled down time | [14 empty] | 8320 |  |  |  |  | 0.95
Unknown | [6 empty] | Weighted average of the above shifts2 | [14 empty] | 5702 |  |  |  |  | 0.84
1 Coincidence factor for one shift is an initial estimate until Hawaii-specific operational data becomes available; it currently assumes an average of one hour of one-shift operation is coincident with Hawaii's peak demand period of 5-9 PM. Coincidence factor for two shifts, three shifts, and continual operation assumed to be 0.95 to account for shift changes or downtime.
2 Weighting of 16% one shift, 23% two shifts, 25% three shifts and 36% continual operation based on DOE evaluation of the Compressed Air Challenge, section 2.1.5 Facility Operating Schedules.
Table 2. Baseline Compressor Factors by Control Type and Size
Baseline Control Type | [13 empty] | Baseline Compressor Factor1 ≥ 10 to ≤ 75 HP
Inlet Modulating with Blowdown | [13 empty] | 0.829
Load/Unload with 1 gal/CFM storage | [13 empty] | 0.851
Load/Unload with 2 gal/CFM storage | [13 empty] | 0.809
Load/Unload with 3 gal/CFM storage | [13 empty] | 0.78
Load/Unload with 4 gal/CFM storage | [13 empty] | 0.762
Load/Unload with 5 gal/CFM storage | [13 empty] | 0.757
1 Compressor factors for ≥ 10 to ≤ 75 HP were developed using DOE part load data for different compressor control types as well as load profiles from New York facilities employing air compressors ≥ 10 to ≤ 75 HP. Refer to "IL TRM VSD Air Compressor - Supporting Information v2.xlsx," sheet named "Introduction" for information on underlying data. Refer to "Mid-Year PY24 TRM - Commercial VFD Compressor - Analysis File" for Hawaii-specific analysis of the data.
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
Enter compressor motor nominal horse power
[5 empty] | 25 |  |  | HP
Shift Type
Three Shifts
[5 empty] | HRSyear = |  |  | 5928 |  |  |  | CF = |  | 0.95
Baseline Control Type
Load/Unload with 5 gal/CFM storage
|  |  |  | CompFBase = |  |  |  | 0.757
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Replacing Load/Unload with 5 gal/CFM storage | [7 empty] | 2.138 | [7 empty] | 13338 | [7 empty] | 173394
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | 2025 Analysis File titled "Mid-Year PY24 TRM - Commercial VFD Compressor - Analysis File."
• | California eTRM, Effective January 1, 2025. <https://www.caetrm.com>
• | DOE evaluation of the Compressed Air Challenge, Section 2.1.5 Facility Operating Schedules. <https://www.energy.gov/sites/default/files/2014/05/f16/eval_cactp_cd.pdf>
• | Efficiency Maine, Commercial/Industrial and Multifamily Technical Reference Manual, Version 2024.3, Effective March 1, 2024. <https://www.efficiencymaine.com/docs/EMT-TRM_Commercial_Industrial_Multifamily_v2024_3.pdf>
• | Efficiency Vermont Technical Reference User Manual (TRM), Measure Savings Algorithms and Cost Assumptions, 2018. <https://puc.vermont.gov/sites/psbnew/files/doc_library/Vermont%20TRM%20Savings%20Verification%202018%20Version_FINAL.pdf>
• | Energy & Resource Solutions, Measure Life Study, Prepared for the Massachusetts Joint Utilities, 2005. Table 1-1.
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 13.0, Volume 2: Commercial and Industrial Measures, FINAL, 2024. <https://icc.illinois.gov/api/web-management/documents/downloads/public/IL-TRM-Version-13.0-Volumes-1-4-Compiled-Final.pdf>
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Supporting Analysis Files: "IL TRM VSD Air Compressor - Supporting Information v2.xlsx" and "compressed-air-analysis-xlsx.xlsx."
• | State of Minnesota Technical Reference Manual for Energy Conservation Improvement Programs, Version 4.0, FINAL, 2023. <https://mn.gov/commerce-stat/pdfs/mn-trm-4.0.pdf>
• | Technical Reference Manual. Prepared for Idaho Power Company. November 24, 2021. <https://docs.idahopower.com/pdfs/EnergyEfficiency/Reports/2020TRM.pdf>
• | Wisconsin Focus on Energy, 2025 Technical Reference Manual, January 29, 2025. <https://assets.focusonenergy.com/production/inline-files/Focus-on-Energy-2025-TRM.pdf>
• | Xcel Energy 2024-2026 Demand Side Management & Beneficial Electrification Plan <https://www.prod2.xcelenergy.com/staticfiles/xe-responsive/Company/Rates%20&%20Regulations/Regulatory%20Filings/CO-DSM/HE%20101_Attachment%20NCM-1,%202024-2026%20DSM%20BE%20Plan_without%20header.pdf>
∆𝑘𝑊ℎ=𝐻𝑃∗0.9 □(64&𝑘𝑊/𝐻𝑃)∗〖𝐻𝑅𝑆〗_𝑦𝑒𝑎𝑟∗(〖𝐶𝑜𝑚𝑝𝐹〗_𝐵𝑎𝑠𝑒−〖𝐶𝑜𝑚𝑝𝐹〗_𝐸𝑓𝑓 )
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊=∆𝑘𝑊ℎ/〖𝐻𝑅𝑆〗_𝑦𝑒𝑎𝑟 ∗𝐶𝐹

## C_Other_Re¦Retro-Commissioning
COMMERCIAL: Re/Retro-commissioning
Return to TOC
MEASURE DETAILS
Description
Hawai‘i Energy incentivizes the actions of building owners to evaluate the effectiveness and efficiency of current building systems to optimize performance. These actions will be documented in a Commissioning Report that shall include:
| - | Executive summary of all activities included in the commissioning process.
| - | Introduction section, including names and contact information for the Building Owner, Building Manager, RCx Trade Ally.
| - | Detailed building and energy systems description, including estimates of the equipment usage profiles.
| - | Detailed operational scheduling of the major systems.
| - | Detailed report of all optimization measures identified.
| - | Cost estimate, energy savings estimate and simple payback for all recommended operational actions, sequencing, and equipment enhancements.
| - | Pre- and post-data logging.
| - | Testing and Balancing (TAB) of HVAC system.
| - | Functional testing of the EMS, if equipped.
| - | Detailed operations and maintenance review.
| - | Documentation of O&M refresher training for facility staff.
| - | Assessment of existing equipment over-sizing and recommendations for right-sizing when HVAC equipment needs replacement, including, but not limited to recommended capital items.
Program Criteria
Program pre-approval is required prior to the start of any energy consumption analysis. Projects can be whole building or by system if determined cost-effective by Hawai‘i Energy. Eligible program participants must:
| - | Own or operate a high energy usage facility that has at least 50,000 square feet of conditioned space or that consumes at least 1,000,000 kWh/year.
| - | Receive electric service from Hawaiian Electric Companies (e.g., HECO, MECO or HELCO) and pay a Hawai‘i public benefits fund surcharge on their electric bill.
| - | For retro-commissioning, building has been in service for at least 2 years and has never been commissioned before. For recommissioning, it has been at least 5 years since the last commissioning activity.
| - | Be willing to commit up to 100% of the incentive value to implement energy conservation measures (ECMs) found to have a 2- year or less payback. Any implemented ECMs are eligible for Hawai‘i Energy’s prescriptive and custom incentives.
| - | Grant Hawai‘i Energy access to their facility’s billing data and other required data to establish an initial benchmark rating via ENERGY STAR Portfolio Manager®.
| - | Grant Hawai‘i Energy access to the facility itself for on-going program assessment, monitoring and measurement purposes.
| - | Be willing to invest facility management time, typically between 8-16 hours, to support multiple site visits and data requests from the RCx consultant.
| - | Perform at least two weeks of metering of all major building systems prior to the implementation of any ECMs and at least two weeks of post metering. The cost of “pre” and “post” metering may be included in the total project cost by the commissioning agent. The metering plan shall be included in the proposal.
| - | The participant’s commissioning specialist shall be certified by a nationally recognized building commissioning organization such as the American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE), AABC Commissioning Group (ACG), Building Commissioning Association (BCA), National Environmental Balancing Bureau (NEBB) or similar organization acceptable to Hawai‘i Energy.
| - | If participant wishes to use a non-certified contractor to perform the Retro-Commissioning or Enhanced Commissioning project, an exception may be granted at Hawai‘i Energy’s sole discretion if:
|  | 1. | The proposed contractor provides evidence of having completed similar commissioning projects for two or more buildings of at least 50,000 square feet (conditioned space) each, and
|  | 2. | The proposed contractor submits at least two verifiable and satisfactory references from customers or clients who used the contractor to complete the similar projects.
| - | All retro-commissioning work performed (to include, but not limited to, documentation and reporting) must follow guidelines recommended by an approved commissioning organization. The commissioning specialist must indicate in their report the organization’s guidelines which were followed for the retro-commissioning process.
| - | The cost of replacement of major end use items may be included in the total project cost from the commissioning agent. Cost of routine maintenance activities identified by the commissioning agent shall not be included in the total project.
Unit of Measure
Any kWh and kW savings brought about by and verified by the retro-commissioning study, such as process optimization, schedule or set-point changes, and routine maintenance.
Baseline Equipment
Pre-commissioning operating procedures.
High Efficiency Equipment
Post-commissioning operating procedures.
ALGORITHMS
(Custom)
SAVINGS
Measure Name |  |  |  | Peak Demand Savings | Annual Energy Savings
Re¦Retro-Commissioning |  |  |  | Custom | Custom

## C_Other_Transformer
COMMERCIAL: Distribution Transformer
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM to clarify the program criteria.
MEASURE DETAILS
Description
The replacement of a distribution transformer manufactured and installed prior to 2007 with a higher efficiency unit that meets or exceeds DOE 2016 efficiency standards. The savings presented here are for no-load conditions.
Program Criteria
• This measure applies to single-phase and three-phase low-voltage distribution transformers in commercial building applications.
• The new transformer must meet or exceed DOE 2016 efficiency standards per 10 CFR 431.196 if the transformer's average loading is ≤35%.
• The new transformer must exceed DOE 2016 efficiency standards per 10 CFR 431.196 if the transformer's average loading is >35%.
• The pre-existing transformer must be manufactured/installed prior to 2007. If age of transformer is not available nor attainable, another proxy may be acceptable; for example, the age of the building which it services, if reasonable.
• Except for the case of new construction, the new transformer must serve the same load as the pre-existing transformer.
• The semi-prescriptive approach presented here does not apply for the following transformer projects. However, these types of projects may qualify under the Custom Incentive Program.
• Replacement of transformers that are > 1000 kVA.
• Replacement of transformers installed after 2007 (on a case-by-case basis).
• Analysis of savings under loaded conditions.
• Projects where the new transformer will serve a load that is >10% higher than the load served by the pre-existing transformer.
Unit of Measure
One transformer
Baseline Equipment
A dual baseline approach is used for transformer projects that qualify for early retirement. The first baseline is the pre-existing transformer. The second baseline is a transformer that meets current minimum federal standards (DOE2016, 10 CFR 431.196). Early retirement eligibility is defined as follows:
| 1) | The pre-existing transformer is functioning with remaining useful life of > 0 years (based on the EUL), and
| 2) | The vintage (and therefore RUL) of the pre-existing transformer can be ascertained and is well-documented.
In cases where the loading on the pre-existing transformer is unknown for a given project, an EUL of 30 years is used when determining eligibility for early retirement. The EUL of 30 years is consistent with the average EUL found in a literature review of other TRMs and distribution transformer guidance documents.
In cases where the average and peak loading conditions are known and well documented for a given project, the EUL will be dependent on the loading characteristics and condition of the pre-existing transformer. For this semi-prescriptive measure, an EUL of 50 years is used for transformers with an average loading of >0% and ≤35% and an EUL of 30 years is used for transformers with an average loading of >35%.
A single baseline approach is used for projects designated as end-of-life or for projects where the RUL is greater than 25 years. For end-of-life projects, the single baseline is a transformer that meets current minimum federal standards (DOE2016, 10 CFR 431.196). An end-of-life single baseline approach should be applied in the following cases:
| 1) | The age of the transformer exceeds the EUL,
| 2) | The transformer is no longer functioning, or
| 3) | It is a new construction project.
For projects where the RUL is greater than 25 years, a single baseline also applies for lifetime savings calculations since Hawai'i Energy's maximum measure life is 25 years. For these projects, the baseline is the pre-existing transformer for the full measure life of 25 years, and the second baseline does not enter into the lifetime savings calculation.
High Efficiency Equipment
Transformer that meets or exceeds current minimum federal standards (DOE2016, 10 CFR 431.196):
• The new transformer must meet or exceed DOE 2016 efficiency standards if its average loading is ≤35%.
• The new transformer must exceed DOE 2016 efficiency standards if its average loading is >35%.
ALGORITHMS
Transformer Losses, kW (No-load Conditions)
[5 empty] | and |  |  |  | (1)
Transformer Losses, kWh (No-load Conditions)
[5 empty] | and |  |  |  | (2)
Cooling System Demand Savings, kW
(3)
Cooling System Energy Savings, kWh
(4)
First Baseline Peak Demand Reduction, kW
(5)
Second Baseline Peak Demand Reduction, kW
(6)
First Baseline Annual Energy Savings, kWh/yr
(7)
Second Baseline Annual Energy Savings, kWh/yr
(8)
Dual Baseline Lifetime Energy Savings, kWh
(9)
Single Baseline Lifetime Energy Savings, kWh
(10)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  | Value | Unit | Sources/Notes
WBL |  |  | Baseline transformer's losses under no-load losses conditions |  |  | See Tables 1 and 2 in the C_Other_Transformer_WKST | W | Varies with applicable baseline approach (refer to Baseline Equipment section above). For dual baseline analysis: a) the first baseline must meet or exceed minimum Pre-TP1 standards (Table 1 in worksheet), and b) the second baseline is defined as meeting current minimum federal standards (Table 2 in worksheet). For single baseline analysis, the baseline is defined as meeting current minimum federal standards (Table 2 in worksheet).
WEE |  |  | Energy efficient transformer's losses under no-load losses conditions |  |  | User Input | W | Varies with transformer product and size. Must meet or exceed current minimum federal standards (10 CFR 431.196), depending on the transformer's average loading. (Refer to the High Efficiency Equipment description above.)
HRSDT |  |  | Transformer hours of operation |  |  | 8760 | hrs/yr | Transformer operates all the time, whether loaded or unloaded.
CSP |  |  | Space cooling system performance |  |  | 0.75 | kW/ton | Only applies to actively cooled transformer rooms. It is used to calculate the cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 0.5 kW per ton. Typical value is 0.75 kW/ton.
3.52 |  |  | Constant |  |  | 3.52 | kW/ton | 1 ton of cooling = 12,000 Btu/hr = 3.52 kW.
EFLHAC |  |  | Equivalent full load hours of the space cooling system |  |  | See Table 3 in the C_Other_Transformer_WKST | hrs/yr | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes and weather data.
CFDT |  |  | Coincidence factor of the distribution transformer |  |  | 1 | - | Transformer operates all the time, whether loaded or unloaded.
CFAC |  |  | Coincidence factor of the space cooling system |  |  | See Table 3 in the C_Other_Transformer_WKST | - | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period.
RUL |  |  | Remaining useful life of the pre-existing transformer |  |  | Variable (Maximum of 25) | yrs | Calculated based on transformer's age and average loading conditions.
EUL |  |  | Effective useful life |  |  | 30 or 50 | yrs | Depends on transformer's average loading conditions. EUL = 50 for >0% and ≤35% loading and EUL = 30 for >35% loading (or if loading is unknown).
MLmax |  |  | Maximum measure life |  |  | 25 | yrs | Hawai'i Energy limits the measure life of any measure to 25 years to match the period of the TRB calculation.
SAVINGS
See the accompanying Transformer worksheet:
C_Other_Transformer_WKST
RESOURCES
• | ICF's analysis file named "PY26 TRM - Commercial Transformer - Analysis File."
• | AEG's analysis file named "PY24 TRM - Commercial Transformer - Analysis File."
• | Energy Efficiency & Renewable Energy Office (EERE): Technical Support Document: Energy Efficiency Program for Consumer Products & Commercial & Industrial Equipment, Distribution Transformers, 2013.
• | Michigan Energy Measure Database, 2018 MEMD Master Database, https://www.michigan.gov/mpsc/0,4639,7-159-52495_55129---,00.html. Spreadsheet.
• | Northwest Power Conservation Council (NWPCC), Commercial Data Centers, Version 6 - Seventh Power Plan Conservation Supply Workbooks, February 25, 2016. Spreadsheet. Northwest Power Conservation Council (NWPCC), Industrial Tool, Version 9 - Seventh Power Plan Conservation Supply Workbooks, February 25, 2016. Spreadsheet.
• | Oak Ridge National Laboratory, Determination Analysis of Energy Conservation Standards for Distribution Transformers, ORNL-6847, Oak Ridge, TN, 1996, https://www.osti.gov/servlets/purl/405744.
• | State of Hawaii EM&V: Early Guidance on Transformer Measure Baseline Determination, Memorandum, Prepared by Michael Daukoru and Kelly Parmenter, AEG, Prepared for Ramsey Brown and Keith Block, Hawai'i Energy, Sep. 24, 2018. See also related spreadsheet named "Literature Review of Transformers in TRMs (for Memo)."
• | State of Minnesota, Technical Reference Manual for Energy Conservation Improvement Programs, Version 2.2, May 2, 2018.
• | Title 10: Energy, PART 431—ENERGY EFFICIENCY PROGRAM FOR CERTAIN COMMERCIAL AND INDUSTRIAL EQUIPMENT, Subpart K—Distribution Transformers, §431.196 Energy conservation standards and their effective dates, Electronic Code of Federal Regulations, U.S. Government Publishing Office.
• | Transformer Replacement Program, Low-Voltage Dry-Type 25-300 KVA Transformers, Implementation Manual, Version 2, National Grid, January 24, 2018.
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒, 𝑑𝑢𝑎𝑙)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(𝐸𝑈𝐿−𝑅𝑈𝐿)
〖∆𝑘𝑊〗_1𝑠𝑡=(〖𝑘𝑊〗_(𝐵𝐿,1)−〖𝑘𝑊〗_𝐸𝐸 )∗〖𝐶𝐹〗_𝐷𝑇+〖∆𝑘𝑊〗_(𝐶𝐿,1)∗〖𝐶𝐹〗_𝐴𝐶
〖∆𝑘𝑊〗_2𝑛𝑑=(〖𝑘𝑊〗_(𝐵𝐿,2)−〖𝑘𝑊〗_𝐸𝐸 )∗〖𝐶𝐹〗_𝐷𝑇+〖∆𝑘𝑊〗_(𝐶𝐿,2)∗〖𝐶𝐹〗_𝐴𝐶
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=(〖𝑘𝑊ℎ〗_(𝐵𝐿,1)−〖𝑘𝑊ℎ〗_𝐸𝐸 )+〖∆𝑘𝑊ℎ〗_(𝐶𝐿,1)
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=(〖𝑘𝑊ℎ〗_(𝐵𝐿,2)−〖𝑘𝑊ℎ〗_𝐸𝐸 )+〖∆𝑘𝑊ℎ〗_(𝐶𝐿,2)
/1000
〖𝑘𝑊〗_𝐵𝐿=𝑊_𝐵𝐿/1000
〖𝑘𝑊ℎ〗_𝐵𝐿=〖𝑘𝑊〗_𝐵𝐿∗〖𝐻𝑅𝑆〗_𝐷𝑇
〖∆𝑘𝑊〗_𝐶𝐿=((〖𝑘𝑊〗_𝐵𝐿−〖𝑘𝑊〗_𝐸𝐸 ))/3.52∗𝐶𝑆𝑃
〖∆𝑘𝑊ℎ〗_𝐶𝐿=〖∆𝑘𝑊〗_𝐶𝐿∗〖𝐸𝐹𝐿𝐻〗_𝐴𝐶
/1000
〖𝑘𝑊〗_𝐸𝐸=𝑊_𝐸𝐸/1000
〖𝑘𝑊ℎ〗_𝐸𝐸=〖𝑘𝑊〗_𝐸𝐸∗〖𝐻𝑅𝑆〗_𝐷𝑇
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒, 𝑠𝑖𝑛𝑔𝑙𝑒)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗〖𝑀𝐿〗_𝑚𝑎𝑥

## C_Other_Transformer_WKST
COMMERCIAL: Transformer Savings Calculator
Return to TOC
Step 1: Select the Facility Type:
|  | Facility Type: | Restaurant | [5 empty] | Transformer Hours of Operation: | 8760 |  | Transformer CF: | 1 |  | Measure Life: | 25
[9 empty] | EFLHs of Cooling: | 2451 |  | Cooling CF: | 0.4
Notes:
· If age of transformer is unavailable or unattainable, another proxy may be acceptable; for example, use the age of the building which it services, if reasonable.
· The "Average Loading Percentage" column should only be used when the loading conditions are known and well documented for a given project.
· The semi-prescriptive approach is limited to 1000 kVA transformers. Transformers > 1000 kVA (3-Phase) will use a custom approach.
· For the semi-prescriptive approach, the pre-existing transformer must be manufactured/installed prior to 2007.
Step 2: Fill in the green cells in the table below with information for one or more transformers. | [7 empty] | Step 3: Select whether to use user input baseline values or reference values (reference by default)
The blue entries are examples only. | [7 empty] | Reference
Size (kVA) | Qty | Location | Baseline Equipment Manufacture Year | Average Loading Percentage | Age (Years) | RUL (Years) | Replacement Event | 1st Baseline Transformer |  |  | 2nd Baseline Transformer |  | Replacement Transformer |  | Cooling Load Impact | [5 empty] | Peak Demand Savings (kW) |  | Annual Energy Savings (kWh/yr) |  | Lifetime Energy Savings (kWh) | TRB Calculation
[8 empty] | No Load Losses (Watts) User Input* | No Load Losses (Watts) Reference | Annual Losses (kWh) | No Load Losses (Watts) Reference | Annual Losses (kWh) | No Load Losses (Watts) | Annual Losses (kWh) | Actively-cooled Transformer Room | Cooling System Performance (kW/ton) | 1st BL Cooling Load Reduction (kW) | 1st BL Cooling kWh Reduction (kWh) | 2nd BL Cooling Load Reduction (kW) | 2nd BL Cooling kWh Reduction (kWh) | 1st Baseline | 2nd Baseline | 1st Baseline | 2nd Baseline |  |  | (Hidden dropdowns)
37.5 | 1 |  | 1980 | 10% | 46 | 4 | Retrofit |  | 533 | 4669.08 | 151.7804 | 1329.5965 | 100 | 876 | Yes | 0.75 | 0.092259 | 226.1256 | 0.011033 | 27.0413 | 0.4699 | 0.056194 | 4019.2056 | 480.6378 | 26170.2169 | Dual Baseline | Yes
30 | 1 |  | 1980 | 60% | 46 | 0 | End of Life |  | 128.6774 | 1127.2142 |  |  | 100 | 876 | Yes | 0.75 | 0.0061102 | 14.9762 |  |  | 0.031122 |  | 266.1904 |  | 6654.7612 | Single Baseline | No
30 | 1 |  | 2007 | 36% |  |  | NA |  | NA |  |  |  | 100 |  | Yes | [11 empty] | User Input
37.5 | 1 |  | 2005 | 10% | 21 | 29 | Retrofit |  | 533 | 4669.08 | 151.7804 | 1329.5965 | 100 | 876 | Yes | 0.75 | 0.092259 | 226.1256 | 0.011033 | 27.0413 | 0.4699 | 0.056194 | 4019.2056 | 480.6378 | 100480.141 | Single Baseline | Reference
37.5 | 1 |  | 1980 |  | 46 | 0 | End of Life |  | 151.7804 | 1329.5965 |  |  | 100 | 876 | No | 0 | 0 | 0 |  |  | 0.05178 |  | 453.5965 |  | 11339.9133 | Single Baseline
30 | 1 |  | 1970 |  | 56 | 0 | End of Life |  | 128.6774 | 1127.2142 |  |  | 100 | 876 | No | 0 | 0 | 0 |  |  | 0.028677 |  | 251.2142 |  | 6280.3558 | Single Baseline
30 | 1 |  | 2020 | 15% |  |  | NA |  | NA |  |  |  | 100 |  | No
Total: | [20 empty] | 1.051 | 0.112 | 9009.41 | 961.28 | 150925.39
*This is optional in the case more accurate baseline values are known
|  |  | Table 1. Pre-TP1 No-Load Losses |  |  | Table 2. DOE2016 No-Load Losses |  |  | Table 3. HVAC EFLH and CF Values |  |  |  | Table 4. Event Type |  | Table 5. EUL
|  |  | Pre-TP1 |  |  | DOE2016 |  |  | HVAC EFLH and CF |  |  |  | Event Type |  | EUL | [11 empty] | Reminder to link EFLHs and CFs to TRM's EFLH & CF Sheet
|  |  | kVA | No-Load Losses (W) |  | kVA | No-Load Losses (W) |  | Building Type | EFLH | CF |  | Retrofit |  | 30
|  |  | 10 | 233.6667 |  | 10 | 57.0733 |  | Misc. Commercial | 2594 | 0.38 |  | End of Life |  | 50
|  |  | 15 | 286 |  | 15 | 77.0442 |  | Cold Storage | Varies | Varies
|  |  | 20 | 461 |  | 20 | 95.3224 |  | Education | 2549 | 0.43 | [15 empty] | Removed the tables related to incentives and special offerings
|  |  | 25 | 282 |  | 25 | 112.4367 |  | Grocery | 1531 | 0.27 | [15 empty] | Removed the efficiency tables (not used)
|  |  | 30 | 443 |  | 30 | 128.6774 |  | Health | 4891 | 0.55 | [15 empty] | Removed the TP-1 No-Load Losses table (not used)
|  |  | 37.5 | 533 |  | 37.5 | 151.7804 |  | Hotel/Motel | 4910 | 0.6
|  |  | 45 | 623 |  | 45 | 173.704 |  | Industrial | Varies | Varies
|  |  | 50 | 585 |  | 50 | 187.7891 |  | Office | 2754 | 0.48
|  |  | 63 | 765.8 |  | 63 | 222.8151 |  | Restaurant | 2451 | 0.4
|  |  | 75 | 861 |  | 75 | 253.5 |  | Retail | 1913 | 0.29
|  |  | 100 | 1089.6667 |  | 100 | 313.6409 |  | Warehouse | 1033 | 0.01
|  |  | 112.5 | 1204 |  | 112.5 | 342.2043 |  | Use custom approach for entries noted as "Varies."
|  |  | 125 | 1300.6667 |  | 125 | 369.9526
|  |  | 150 | 1494 |  | 150 | 423.3896
|  |  | 167 | 1570.3867 |  | 167 | 458.3981
|  |  | 200 | 1718.6667 |  | 200 | 523.8354
|  |  | 225 | 1831 |  | 225 | 571.5414
|  |  | 250 | 2030.3333 |  | 250 | 617.8858
|  |  | 300 | 2429 |  | 300 | 707.135
|  |  | 400 | 2740.3333 |  | 400 | 874.8972
|  |  | 500 | 3269 |  | 500 | 1031.978
|  |  | 750 | 3830 |  | 750 | 1393.0861
|  |  | 1000 |  |  | 1000 | 1723.5847
Formulas:
Age (Years) = IF(OR([Baseline Equipment Manufacture Year]="",[Baseline Equipment Manufacture Year]>2006),"",YEAR(TODAY())-[Baseline Equipment Manufacture Year])
Replacement Event = IF([Baseline Equipment Manufacture Year]="","",IF([Baseline Equipment Manufacture Year]>2006,"NA",IF(OR([Average Loading Percentage]>0.35, [Average Loading Percentage]=0), IF(YEAR(TODAY())-[Baseline Equipment Manufacture Year]<INDEX(EUL,1), INDEX(EventType,1), INDEX(EventType,2)), IF(YEAR(TODAY())-[Baseline Equipment Manufacture Year]<INDEX(EUL,2), INDEX(EventType,1), INDEX(EventType,2)))))
Note on D45: Source: Validated data from Powersmiths International Corp. database of field measurements as of May 18, 2017. Non-bold capacities are interpolated.
Note on G45: Source: Energy Efficiency & Renewable Energy Office (EERE): Technical Support Document: Energy Efficiency Program for Consumer Products & Commercial & Industrial Equipment, Distribution Transformers, 2013. No-load losses calculated using formula presented in Chapter 5.2.2: Scaling Relationships in Transformer Manufacturing.
Note on J45: Source: Hawai`i Energy Technical Reference Manual (TRM).
Note on H56: Source: Energy Efficiency & Renewable Energy Office (EERE): Final Rule LCC Spreadsheet: Design Line #7: 75kVA, Dry Type, 3-Phase, 10kV BIL. Average of transformers filtered for 98.60% (DOE2016) efficiency.

## R_Appliance_Clothes Washer
RESIDENTIAL: Clothes Washer
Return to TOC
UPDATE STATUS
Updated in Winter 2022-2023 for the PY23 TRM.
MEASURE DETAILS
Description
Residential standard-sized front- or top-loading energy efficient clothes washer for use in a single family home or in-unit installation in a multifamily home.
Program Criteria
Must be ENERGY STAR v8.1-certified and/or have a Consortium for Energy Efficiency (CEE) rating of Tier 1 or higher.
Unit of Measure
One clothes washer.
Baseline Equipment
Clothes washer meeting the federal requirements in effect for the given program year. Table 1 shows the current requirements, which have been in effect since Jan. 1, 2018. The Integrated Modified Energy Factor (IMEF) is used in the savings calculations. IMEF is a measure of energy efficiency that considers the energy used by the washer during the cycle and while on standby, the energy used to heat the water, and the energy used to run the dryer.
Table 1. Federal Standards for Standard-Sized Clothes Washers. Effective as of Jan. 1, 2018.1 Weighted by Shares of Top- and Front-Loading Clothes Washers per RECS 2020.2
| Product Class |  |  | Minimum Integrated Modified Energy Factor (IMEF), cu.ft./kWh/cycle |  |  |  | Maximum Integrated Water Factor (IWF), gal/cycle/cu.ft. |  |  |  | Share by Type (Hot-Humid Climate Region)
| Top-loading, Standard, ≥ 1.6 cu.ft. capacity |  |  | 1.57 |  |  |  | 6.5 |  |  |  | 75.32%
| Front-loading, Standard, ≥ 1.6 cu.ft. capacity |  |  | 1.84 |  |  |  | 4.7 |  |  |  | 24.68%
| Weighted Average Across Top- and Front-loading Washers, Hot-Humid Climate |  |  | 1.64 |  |  |  | 6.06 |  |  |  | 100%
Notes:
1. Code of Federal Regulations, 10 CFR 430.32, Subpart C, Energy and Water Conservation Standards and their Effective Dates, Paragraph (g): Clothes Washers, available here: <https://www.govinfo.gov/content/pkg/CFR-2022-title10-vol3/pdf/CFR-2022-title10-vol3-sec430-32.pdf>, accessed 1/23/2023.
2. 2020 Residential Energy Consumption Survey (RECS), Table HC3.6 Appliances in U.S. Homes, by Climate Region, Hot-Humid Climate, available here: <https://www.eia.gov/consumption/residential/data/2020/#appliances>, accessed 1/23/2023.
High Efficiency Equipment
Three tiers of efficient equipment:
1) ENERGY STAR or CEE Tier 1 certified
2) ENERGY STAR Most Efficient, or CEE Tier 2 certified
3) CEE Tier 3 certified
See Table 2 for criteria.
Table 2. ENERGY STAR v8.1 and CEE Criteria for Residential Clothes Washers.1,2
| Product Type |  |  | Minimum IMEF, cu.ft./kWh/cycle | [7 empty] | Maximum IWF, gal/cycle/cu.ft.
|  |  |  | Not Connected |  |  |  | Connected3
| ENERGY STAR or CEE Tier 1: Top- or Front-loading, ≤ 2.5 cu.ft. |  |  | 2.07 |  |  |  | 1.9665 |  |  |  | 4.2
| ENERGY STAR: Top-loading, > 2.5 cu.ft. |  |  | 2.06 |  |  |  | 1.957 |  |  |  | 4.3
| ENERGY STAR: Front-loading, > 2.5 cu.ft. |  |  | 2.76 |  |  |  | 2.622 |  |  |  | 3.2
| CEE Tier 1: Top- or Front-loading, > 2.5 cu.ft. |  |  | 2.76 |  |  |  | - |  |  |  | 3.2
| ENERGY STAR Most Efficient or CEE Tier 2: Top- or Front-loading, ≤ 2.5 cu.ft. |  |  | 2.2 | [7 empty] | 3.7
| ENERGY STAR Most Efficient or CEE Tier 2: Top- or Front-loading, > 2.5 cu.ft. |  |  | 2.92 | [7 empty] | 3.2
| CEE Tier 3: Top- or Front-loading, > 2.5 cu.ft. |  |  | 3.1 | [7 empty] | 3
Notes:
1. ENERGY STAR Version 8.1 Clothes Washer Specification, available here: <https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Version%208.1%20Clothes%20Washer%20Final%20Specificaiton%20-%20Partner%20Commitments%20and%20Eligibility%20Criteria.pdf>.
2. CEE Super Efficient Home Appliances Initiative, High Efficiency Specifications for Residential Clothes Washers, Effective Feb. 5, 2018, available here: <https://library.cee1.org/system/files/library/13445/CEE_ResidentialClothesWasherSpecification_05Feb2018.pdf>, accessed Jan. 26, 2023.
3. Connected systems include hardware and software required to enable communication in response to consumer-authorized energy related commands.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Tier 1 |  | Tier 2 |  | Tier 3 | Unit | Source/Notes
CAP |  | Average clothes washer capacity in cubic feet (cu.ft.) |  |  | 4.22 |  |  |  |  | cu.ft. | Based on AEG's analysis of CEE and ENERGY STAR qualifying clothes washer data, accessed Jan. 23, 2023.1,2,3 This value represents the weighted average across the three tiers and across all front- and top-loading models in the datasets.
IMEF_base |  | Integrated Modified Energy Factor of baseline unit |  |  | 1.64 |  |  |  |  | cu.ft./ kWh/ cycle | Based on Federal Standards as of Jan. 1, 2018. This value represents the weighted average across front- and top-loading units using 2020 RECS data for the hot-humid climate region. See Table 1 above for derivation.
IMEF_he |  | Integrated Modified Energy Factor of efficient unit |  |  | 2.42 |  | 2.86 |  | 3.1 | cu.ft./ kWh/ cycle | Based on AEG's analysis of CEE and ENERGY STAR qualifying clothes washer data, accessed Jan. 23, 2023.1,2,3 These values represent the weighted averages across all front- and top-loading models in the datasets, for each tier.
CYCLES |  | Average number of washer cycles per washer per year |  |  | 219 |  |  |  |  | - | Based on AEG's analysis of 2020 RECS data, Table HC3.6, Clothes washer usage, hot-humid climate zone. This value represents the weighted average of usage per week across usage bins, multiplied by 52 weeks per year.3
%E_wash,base |  | Percentage of total energy consumption for clothes washer operation for a baseline model |  |  | 7% |  |  |  |  | % | Values are derived from the Maryland/Mid-Atlantic TRM v10.4 The percentages were initially based on a weighted average of top-loading and front-loading units for each tier and each capacity bin (> 2.5 cu.ft. and ≤ 2.5 cu.ft.) using data from the ENERGY STAR qualified product list (accessed on Mar. 17, 2020) and consumption data from the U.S. DOE's Life-Cycle Cost and Payback Period Excel-based analytical tool.5 AEG then developed weighted averages of the percentages for the two capacity bins using CEE and ENERGY STAR qualifying clothes washer data, accessed Jan. 23, 2023.1,2,3
%E_heat,base |  | Percentage of total energy consumption for water heating for a baseline model |  |  | 28% |  |  |  |  | %
%E_dry,base |  | Percentage of total energy consumption for clothes drying for a baseline model |  |  | 65% |  |  |  |  | %
%E_wash,he |  | Percentage of total energy consumption for clothes washer operation for efficient unit |  |  | 5.75% |  | 9.767% |  | 10% | %
%E_heat,he |  | Percentage of total energy consumption for water heating for efficient unit |  |  | 29% |  | 4.977% |  | 3% | %
%E_dry,he |  | Percentage of total energy consumption for clothes drying for efficient unit |  |  | 65.25% |  | 85.26% |  | 87% | %
%DRYER_electric |  | Percentage of dryers assumed to be electric |  |  | 69% |  |  |  |  | % | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Derived from responses to Q20, Q27, Q35, and Q40L of the residential phone / audit survey.
%HEATER_electric |  | Percentage of water heating assumed to be electric |  |  | 59% |  |  |  |  | % | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Derived from responses to Q47 of the residential phone / audit survey.
EFLH |  | Equivalent full load hours from load shape analysis |  |  | 2448 |  |  |  |  | hrs/yr | AEG 2023 load shape analysis for Hawaii peak period of 5-9 pm weekdays.3,6
CF |  | Coincidence Factor |  |  | 0.31 |  |  |  |  | % | AEG 2023 load shape analysis for Hawaii peak period of 5-9 pm weekdays.3,7
EULEE |  | Effective useful life of measure |  |  | 12 |  |  |  |  | yrs | AEG 2023 benchmarking. Several sources say front-loading machines typically last 11 years while top-loading machines typically last 14 years. This value represents a weighted average across front- and top-loading counts using CEE and ENERGY STAR data, accessed Jan. 23, 2023.1,2,3
Notes:
1. ENERGY STAR Product Finder, available here: <https://www.energystar.gov/productfinder/product/certified-clothes-washers/results>.
2. CEE Residential Clothes Washers Qualifying Product List, available here: <https://library.cee1.org/content/qualifying-product-lists-residential-clothes-washers>.
3. Refer to AEG's analysis file named "PY23 TRM - Residential Clothes Washer - Analysis File." Relevant analysis sheets include "Variables & Assumptions," "CAP Analysis," "IMEF Analysis," "CEE Data >2.5 cu.ft.," "CEE Data <=2.5 cu.ft.," ENERGY STAR Data," "RECS 2020," and "Loadshape Analysis."
4. Maryland/Mid-Atlantic Technical Reference Manual, Version 10, Prepared by Shelter Analytics, Facilitated and Managed by Northeast Energy Efficiency Partnerships, March 2020.
5. See "EERE-2008-BT-STD-0019-0047_attachment_23.pdf" for user instructions for life-cycle cost and payback period spreadsheets, available here: <https://www.regulations.gov/docket/EERE-2008-BT-STD-0019>.
6. The EFLH value was derived from 8760 hourly load shape data for an average clothes washer, assuming EFLH = Annual kWh/Max kW during year. The analysis leverages load shapes compiled for the 2020 State of Hawaii Market Potential Study. The source of the clothes washer load shape data is the California Energy Commission. This analysis assumes the clothes washer's load shape is a reasonable proxy for the savings load shape. Note: The EFLH value is not intended to represent the operating hours of a single clothes washer. This EFLH value must be paired with the CF value below to yield meaningful peak demand savings.
7. The CF value was derived from 8760 hourly load shape data for an average clothes washer, assuming CF = Average kW during average weekday peak period/Max kW during year. The analysis leverages load shapes compiled for the 2020 State of Hawaii Market Potential Study. The source of the clothes washer load shape data is the California Energy Commission. This analysis assumes the clothes washer's load shape is a reasonable proxy for the savings load shape. This CF value must be paired with the EFLH value above to yield meaningful peak demand savings.
SAVINGS
Measure Name |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  |  |  | Lifetime Energy Savings
Clothes Washer Tier 1 |  |  | 0.016 |  |  | 126.04 |  |  |  |  | 1512.48
Clothes Washer Tier 2 |  |  | 0.02 |  |  | 154.14 |  |  |  |  | 1849.68
Clothes Washer Tier 3 |  |  | 0.022 |  |  | 171.23 |  |  |  |  | 2054.76
RESOURCES
• | AEG's 2023 Analysis File named "PY23 TRM - Residential Clothes Washer - Analysis File."
• | AEG's Analysis File named "AEG HPUC Baseline Study Data - Analysis File."
• | California eTRM, Clothes Washer, Residential, SWAP004-03, effective Jan. 1, 2023, available here: <https://www.caetrm.com/measure/SWAP004/03/>, accessed Jan. 23, 2023.
• | CEE Residential Clothes Washers Qualifying Product List, available here: <https://library.cee1.org/content/qualifying-product-lists-residential-clothes-washers>, accessed Jan. 23, 2023.
• | CEE Super Efficient Home Appliances Initiative, High Efficiency Specifications for Residential Clothes Washers, Effective Feb. 5, 2018, available here: <https://library.cee1.org/system/files/library/13445/CEE_ResidentialClothesWasherSpecification_05Feb2018.pdf>, accessed Jan. 26, 2023.
• | Code of Federal Regulations, 10 CFR 430.32, Subpart C, Energy and Water Conservation Standards and their Effective Dates, Paragraph (g): Clothes Washers, available here: <https://www.govinfo.gov/content/pkg/CFR-2022-title10-vol3/pdf/CFR-2022-title10-vol3-sec430-32.pdf>.
• | Consortium for Energy Efficiency, CEE Tiers and ENERGY STAR, <https://cee1.org/content/cee-tiers-and-energy-star>.
• | ENERGY STAR Version 8.1 Clothes Washer Specification, available here: <https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Version%208.1%20Clothes%20Washer%20Final%20Specificaiton%20-%20Partner%20Commitments%20and%20Eligibility%20Criteria.pdf>.
• | ENERGY STAR Product Finder, available here: <https://www.energystar.gov/productfinder/product/certified-clothes-washers/results>, accessed Jan. 23, 2023.
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | 2023 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 11.0, Volume 3: Residential Measures, FINAL, September 22, 2022. Effective: January 1, 2023.
• | Maryland/Mid-Atlantic Technical Reference Manual, Version 10, Prepared by Shelter Analytics, Facilitated and Managed by Northeast Energy Efficiency Partnerships, March 2020.
• | New York State Joint Utilities, New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs – Residential, Multi-Family, and Commercial/Industrial Measures, Version 10, Effective Date - Jan. 1, 2023.
• | Public Utility Commission of Texas, Texas Technical Reference Manual, Version 10.0, Volume 2: Residential Measures, Program Year 2023.
• | Regional Technical Forum, UES Measures, Residential Clothes Washers, Version 8.0, Apr. 18, 2022, available here: <https://rtf.nwcouncil.org/measure/clothes-washers-0/>.
• | 2020 Residential Energy Consumption Survey (RECS), Table HC3.6 Appliances in U.S. Homes, by Climate Region, available here: <https://www.eia.gov/consumption/residential/data/2020/#appliances>, accessed Jan. 23, 2023.
• | Technical Support Document: Energy Efficiency Program for Consumer Products and Commercial and Industrial Equipment: Residential Clothes Washers, April 2012, U.S. Department of Energy, available here: <https://www.regulations.gov/document/EERE-2008-BT-STD-0019-0047>.
• | The Spruce, T. Dale, How Long Does a Washing Machine Last?, Sep. 2, 2022, available here: <https://www.thespruce.com/how-long-does-a-washing-machine-last-5272534>.
• | U.S. Department of Energy, Energy Conservation Program: Energy Conservation Standards for Residential Clothes Washers, EERE-2008-BT-STD-0019, available here: <https://www.regulations.gov/docket/EERE-2008-BT-STD-0019>.
∆𝑘𝑊ℎ=𝐶𝐴𝑃∗ 𝐶𝑌𝐶𝐿𝐸𝑆 ∗
{█((1∕〖𝐼𝑀𝐸𝐹〗_𝑏𝑎𝑠𝑒 )∗[〖%𝐸〗_(𝑤𝑎𝑠ℎ,𝑏𝑎𝑠𝑒)+(〖%𝐸〗_(ℎ𝑒𝑎𝑡,𝑏𝑎𝑠𝑒)∗〖%𝐻𝐸𝐴𝑇𝐸𝑅〗_𝑒𝑙𝑒𝑐𝑡𝑟𝑖𝑐 )+(〖%𝐸〗_(𝑑𝑟𝑦,𝑏𝑎𝑠𝑒)∗〖%𝐷𝑅𝑌𝐸𝑅〗_𝑒𝑙𝑒𝑐𝑡𝑟𝑖𝑐 )]@−(1∕〖𝐼𝑀𝐸𝐹〗_ℎ𝑒 )∗[〖%𝐸〗_(𝑤𝑎𝑠ℎ,ℎ𝑒)+(〖%𝐸〗_(ℎ𝑒𝑎𝑡,ℎ𝑒)∗〖%𝐻𝐸𝐴𝑇𝐸𝑅〗_𝑒𝑙𝑒𝑐𝑡𝑟𝑖𝑐 )+(〖%𝐸〗_(𝑑𝑟𝑦,ℎ𝑒)∗〖%𝐷𝑅𝑌𝐸𝑅〗_𝑒𝑙𝑒𝑐𝑡𝑟𝑖𝑐 )] )}
∆𝑘𝑊=∆𝑘𝑊ℎ∗𝐶𝐹/𝐸𝐹𝐿𝐻
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## R_Appliance_Heat Pump Dryer
RESIDENTIAL: Heat Pump Clothes Dryer
Return to TOC
UPDATE STATUS
Added in Fall 2023 for the Mid-Year PY23 TRM V2.
MEASURE DETAILS
Description
Replacement of an Electric Resistance Clothes Dryer with an ENERGY STAR Heat Pump Clothes Dryer in an existing home, or installation of an Heat Pump Clothes Dryer in a newly constructed home.
Program Criteria
The High Efficiency Equipment must be an ENERGY STAR certified Heat Pump Clothes Dryer.
Unit of Measure
One clothes dryer.
Baseline Equipment
The Baseline Equipment is an Electric Resistance Clothes Dryer.
High Efficiency Equipment
The High Efficiency equipment is an ENERGY STAR certified Heat Pump Clothes Dryer.
ALGORITHMS
Baseline Annual Energy Use, kWh/yr
(1)
High Efficiency Annual Energy Use, kWh/yr
(2)
Annual Energy Savings, kWh/yr
(3)
Peak Demand Reduction, kW
(4)
Lifetime Energy Savings, kWh
(5)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [10 empty] | Value |  | Unit | Source/Notes
kWhbase |  |  |  | Annual energy use of electric resistance clothes dryer | [10 empty] | See Equation 1 |  | kWh
kWhee |  |  |  | Annual energy use of heat pump clothes dryer | [10 empty] | See Equation 2 |  | kWh
LOAD | HOURS | HOURS | HOURS | Average weight of load in compact electric dryer | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | 3 |  | lbs/cycle | Code for Federal Regulations for clothes dryer.1
|  |  |  | Average weight of load in standard electric dryer | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | 8.45
CEFbase |  |  |  | Combined Energy Factor of vented and ventless 120-V compact electric clothes dryer | [10 empty] | 3.61 |  | lbs/kWh | Code for Federal Regulations for clothes dryer1
|  |  |  | Combined Energy Factor of vented 240-V compact electric clothes dryer | [10 empty] | 3.27
|  |  |  | Combined Energy Factor of ventless 240-V compact electric clothes dryer | [10 empty] | 2.55
|  |  |  | Combined Energy Factor of vented and ventless standard electric clothes dryer | [10 empty] | 3.73
CEFee |  |  |  | Combined Energy Factor of heat pump clothes dryer | [10 empty] | 4.5 |  | lbs/kWh | California Technical Forum.2 CEF applies to all voltage levels, vented and ventless, and dryer sizes.
CYCLES | HOURS | HOURS | HOURS | Annual number of cycles for compact size electric dryer | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | 251 |  |  | California Technical Forum.2
|  |  |  | Annual number of cycles for standard size electric dryer | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | 283
ΔkWh |  |  |  | Annual energy savings | [10 empty] | See Equation 3 |  | kWh
ΔkW |  |  |  | Peak demand reduction | [10 empty] | See Equation 4 |  | kW
EFLH | HOURS | HOURS | HOURS | Equivalent full load hours, defined here as the sum of the 8760 hourly loads (kWh) from an average single family clothes drying load shape divided by the maximum hourly load (kW) from the same load shape | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | 3432 |  | hrs | Results of clothes drying load shape analysis using Hawaii's peak demand period of non-holiday weekdays, from 5 to 9 pm.3
CF | CF | CF | CF | Peak demand coincidence factor, defined here as the average hourly load (kW) for clothes drying during the average weekday peak period divided by the maximum hourly load (kW) for clothes drying during the year. The CF is calculated using the same load shape used for the EFLH calculation. | [10 empty] | 0.5 |  | - | Results of clothes drying load shape analysis using Hawaii's peak demand period of non-holiday weekdays, from 5 to 9 pm.3
ΔkWhlife |  |  |  | Lifetime energy savings | [10 empty] | See Equation 4 |  | kWh
EULee | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 12 |  | yrs | California Technical Forum.2
1. Federal Standard 10 CFR 430.32(h) Federal Required Minimum CEF Requirements for Clothes Dryers. Title 10 was last amended on 9/29/2023. <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430>
2. California Technical Forum, SWAP003-04, Clothes Dryer, Residential, CPUC Approved January 1, 2023. <https://www.caetrm.com/measure/SWAP003/04/>
3. AEG's analysis of an average clothes drying load shape for a single family house using the Hawaii peak demand period of non-holiday weekdays, from 5 to 9 pm: "Load_shape_by_segment_110519_Clothes Drying 10032023." The source of the clothes drying load shape data is the California Energy Commission. The load shape was compiled along with other load shapes during the 2020 Market Potential Study for Hawaii. The clothes drying load shape analysis provides EFLH=3432 hours and CF=0.50. See "SF_Clothes Drying" tab in AEG's 2023 Analysis File titled "Mid-year PY23 TRM - Residential Heat Pump Dryer - Analysis File." This analysis assumes the clothes drying load shape is a reasonable proxy for the heat pump clothes dryer savings shape. Note: The EFLH value is not intended to represent the operating hours of a single heat pump dryer. This EFLH value must be paired with the CF value to yield meaningful peak demand savings.
SAVINGS
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings |  |  | Lifetime Energy Savings
Residential Vented and Ventless Compact 120-V Heat Pump Dryer | [7 empty] | 0.006 | [7 empty] | 41.25 |  |  | 495
Residential Vented Compact 240-V Heat Pump Dryer | [7 empty] | 0.009 | [7 empty] | 62.94 |  |  | 755.28
Residential Ventless Compact 240-V Heat Pump Dryer | [7 empty] | 0.019 | [7 empty] | 127.96 |  |  | 1535.52
Residential Vented and Ventless Standard Heat Pump Dryer | [7 empty] | 0.016 | [7 empty] | 109.7 |  |  | 1316.4
RESOURCES
• | AEG's 2023 Analysis File titled Mid-year PY23 TRM - Residential Heat Pump Dryer - Analysis File."
• | AEG's Load Shape Analysis File titled "Load_shape_by_segment_110519_Clothes Drying 10032023."
• | California Technical Forum, SWAP003-04, Clothes Dryer, Residential, CPUC Approved January 1, 2023. <https://www.caetrm.com/measure/SWAP003/04/>.
• | Federal Standard 10 CFR 430.32(h) Federal Required Minimum CEF Requirements for Clothes Dryers. Title 10 was last amended on 9/29/2023. <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430>.
∆𝑘𝑊=∆𝑘𝑊ℎ/𝐸𝐹𝐿𝐻∗𝐶𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝑒𝑒
∆𝑘𝑊ℎ=(〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊ℎ〗_𝑒𝑒 )
〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒=𝐿𝑂𝐴𝐷/𝐶𝐸𝐹𝑏𝑎𝑠𝑒∗𝐶𝑌𝐶𝐿𝐸𝑆
〖𝑘𝑊ℎ〗_𝑒𝑒=𝐿𝑂𝐴𝐷/𝐶𝐸𝐹𝑒𝑒∗𝐶𝑌𝐶𝐿𝐸𝑆

## R_Appliance_Clothes Dryer
RESIDENTIAL: Clothes Dryer
Return to TOC
MEASURE DETAILS
Description
Energy efficient clothes dryer as specified below replacing a baseline clothes dryer.
Program Criteria
ENERGY STAR certified
Unit of Measure
One dryer
Baseline Equipment
Clothes dryer meeting minimum federal requirements (blended average of pre-1/1/15 and post-1/1/15 federal standards).
High Efficiency Equipment
ENERGY STAR certified electric clothes dryer ≥ 4.4 ft3
ALGORITHMS
ΔE |  |  | = [(LOAD / CEF_base) - (LOAD / CEF_he)] * CYCLES
ΔP |  |  | = (ΔE / HRS) * CF
ΔE_lifetime |  |  | = ΔE * (Measure Life)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Value | Unit | Notes
ΔE |  | Annual energy reduction |  |  | Calculated | kWh
ΔP |  | Peak power demand reduction |  |  | Calculated | kW
LOAD |  | Average total weight (lbs) of clothes per drying cycle |  |  | 8.45 | lbs | Based on ENERGY STAR product criteria testing.1
CEF_base |  | Combined Energy Factor (lbs/kWh) of the baseline unit |  |  | 3.15 | - | Blended average of early replacement (80%) and replace on burnout (20%) baselines, using federal minimum CEF. From 1994-2014, minimum CEF was 3.01 (early replacement baseline). Since 2015, minimum CEF has been 3.73 (replace on burnout baseline).
CEF_he |  | Combined Energy Factor (lbs/kWh) of the efficient unit |  |  | 3.93 | - | Based on ENERGY STAR product criteria testing.
CYCLES |  | Average number of dryer cycles per dryer per year |  |  | 311 | - | NEEA Dryer Field Study, 2014.2
HRS |  | Average run hours per dryer per year |  |  | 290 | hrs | 56 minutes/cycle based on NEEA Dryer Field Study, 2014.2
CF |  | Coincidence factor |  |  | 5.7% | - | Based on analysis of clothes dryer loadshape curve from DOE PNNL study. See Tab 2 for calculation.3
Measure Life |  | Expected duration of savings |  |  | 14 | yrs | ENERGY STAR Market & Industry Scoping Report, 2011.4
1 https://www.energystar.gov/products/appliances/clothes_dryers/key_product_criteria
2 https://www.neea.org/docs/default-source/reports/neea-clothes-dryer-field-study.pdf
3 http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20110.pdf
4 https://www.energystar.gov/sites/default/files/asset/document/ENERGY_STAR_Scoping_Report_Residential_Clothes_Dryers.pdf
SAVINGS
Measure Name |  |  |  | Peak Demand Savings | Annual Energy Savings
Clothes Dryer |  |  |  | 0.033 | 165.58

## R_Appliance_Refrigerator
RESIDENTIAL: Refrigerator and Freezer
Return to TOC
UPDATE STATUS
Updated in Winter 2019-2020 for PY20 TRM.
MEASURE DETAILS
Description
ENERGY STAR v5.0 certified refrigerator/freezer as specified below replacing a non-ENERGY STAR refrigerator/freezer and turning in the existing refrigerator/freezer to be recycled. Also, turn-in only refrigerator/freezer rebate available.
Program Criteria
ENERGY STAR v5.0 certified.
Unit of Measure
One refrigerator/freezer.
Baseline Equipment
The base case for the new unit is the current federal requirement (National Appliance Energy Conservation Act, or NAECA, 2011) for a refrigerator/freezer, effective as of September 15, 2014. The base case for a turned-in unit is the pre-existing refrigerator/freezer.
High Efficiency Equipment
The efficient case for the new unit is an ENERGY STAR v5.0 qualified refrigerator/freezer, which has an efficiency criteria of 10 percent less energy use than minimum federal requirements.
ALGORITHMS
The base case (minimum federal requirement) and efficient case (ENERGY STAR) for a new refrigerator/freezer are based on the adjusted volume (AV) in cubic feet of the unit. The adjusted volume is calculated as follows (see Equations 1 and 2):
Refrigerator Adjusted Volume (AV), cu ft
(1)
Freezer Adjusted Volume (AV), cu ft
(2)
Unit Replacement Annual Energy Savings, kWh/yr
(3)
Unit Replacement Peak Demand Reduction, kW
(4)
Unit Replacement Lifetime Energy Savings, kWh
(5)
Unit Replacement with Turn-In Annual Energy Savings, kWh/yr
(6)
Unit Replacement with Turn-In Peak Demand Reduction, kW
(7)
Unit Replacement with Turn-In Lifetime Energy Savings, kWh
(8)
2nd Unit Turn-In Only Annual Energy Savings, kWh/yr
(9)
2nd Unit Turn-In Only Peak Demand Reduction, kW
(10)
2nd Unit Turn-In Only Lifetime Energy Savings, kWh
(11)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description |  |  |  | Value |  |  | Unit |  | Source/Notes
AVR |  |  |  | Adjusted volume of refrigerator1 |  |  |  | Default = 25.4 |  |  | cu ft |  | See Footnote 2 for Default assumption
AVF |  |  |  | Adjusted volume of freezer1 |  |  |  | Default = 26.0 |  |  | cu ft |  | See Footnote 3 for Default assumption
Fresh volume |  |  |  | Fresh volume of new refrigerator |  |  |  | User entry |  |  | cu ft |  | Based on actual unit; used to calculate AV in Equation 1
Freezer volume |  |  |  | Freezer volume of new refrigerator or freezer |  |  |  | User entry |  |  | cu ft |  | Based on actual unit; used to calculate AV in Equations 1 and 2
EBase |  |  |  | Annual energy usage of baseline unit |  |  |  | See Tables 1 and 2 |  |  | kWh |  | Federal requirements as of September 15, 2014
EEE |  |  |  | Annual energy usage of new efficient unit |  |  |  | See Tables 1 and 2 |  |  | kWh |  | ENERGY STAR as of September 15, 2014
ETurn-in |  |  |  | Annual energy usage of turned-in refrigerator |  |  |  | 758 |  |  | kWh |  | ENERGY STAR "Flip Your Fridge Calculator" 4
|  |  |  | Annual energy usage of turned-in freezer |  |  |  | 574 |  |  | kWh |  | ENERGY STAR "Flip Your Fridge Calculator" 4
PF |  |  |  | Persistence factor |  |  |  | 1 |  |  | - |  | See Footnote 5
HRS |  |  |  | Annual operating hours |  |  |  | 8760 |  |  | hrs |  | Conservative assumption when used to estimate peak demand savings
CF |  |  |  | Coincidence factor |  |  |  | 1 |  |  | - |  | Acceptable if used along with 8760 hours
EULReplace,R |  |  |  | Effective useful life of new refrigerator |  |  |  | 14 |  |  | yrs |  | AEG's Fall 2018 Benchmarking 6
EULReplace,F |  |  |  | Effective useful life of new freezer |  |  |  | 17 |  |  | yrs |  | AEG's Fall 2018 Benchmarking
RULTurn-In,R |  |  |  | Remaining useful life of turned-in refrigerator |  |  |  | 8 |  |  | yrs |  | AEG's Fall 2018 Benchmarking
RULTurn-In,F |  |  |  | Remaining useful life of turned-in freezer |  |  |  | 7 |  |  | yrs |  | AEG's Fall 2018 Benchmarking
1 Source of AV equations is ENERGY STAR, Savings Calculator for ENERGY STAR Appliances, available at: https://www.energystar.gov/sites/default/files/asset/document/appliance_calculator.xlsx, accessed December 15, 2018.
2 Based on average of default values for Total Model Volume for refrigerators from ENERGY STAR calculator (20.5 cu ft), and assuming 68.6% of volume is refrigerator (fresh volume), which is default in ENERGY STAR calculator. Recommendation for future update: Determine average AV of units installed through Hawai‘i program.
3 Based on average of default values for Total Model Volume for freezers (non-compact ) from ENERGY STAR calculator (15.0 cu ft). Recommendation for future update: Determine average AV of units installed through Hawai‘i program.
4 Source: ENERGY STAR "Flip Your Fridge" calculator, <https://www.energystar.gov/index.cfm?fuseaction=refrig.calculator>, accessed on January 21, 2020. Average of five refrigerator types (top, bottom, side, French, 4-door); capacity: 19.0-21.4 cu ft; model year: 2001-2010. Average of two freezer types (upright, chest); capacity: < 16.5 cu ft; model year: 2001-2010. Recommend updating with Hawai‘i-specific data on the types/ages of units turned-in through the program in future TRM update.
5 Use value of PF=1 until more data is available on savings persistence of ENERGY STAR units relative to baseline units.
6 See analysis file titled "AEG HPUC EUL Analysis."
Table 1. Base and Efficient Case Refrigerator Standards, Total Volume ≥ 7.75 cu ft and < 39 cu ft, Equation: E = a*AV + b
Product Category | [7 empty] | Ebase, Federal Standard, Maximum kWh/yr 1 | [5 empty] | EEE, ENERGY STAR, Maximum kWh/yr 2
Equation Term: | [7 empty] | a |  |  | b |  |  | a |  | b
Manual Defrost w/ and w/o TDD, All Configurations | [7 empty] | 6.79 |  |  | 193.6 |  |  | 6.11 |  | 174.2
Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [7 empty] | 8.07 |  |  | 233.7 |  |  | 7.26 |  | 210.3
Auto Defrost w/o TDD, Side by Side | [7 empty] | 8.51 |  |  | 297.8 |  |  | 7.66 |  | 268
Auto Defrost w/o TDD, Bottom Freezer | [7 empty] | 8.85 |  |  | 317 |  |  | 7.97 |  | 285.3
Auto Defrost w/ TDD, Bottom Freezer | [7 empty] | 9.25 |  |  | 475.4 |  |  | 8.33 |  | 436.3
Auto Defrost w/ TDD, Top Freezer | [7 empty] | 8.4 |  |  | 385.4 |  |  | 7.56 |  | 355.3
Auto Defrost w/ TDD, Side by Side | [7 empty] | 8.54 |  |  | 432.8 |  |  | 7.69 |  | 397.9
"Average" Refrigerator 3 | [7 empty] | 8.3443 |  |  | 333.6714 |  |  | 7.5114 |  | 303.9
1 Electronic Code of Federal Regulations, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates. (a) Refrigerators/refrigerator-freezers/freezers, current as of December 13, 2018, accessed December 17, 2018.
2 ENERGY STAR Program Requirements for Residential Refrigerators and Freezers. Eligibility Criteria, V5.0, https://www.energystar.gov/ia/partners/product_specs/program_reqs/Refrigerators_and_Freezers_Program_Requirements_V5.0.pdf, accessed December 17, 2018.
3 Recommend updating with weighted average by type using program data or baseline data in future TRM update.
Table 2. Base and Efficient Case Freezer Standards, Total Volume ≥ 7.75 cu ft and < 39 cu ft, Equation: E = a*AV + b
Product Category | [7 empty] | Ebase, Federal Standard, Maximum kWh/yr 1 | [5 empty] | EEE, ENERGY STAR, Maximum kWh/yr 2
Equation Term: | [7 empty] | a |  |  | b |  |  | a |  | b
Upright Freezers, Manual Defrost | [7 empty] | 5.57 |  |  | 193.7 |  |  | 5.01 |  | 174.3
Upright Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 8.62 |  |  | 228.3 |  |  | 7.76 |  | 205.5
Upright Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 8.62 |  |  | 312.3 |  |  | 7.76 |  | 289.5
Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 9.86 |  |  | 260.9 |  |  | 8.87 |  | 234.8
Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 9.86 |  |  | 344.9 |  |  | 8.87 |  | 318.8
Chest Freezers and All Other Freezers, except Compact Freezers | [7 empty] | 7.29 |  |  | 107.8 |  |  | 6.56 |  | 97
Chest Freezers with Auto Defrost | [7 empty] | 10.24 |  |  | 148.1 |  |  | 9.22 |  | 133.3
"Average" Freezer 3 | [7 empty] | 8.58 |  |  | 228 |  |  | 7.7214 |  | 207.6
1 Electronic Code of Federal Regulations, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates. (a) Refrigerators/refrigerator-freezers/freezers, current as of December 13, 2018, accessed December 17, 2018.
2 ENERGY STAR Program Requirements for Residential Refrigerators and Freezers. Eligibility Criteria, V5.0, https://www.energystar.gov/ia/partners/product_specs/program_reqs/Refrigerators_and_Freezers_Program_Requirements_V5.0.pdf, accessed December 17, 2018.
3 Recommend updating with weighted average by type using program data or baseline data in future TRM update.
SAVINGS - DEEMED
Deemed Savings (based on default value for Adjusted Volume, AV): Refrigerator w/o Turn-In
| Refrigerator w/o Turn-In, AV = 25.4 cu ft Product Category | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Manual Defrost w/ and w/o TDD, All Configurations | [7 empty] | 0.004 |  |  |  | 36.67 |  | 513.38
| Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [7 empty] | 0.005 |  |  |  | 43.97 |  | 615.58
| Auto Defrost w/o TDD, Side by Side | [7 empty] | 0.006 |  |  |  | 51.39 |  | 719.46
| Auto Defrost w/o TDD, Bottom Freezer | [7 empty] | 0.006 |  |  |  | 54.05 |  | 756.7
| Auto Defrost w/ TDD, Bottom Freezer | [7 empty] | 0.007 |  |  |  | 62.47 |  | 874.58
| Auto Defrost w/ TDD, Top Freezer | [7 empty] | 0.006 |  |  |  | 51.44 |  | 720.16
| Auto Defrost w/ TDD, Side by Side | [7 empty] | 0.006 |  |  |  | 56.49 |  | 790.86
| "Average" Refrigerator | [7 empty] | 0.006 |  |  |  | 50.93 |  | 713.02
Deemed Savings (based on default value for Adjusted Volume, AV): Freezer w/o Turn-In
| Freezer w/o Turn-In, AV = 26.0 cu ft Product Category | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Upright Freezers, Manual Defrost | [7 empty] | 0.004 |  |  |  | 33.96 |  | 577.32
| Upright Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 0.005 |  |  |  | 45.16 |  | 767.72
| Upright Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 0.005 |  |  |  | 45.16 |  | 767.72
| Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 0.006 |  |  |  | 51.84 |  | 881.28
| Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 0.006 |  |  |  | 51.84 |  | 881.28
| Chest Freezers and All Other Freezers, except Compact Freezers | [7 empty] | 0.003 |  |  |  | 29.78 |  | 506.26
| Chest Freezers with Auto Defrost | [7 empty] | 0.005 |  |  |  | 41.32 |  | 702.44
| "Average" Freezer | [7 empty] | 0.005 |  |  |  | 42.72 |  | 726.24
Deemed Savings (based on default value for Adjusted Volume, AV): Refrigerator w/ Turn-In
NOTE: Lifetime Energy Savings and Total Resource Benefits (TRBs) must be calculated using a combination of two baseline periods: 1) new refrigerator (EUL = 14 yr) and 2) turned-in refrigerator (RUL = 8 yr).
| Refrigerator w/ Turn-In, AV = 25.4 cu ft Product Category | [5 empty] | Peak Demand Savings, kW |  |  |  |  | Annual Energy Savings, kWh/yr |  |  | Lifetime Energy Savings
[7 empty] | 1st BL: New + Turn-in 1 |  |  | 2nd BL: New Only 2 |  | 1st BL: New + Turn-in 1 |  | 2nd BL: New Only 2
| Manual Defrost w/ and w/o TDD, All Configurations | [5 empty] | 0.091 |  |  | 0.004 |  | 794.67 |  | 36.67 | 6577.38
| Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [5 empty] | 0.092 |  |  | 0.005 |  | 801.97 |  | 43.97 | 6679.58
| Auto Defrost w/o TDD, Side by Side | [5 empty] | 0.092 |  |  | 0.006 |  | 809.39 |  | 51.39 | 6783.46
| Auto Defrost w/o TDD, Bottom Freezer | [5 empty] | 0.093 |  |  | 0.006 |  | 812.05 |  | 54.05 | 6820.7
| Auto Defrost w/ TDD, Bottom Freezer | [5 empty] | 0.094 |  |  | 0.007 |  | 820.47 |  | 62.47 | 6938.58
| Auto Defrost w/ TDD, Top Freezer | [5 empty] | 0.092 |  |  | 0.006 |  | 809.44 |  | 51.44 | 6784.16
| Auto Defrost w/ TDD, Side by Side | [5 empty] | 0.093 |  |  | 0.006 |  | 814.49 |  | 56.49 | 6854.86
| "Average" Refrigerator | [5 empty] | 0.092 |  |  | 0.006 |  | 808.93 |  | 50.93 | 6777.02
1 Use for Years 1 through 8 in TRB calculation.
2 Use for Years 9 through 14 in TRB calculation.
Deemed Savings (based on default value for Adjusted Volume, AV): Freezer w/ Turn-In
NOTE: Lifetime Energy Savings and Total Resource Benefits (TRBs) must be calculated using a combination of two baseline periods: 1) new freezer (EUL = 17 yr) and 2) turned-in freezer (RUL = 7 yr).
| Freezer w/ Turn-In, AV = 26.0 cu ft Product Category | [5 empty] | Peak Demand Savings, kW |  |  |  |  | Annual Energy Savings, kWh/yr |  |  | Lifetime Energy Savings
[7 empty] | 1st BL: New + Turn-in 1 |  |  | 2nd BL: New Only 2 |  | 1st BL: New + Turn-in 1 |  | 2nd BL: New Only 2
| Upright Freezers, Manual Defrost | [5 empty] | 0.069 |  |  | 0.004 |  | 607.96 |  | 33.96 | 4595.32
| Upright Freezers, Auto Defrost, w/o Auto Icemaker | [5 empty] | 0.071 |  |  | 0.005 |  | 619.16 |  | 45.16 | 4785.72
| Upright Freezers, Auto Defrost, w/ Auto Icemaker | [5 empty] | 0.071 |  |  | 0.005 |  | 619.16 |  | 45.16 | 4785.72
| Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [5 empty] | 0.071 |  |  | 0.006 |  | 625.84 |  | 51.84 | 4899.28
| Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [5 empty] | 0.071 |  |  | 0.006 |  | 625.84 |  | 51.84 | 4899.28
| Chest Freezers and All Other Freezers, except Compact Freezers | [5 empty] | 0.069 |  |  | 0.003 |  | 603.78 |  | 29.78 | 4524.26
| Chest Freezers with Auto Defrost | [5 empty] | 0.07 |  |  | 0.005 |  | 615.32 |  | 41.32 | 4720.44
| "Average" Freezer | [5 empty] | 0.07 |  |  | 0.005 |  | 616.72 |  | 42.72 | 4744.24
1 Use for Years 1 through 7 in TRB calculation.
2 Use for Years 8 through 17 in TRB calculation.
Deemed Savings: Refrigerator or Freezer Turn-In Only
| Measure Name | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Refrigerator Turn-In Only, AV = 25.4 cu ft Product Category | [7 empty] | 0.087 |  |  |  | 758 |  | 6064
| Freezer Turn-In Only, AV = 26.0 cu ft Product Category | [7 empty] | 0.066 |  |  |  | 574 |  | 4018
SAVINGS - SEMI-PRESCRIPTIVE CALCULATOR
| Refrigerator | [6 empty] | Freezer
| Enter Fresh Volume |  |  |  |  | 22 |  | Enter Frozen Volume | [5 empty] | 12
| Enter Frozen Volume |  |  |  |  | 8
|  | AVR = | 36.1 |  | per Equation 1 |  |  |  | AVF = | 20.8 |  |  | per Equation 2
Semi-Prescriptive Savings (based on user entry): Refrigerator w/o Turn-In
| Refrigerator w/o Turn-In Product Category | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Manual Defrost w/ and w/o TDD, All Configurations | [7 empty] | 0.005 |  |  |  | 43.95 |  | 615.3
| Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [7 empty] | 0.006 |  |  |  | 52.64 |  | 736.96
| Auto Defrost w/o TDD, Side by Side | [7 empty] | 0.007 |  |  |  | 60.48 |  | 846.72
| Auto Defrost w/o TDD, Bottom Freezer | [7 empty] | 0.007 |  |  |  | 63.47 |  | 888.58
| Auto Defrost w/ TDD, Bottom Freezer | [7 empty] | 0.008 |  |  |  | 72.31 |  | 1012.34
| Auto Defrost w/ TDD, Top Freezer | [7 empty] | 0.007 |  |  |  | 60.42 |  | 845.88
| Auto Defrost w/ TDD, Side by Side | [7 empty] | 0.007 |  |  |  | 65.59 |  | 918.26
| "Average" Refrigerator | [7 empty] | 0.007 |  |  |  | 59.84 |  | 837.76
Semi-Prescriptive Savings (based on user entry): Freezer w/o Turn-In
| Freezer w/o Turn-In Product Category | [7 empty] | Peak Demand Savings |  |  |  | Annual Energy Savings |  | Lifetime Energy Savings
| Upright Freezers, Manual Defrost | [7 empty] | 0.004 |  |  |  | 31.05 |  | 527.85
| Upright Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 0.005 |  |  |  | 40.69 |  | 691.73
| Upright Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 0.005 |  |  |  | 40.69 |  | 691.73
| Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [7 empty] | 0.005 |  |  |  | 46.69 |  | 793.73
| Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [7 empty] | 0.005 |  |  |  | 46.69 |  | 793.73
| Chest Freezers and All Other Freezers, except Compact Freezers | [7 empty] | 0.003 |  |  |  | 25.98 |  | 441.66
| Chest Freezers with Auto Defrost | [7 empty] | 0.004 |  |  |  | 36.02 |  | 612.34
| "Average" Freezer | [7 empty] | 0.004 |  |  |  | 38.26 |  | 650.42
Semi-Prescriptive Savings (based on user entry): Refrigerator w/ Turn-In
NOTE: Lifetime Energy Savings and Total Resource Benefits (TRBs) must be calculated using a combination of two baseline periods: 1) new refrigerator (EUL = 14 yr) and 2) turned-in refrigerator (RUL = 8 yr).
| Refrigerator w/ Turn-In Product Category | [5 empty] | Peak Demand Savings, kW |  |  |  |  | Annual Energy Savings, kWh/yr |  |  | Lifetime Energy Savings
[7 empty] | 1st BL: New + Turn-in 1 |  |  | 2nd BL: New Only 2 |  | 1st BL: New + Turn-in 1 |  | 2nd BL: New Only 2
| Manual Defrost w/ and w/o TDD, All Configurations | [5 empty] | 0.092 |  |  | 0.005 |  | 801.95 |  | 43.95 | 6679.3
| Auto Defrost w/o TDD, Top Freezer and Single Door Refrigerators | [5 empty] | 0.093 |  |  | 0.006 |  | 810.64 |  | 52.64 | 6800.96
| Auto Defrost w/o TDD, Side by Side | [5 empty] | 0.093 |  |  | 0.007 |  | 818.48 |  | 60.48 | 6910.72
| Auto Defrost w/o TDD, Bottom Freezer | [5 empty] | 0.094 |  |  | 0.007 |  | 821.47 |  | 63.47 | 6952.58
| Auto Defrost w/ TDD, Bottom Freezer | [5 empty] | 0.095 |  |  | 0.008 |  | 830.31 |  | 72.31 | 7076.34
| Auto Defrost w/ TDD, Top Freezer | [5 empty] | 0.093 |  |  | 0.007 |  | 818.42 |  | 60.42 | 6909.88
| Auto Defrost w/ TDD, Side by Side | [5 empty] | 0.094 |  |  | 0.007 |  | 823.59 |  | 65.59 | 6982.26
| "Average" Refrigerator | [5 empty] | 0.093 |  |  | 0.007 |  | 817.84 |  | 59.84 | 6901.76
1 Use for Years 1 through 8 in TRB calculation.
2 Use for Years 9 through 14 in TRB calculation.
Semi-Prescriptive Savings (based on user entry): Freezer w/ Turn-In
NOTE: Lifetime Energy Savings and Total Resource Benefits (TRBs) must be calculated using a combination of two baseline periods: 1) new freezer (EUL = 17 yr) and 2) turned-in freezer (RUL = 7 yr).
| Freezer w/ Turn-In Product Category | [5 empty] | Peak Demand Savings, kW |  |  |  |  | Annual Energy Savings, kWh/yr |  |  | Lifetime Energy Savings
[7 empty] | 1st BL: New + Turn-in 1 |  |  | 2nd BL: New Only 2 |  | 1st BL: New + Turn-in 1 |  | 2nd BL: New Only 2
| Upright Freezers, Manual Defrost | [5 empty] | 0.069 |  |  | 0.004 |  | 605.05 |  | 31.05 | 4545.85
| Upright Freezers, Auto Defrost, w/o Auto Icemaker | [5 empty] | 0.07 |  |  | 0.005 |  | 614.69 |  | 40.69 | 4709.73
| Upright Freezers, Auto Defrost, w/ Auto Icemaker | [5 empty] | 0.07 |  |  | 0.005 |  | 614.69 |  | 40.69 | 4709.73
| Built-in Freezers, Auto Defrost, w/o Auto Icemaker | [5 empty] | 0.071 |  |  | 0.005 |  | 620.69 |  | 46.69 | 4811.73
| Built-in Freezers, Auto Defrost, w/ Auto Icemaker | [5 empty] | 0.071 |  |  | 0.005 |  | 620.69 |  | 46.69 | 4811.73
| Chest Freezers and All Other Freezers, except Compact Freezers | [5 empty] | 0.068 |  |  | 0.003 |  | 599.98 |  | 25.98 | 4459.66
| Chest Freezers with Auto Defrost | [5 empty] | 0.07 |  |  | 0.004 |  | 610.02 |  | 36.02 | 4630.34
| "Average" Freezer | [5 empty] | 0.07 |  |  | 0.004 |  | 612.26 |  | 38.26 | 4668.42
1 Use for Years 1 through 7 in TRB calculation.
2 Use for Years 8 through 17 in TRB calculation.
RESOURCES
• | AEG's Analysis Files titled "AEG HPUC Dual BL and TRB - Analysis File" and "AEG HPUC Update of Residential Measures - Analysis file."
• | Electronic Code of Federal Regulations, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates. (a) Refrigerators/refrigerator-freezers/freezers, current as of December 13, 2018, accessed December 17, 2018.
• | Energy Information Administration, Residential Energy Consumption Survey, 2015, Table CE3.5: Annual household site end-use consumption in the West--totals and averages, 2015, https://www.eia.gov/consumption/residential/data/2015/c&e/pdf/ce3.5.pdf, accessed December 17, 2018.
• | ENERGY STAR, Flip Your Fridge Calculator, https://www.energystar.gov/index.cfm?fuseaction=refrig.calculator, accessed January 21, 2020.
• | ENERGY STAR, Key Product Criteria, https://www.energystar.gov/products/appliances/refrigerators/key_product_criteria.
• | ENERGY STAR Program Requirements for Residential Refrigerators and Freezers. Eligibility Criteria, V5.0, https://www.energystar.gov/ia/partners/product_specs/program_reqs/ Refrigerators_and_Freezers_Program_Requirements_V5.0.pdf, accessed December 17, 2018.
• | ENERGY STAR, Savings Calculator for ENERGY STAR Appliances, available at: https://www.energystar.gov/sites/default/files/asset/document/appliance_calculator.xlsx, accessed December 15, 2018.
〖𝐴𝑉〗_𝑅=𝐹𝑟𝑒𝑠ℎ 𝑉𝑜𝑙𝑢𝑚𝑒+1.76∗𝐹𝑟𝑒𝑒𝑧𝑒𝑟 𝑉𝑜𝑙𝑢𝑚𝑒
〖𝐴𝑉〗_𝐹=1.73∗𝐹𝑟𝑒𝑒𝑧𝑒𝑟 𝑉𝑜𝑙𝑢𝑚𝑒
〖∆𝑘𝑊ℎ〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒=〖(𝐸〗_𝐵𝑎𝑠𝑒−𝐸_𝐸𝐸)∗𝑃𝐹
〖∆𝑘𝑊〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒=〖(〖∆𝑘𝑊ℎ〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒〗∕〖𝐻𝑅𝑆)∗𝐶𝐹〗
〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒+𝑇𝑢𝑟𝑛−𝑖𝑛)=〖(𝐸〗_𝐵𝑎𝑠𝑒−𝐸_𝐸𝐸+𝐸_(𝑇𝑢𝑟𝑛−𝑖𝑛))∗𝑃𝐹
〖∆𝑘𝑊〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒+𝑇𝑢𝑟𝑛−𝑖𝑛)=〖(〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒+𝑇𝑢𝑟𝑛−𝑖𝑛)〗∕〖𝐻𝑅𝑆)∗𝐶𝐹〗
〖∆𝑘𝑊〗_(𝑇𝑢𝑟𝑛−𝑖𝑛 𝑂𝑛𝑙𝑦)=〖(〖∆𝑘𝑊ℎ〗_(𝑇𝑢𝑟𝑛−𝑖𝑛 𝑂𝑛𝑙𝑦)〗∕〖𝐻𝑅𝑆)∗𝐶𝐹〗
〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒, 𝐿𝑖𝑓𝑒)=〖∆𝑘𝑊ℎ〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒∗〖𝐸𝑈𝐿〗_𝑅𝑒𝑝𝑙𝑎𝑐𝑒
〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒+𝑇𝑢𝑟𝑛−𝑖𝑛, 𝐿𝑖𝑓𝑒)=〖∆𝑘𝑊ℎ〗_(𝑅𝑒𝑝𝑙𝑎𝑐𝑒, 𝐿𝑖𝑓𝑒)+(𝐸_(𝑇𝑢𝑟𝑛−𝑖𝑛)∗𝑃𝐹∗〖𝑅𝑈𝐿〗_(𝑇𝑢𝑟𝑛−𝑖𝑛))
〖∆𝑘𝑊ℎ〗_(𝑇𝑢𝑟𝑛−𝑖𝑛, 𝐿𝑖𝑓𝑒)=〖∆𝑘𝑊〗_(𝑇𝑢𝑟𝑛−𝑖𝑛 𝑂𝑛𝑙𝑦)∗〖𝑅𝑈𝐿〗_(𝑇𝑢𝑟𝑛−𝑖𝑛)
〖∆𝑘𝑊ℎ〗_(𝑇𝑢𝑟𝑛−𝑖𝑛 𝑂𝑛𝑙𝑦)=𝐸_(𝑇𝑢𝑟𝑛−𝑖𝑛)∗𝑃𝐹

## R_Appliance_Dishwasher
RESIDENTIAL: Dishwasher
Return to TOC
UPDATE STATUS
Added in Spring 2019 for PY19 TRM. One parameter was updated in Winter 2019-2020 for PY20 TRM: %DHW.electric.
MEASURE DETAILS
Description
An energy efficient, ENERGY STAR-certified dishwasher for use in residential applications.
Program Criteria
Must have ENERGY STAR certification.
Unit of Measure
One unit.
Baseline Equipment
Non-ENERGY STAR dishwasher that meets the federal standard.
High Efficiency Equipment
ENERGY STAR certified dishwasher that exceeds the federal standard.
ALGORITHMS
peak kW savings | [5 empty] | = [ΔkWh / (Cycles * HRS.cycle)] * CF
annual kWh savings, ΔkWh | [5 empty] | = (kWh.base,yr - kWh.ee,yr) * (%kWh.Op + %kWh.heat * %DHW.electric)
lifetime kWh savings | [5 empty] | = ΔkWh * EUL
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description |  |  | Value |  | Unit | Notes
kWh.base,yr |  |  |  | Annual energy usage of standard non-ES dishwasher. |  |  | 307 |  | kWh/yr | DOE standard effective May 30, 2013.
kWh.ee,yr |  |  |  | Annual energy usage of standard ES dishwasher. |  |  | 270 |  | kWh/yr | ENERGY STAR Residential Dishwasher Specification Version 6.0.
%kWh.Op |  |  |  | Percentage of dishwasher energy consumption used for unit operation. |  |  | 44% |  | % | Assume default of 44% (0.44) per the ENERGY STAR Appliance Calculator.
%kWh.heat |  |  |  | Percentage of dishwasher energy consumption used for water heating. |  |  | 56% |  | % | Assume default of 56% (0.56) per the ENERGY STAR Appliance Calculator.
%DHW.electric |  |  |  | Percentage of domestic hot water assumed to be electric. |  |  | 59% |  | % | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Derived from responses to Q47 of the residential phone / audit survey.
Cycles | CF* | CF* | CF* | Number of cycles per year. |  |  | 215 |  | cycle | Representative average dishwasher use in 10 CFR 430, Subpart B, Appendix C1 - Uniform Test Method for Measuring the Energy Consumption of Dishwashers.
HRS.cycle | CF* | CF* | CF* | Hours per dishwashing cycle. |  |  | 1.5 |  | hrs / cycle | Efficiency Vermont TRM 2015.
CF | CF* | CF* | CF* | Coincidence factor |  |  | 0.036815 |  | - | In the absence of a true region-specific system peak coincidence factor for the end-use, use a run-time average factor calculated as hours of use divided by 8,760 hours per year.
EUL | Measure Life (yrs) | Measure Life (yrs) | Measure Life (yrs) | Effective useful life of measure |  |  | 11 |  | yrs | DEER2020.
SAVINGS
Measure Name |  |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Dishwasher |  |  |  |  | 0.003 |  |  | 28.5 |  |  | 313.5
RESOURCES
• | AEG's Analysis Files titled 1) "New Residential Measures Summary - AEG Analysis file" and 2) "AEG HPUC Baseline Study Data - Analysis File."
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | California Public Utilities Commission, Database of Energy Efficiency Resources, 2020 update, (DEER2020), READI v.2.5.0, Ex Ante Database Support Table Export, EUL_basis, created on 8/24/2018, available here: www.deeresources.com/index.php/homepage. Spreadsheet.
• | Code of Federal Regulations, 10 CFR 430, Subpart B, Appendix C1 - Uniform Test Method for Measuring the Energy Consumption of Dishwashers.
• | Efficiency Vermont Technical Reference User Manual, Measure Savings Algorithms and Cost Assumptions, 2015.
• | ENERGY STAR, Appliance Calculator, available here: https://www.energystar.gov/sites/default/files/asset/.../appliance_calculator.xlsx.
• | ENERGY STAR, Dishwashers, webpage, https://www.energystar.gov/products/appliances/dishwashers.
• | ENERGY STAR, Residential Dishwasher Specification Version 6.0, available here: https://www.energystar.gov/products/spec/residential_dishwasher_specification_version_6_0_pd.

## R_Appliance_Air Purifier
RESIDENTIAL: Air Purifier
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the PY25 TRM.
MEASURE DETAILS
Description
Energy efficient domestic room air purifier, which is defined as a product for improving indoor air quality, other than a central air conditioner, room air conditioner, portable air conditioner, dehumidifier, or furnace, that is an electrically-powered, self-contained, mechanically encased assembly that contains means to remove, destroy, or deactivate particulates, VOC, and/or microorganisms from the air. It excludes products that operate solely using ultraviolet light without a fan for air circulation.
Program Criteria
Air purifier must be ENERGY STAR certified. To be eligible for ENERGY STAR certification, measured ozone shall not exceed 50 parts per billion (ppb). Ozone generators and combination products that provide an additional function, like an air cleaner with a humidifier, are not eligible.
Unit of Measure
One air purifier.
Baseline Equipment
Non-ENERGY STAR air purifier.
High Efficiency Equipment
ENERGY STAR certified air purifier.
ALGORITHMS - ENERGY STAR V2.0, effective before December 31, 2025
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
where
(3)
Lifetime Energy Savings, kWh
(4)
ALGORITHMS - ENERGY STAR V3.0, effective on and after December 31, 2025
Peak Demand Reduction, kW
(5)
Annual Energy Savings, kWh/yr
(6)
Lifetime Energy Savings, kWh
(7)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  |  | Value | Unit | Source/Notes
CAP |  |  | Capacity |  |  |  | See Tables 3 & 5 | CADR | ENERGY STAR Qualified Product List (QPL)
ηb |  |  | Baseline efficiency rating representing the integrated energy factor (IEF) as defined by federal code; use before December 31, 2025 |  |  |  | See Table 1 | PM2.5 CADR/W | Code of Federal Regulations at 10 CFR 430.32(ee), before December 31, 2025
ηe |  |  | High efficiency rating representing the smoke-free clean air delivery rate per watt (CADR/W); use before December 31, 2025 |  |  |  | See Table 3 | Smoke-Free CADR/W | Based on Hawai'i Energy PY23 program data for products certified to ENERGY STAR Product Specification for Room Air Cleaners V2.0
IEFb |  |  | Baseline integrated energy factor - the energy the air cleaner uses when it is in standby mode, as well as its active mode energy; use on or after December 31, 2025 |  |  |  | See Table 4 | PM2.5 CADR/W | Code of Federal Regulations at 10 CFR 430.32(ee), on or after December 31, 2025; definition assumed to match ENERGY STAR Product Specification for Room Air Cleaners V3.0
IEFe |  |  | Efficient integrated energy factor - the energy the air cleaner uses when it is in standby mode, as well as its active mode energy; use on or after December 31, 2025 |  |  |  | See Table 5 | PM2.5 CADR/W | Definition & values per ENERGY STAR Product Specification for Room Air Cleaners V3.0
Pstdby_b |  |  | Baseline efficiency standby power (partial on mode power) |  |  |  | Calculated; see Table 2 | W | ENERGY STAR QPL & Room Air Cleaner Product Spec V2.0
Pbase_allowance |  |  | Partial on mode base power allowance for all products |  |  |  | 1 | W | ENERGY STAR Product Specification for Room Air Cleaners V2.0
Pnet_connected |  |  | Partial on mode network connected power allowance for models with Wi-Fi capability; if no Wi-Fi, this value is 0. |  |  |  | 1 | W | ENERGY STAR Product Specification for Room Air Cleaners V2.0
%wifi |  |  | Share of wi-fi connected products |  |  |  | See Table 2 | % | Derived from ENERGY STAR products available as of May 16, 2025
Pstdby_e |  |  | High efficiency standby power (partial on mode power) |  |  |  | See Table 2 | W | ENERGY STAR Qualified Product List (QPL)
CF |  |  | Coincidence factor, percent of time equipment load corresponds with utility peak load |  |  |  | 0.873 | - | In absence of an air cleaner load shape, the CF was calculated by using HVAC fan load shape as a proxy. See ICF's 2025 analysis file named "Load_shape_by_segment_110519_Air Purifier_05302025."
HRS |  |  | Equipment annual operating hours |  |  |  | 5840 | hrs/yr | ENERGY STAR Appliance Calculator: 16 hrs/day, 365 days/year.
Constant |  |  | Watt/kilowatts conversion |  |  |  | 1000 | W/kW
CADR |  |  | Clean air delivery rate - the measure of the delivery of contaminant free air, within a defined particle size range, by an air cleaner, expressed in cubic feet per minute |  |  |  | Varies | CFM | Definition from ENERGY STAR Product Specification for Room Air Cleaners V3.0
CADR/W |  |  | Clean Air Delivery Rate per Watt |  |  |  | Varies | CADR/W | Used in various energy efficiency metrics related to air cleaners
PM2.5 |  |  | A particulate matter with an aerodynamic diameter less than or equal to a nominal 2.5 micrometers. |  |  |  | Varies | µm | Definition from ENERGY STAR Product Specification for Room Air Cleaners V3.0
PM2.5 CADR |  |  | The combination of CADR of cigarette smoke particle sizes ranging from 0.1 and 0.5 microns with the CADR of dust particles that fall in the range of 0.5 to 2.5 microns and performing a geometric average calculation |  |  |  | Varies | CFM | Definition from ENERGY STAR Product Specification for Room Air Cleaners V3.0
EUL |  |  | Effective useful life of measure |  |  |  | 9 | yrs | DOE, Energy Conservation Standards for Air Cleaners, EERE-2021-BT-STD-0035
SAVINGS - ENERGY STAR V2.0, effective before December 31, 2025
Table 1: Federal Baseline Efficiency (PM2.5 CADR/W) Requirement
| Product Capacity |  |  | ηb (PM2.5 CADR/W)1, 2
| 10 ≤ PM2.5 CADR < 100 |  |  | 1.7
| 100 ≤ PM2.5 CADR < 150 |  |  | 1.9
| PM2.5 CADR ≥ 150 |  |  | 2
1. Code of Federal Regulations at 10 CFR 430.32(ee) 2. Minimum values valid for units manufactured on or after December 31, 2023, and before December 31, 2025
Table 2: Partial On Mode Standby Power
| Product Capacity |  |  | % Wi-Fi connected1 |  | Pnet_connected Wtd Avg (W) | Baseline Pstdby_b (W) | Efficient Pstdby_e (W)1
| 30 ≤ CADR < 100 |  |  | 20.8% |  | 0.208 | 1.208 | 0.4791
| 100 ≤ CADR < 150 |  |  | 23.19% |  | 0.23188 | 1.2319 | 0.5313
| CADR ≥ 150 |  |  | 28.3% |  | 0.28297 | 1.283 | 0.61018
| Weighted Average | [5 empty] | 1.2556 | 0.56444
1. Values based on ENERGY STAR products available as of May 16, 2025. See "ES-air-cleaners_5-16-25" sheet in ICF's 2025 Analysis File named "PY25 TRM - Residential Air Purifier - Analysis File."
Table 3: ENERGY STAR V2.0 Smoke-Free CADR/W Values & Savings
| Product Capacity |  |  | Average Capacity (CADR)1 | Hawaii Rebate Product %1 |  | ηe (Smoke-Free CADR/W)1 | Savings
[8 empty] | kW |  | kWh
| 30 ≤ CADR < 100 |  |  | 83.625 | 22.86% |  | 2.475 | 0.013447 |  | 92.0837
| 100 ≤ CADR < 150 |  |  | 120.7 | 20% |  | 3.2714 | 0.023249 |  | 157.5714
| 150 ≤ CADR < 250 |  |  | 199.6 | 28.57% |  | 4.235 | 0.04598 |  | 309.5512
| CADR ≥ 250 |  |  | 358.82 | 28.57% |  | 4.89 | 0.092566 |  | 621.1895
| Weighted Average |  |  | 202.8029 |  |  |  | 0.047308 |  | 318.4879
1. Values based on rebates provided by Hawai'i Energy during PY23. See "HI_Air Purifier_rebates" sheet in ICF's 2025 Analysis File named "PY25 TRM - Residential Air Purifier - Analysis File."
Note: Sunset date for ENERGY STAR V2.0 savings is December 30, 2025, when federal code changes
Measure Name |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Room Air Purifier, ENERGY STAR V2.0 |  |  |  | 0.047 |  |  | 318.49 |  |  | 2866.41
SAVINGS - ENERGY STAR V3.0, effective on and after December 31, 2025
Table 4: Federal Baseline Efficiency (PM2.5 CADR/W) Requirement
| Product Capacity |  |  | IEFb (PM2.5 CADR/W)1, 2
| 10 ≤ PM2.5 CADR < 100 |  |  | 1.9
| 100 ≤ PM2.5 CADR < 150 |  |  | 2.4
| PM2.5 CADR ≥ 150 |  |  | 2.9
1. See Code of Federal Regulations at 10 CFR 430.32(ee) 2. Minimum values valid for units manufactured on or after December 31, 2025
Table 5: Minimum ENERGY STAR V3.0 Efficiency (PM2.5 CADR/W) Requirement & Savings
| Product Capacity |  |  | Average Capacity (CADR)1 | Hawaii Rebate Product %1 |  | IEFe (PM2.5 CADR/W)2 | Savings
[8 empty] | kW |  | kWh
| 30 ≤ PM2.5 CADR < 100 |  |  | 83.625 | 22.86% |  | 4.4 | 0.021832 |  | 146.0437
| 100 ≤ PM2.5 CADR < 150 |  |  | 120.7 | 20% |  | 5.4 | 0.024391 |  | 163.1685
| 150 ≤ PM2.5 CADR < 250 |  |  | 199.6 | 28.57% |  | 5.6 | 0.02897 |  | 193.7988
| PM2.5 CADR ≥ 250 |  |  | 358.82 | 28.57% |  | 5.6 | 0.05208 |  | 348.3912
| Weighted Average |  |  | 202.8029 |  |  |  | 0.033025 |  | 220.9266
1. Values based on rebates provided by Hawai'i Energy during PY23. See "HI_Air Purifier_rebates" sheet in ICF's 2025 Analysis File named "PY25 TRM - Residential Air Purifier - Analysis File." 2. See ENERGY STAR Product Specification for Room Air Cleaners V3.0
Note: Effective date for ENERGY STAR V3.0 savings is December 31, 2025
Measure Name |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Room Air Purifier, ENERGY STAR V3.0 |  |  |  | 0.033 |  |  | 220.93 |  |  | 1988.37
RESOURCES
• | ICF's 2025 Analysis File named "PY25 TRM - Residential Air Purifier - Analysis File."
• | AEG's 2019 Analysis File titled "New Residential Measures Summary - AEG Analysis file."
• | Code of Federal Regulations, Title 10, Part 430, Subpart C. Available here: https://www.ecfr.gov/current/title-10/part-430/section-430.32#p-430.32(ee)
• | ENERGY STAR, Air Cleaners (Purifiers), webpage: https://www.energystar.gov/products/air_cleaners
• | ENERGY STAR, Air Cleaners (Purifiers), Qualified Product List (QPL), accessed 5/16/25. Available here: https://www.energystar.gov/productfinder/download/certified-room-air-cleaners/
• | ENERGY STAR Appliance Calculator. Available here: https://dnr.mo.gov/sites/dnr/files/media/file/2021/01/energy-star-appliance-calculator.xlsx
• | ENERGY STAR Product Specification for Room Air Cleaners, Version 2.0, Rev. May-2022, May 2022. Available here: https://www.energystar.gov/sites/default/files/2024-08/ENERGY%20STAR%20Version%202.0%20Room%20Air%20Cleaners%20Specification%20Rev.%20May%202022.pdf
• | ENERGY STAR Product Specification for Room Air Cleaners, Version 3.0. Available here: https://www.energystar.gov/sites/default/files/2025-01/ENERGY%20STAR%20Version%203.0%20Room%20Air%20Cleaners%20Final%20Specification%20with%20Partner%20Commitments.pdf
• | Energy Conservation Program: Energy Conservation Standards for Air cleaners, Department of Energy, 10 CFR Parts 429 and 430, EERE-2021-BT-STD-0035, RIN 1904-AF46 . Available here: https://www.energy.gov/sites/default/files/2023-03/air-cleaners-ecs-dfr.pdf
∆𝑘𝑊=𝐶𝐴𝑃/1000∗(1/𝜂_𝑏 −1/𝜂_𝑒 )∗𝐶𝐹
∆𝑘𝑊ℎ=𝐶𝐴𝑃/1000∗[(1/𝜂_𝑏 −1/𝜂_𝑒 )+(8760−𝐻𝑅𝑆)∗(𝑃_(𝑠𝑡𝑑𝑏𝑦_𝑏)−𝑃_(𝑠𝑡𝑑𝑏𝑦_𝑒) )]∗𝐻𝑅𝑆
∆〖𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=Δ𝑘𝑊ℎ∗𝐸𝑈𝐿
𝑃_(𝑠𝑡𝑑𝑏𝑦_𝑏)=𝑃_(𝑏𝑎𝑠𝑒_𝑎𝑙𝑙𝑜𝑤𝑎𝑛𝑐𝑒)+𝑃_(𝑛𝑒𝑡_𝑐𝑜𝑛𝑛𝑒𝑐𝑡𝑒𝑑)∗%_𝑤𝑖𝑓𝑖
∆𝑘𝑊=𝐶𝐴𝑃/1000∗(1/〖𝐼𝐸𝐹〗_𝑏 −1/〖𝐼𝐸𝐹〗_𝑒 )∗𝐶𝐹
∆𝑘𝑊ℎ=𝐶𝐴𝑃/1000∗(1/〖𝐼𝐸𝐹〗_𝑏 −1/〖𝐼𝐸𝐹〗_𝑒 )∗𝐻𝑅𝑆
∆〖𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=Δ𝑘𝑊ℎ∗𝐸𝑈𝐿

## R_Appliance_Cooktop
RESIDENTIAL: Cooktop
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. This update creates a new residential cooktop measure that combines a revised version of the TRM's previous induction cooktop measure with a new non-induction cooktop measure.
MEASURE DETAILS
Description
Replacement of a non-ENERGY STAR electric cooktop with an ENERGY STAR-certified cooktop in an existing home, or installation of an ENERGY STAR-certified electric cooktop in a newly constructed home.
Program Criteria
| • | This measure is valid for replace on burnout (ROB) retrofit and new construction projects.
| • | Newly installed cooktop must be ENERGY STAR-certified to qualify.
| • | High efficiency equipment must be a standalone cooktop or an electric range with a cooktop. A range combines an oven and cooktop. However, only the energy used by the cooktop itself is included in energy savings calculations.
| • | The cooktop must include four or five burner units.
| • | Used or rebuilt equipment is not eligible.
Unit of Measure
One cooktop.
Baseline Equipment
The baseline equipment is a standard efficiency electric resistance cooktop, either a standalone unit or part of a range.
High Efficiency Equipment
The high efficiency equipment is an ENERGY STAR-certified cooktop, either a standalone unit or a part of a range.
| • | The standalone cooktop or cooktop component of an electric range must meet the ENERGY STAR Version 1.0 specification, with an integrated annual energy consumption (IAEC) that does not exceed 195 kWh/yr.
ALGORITHMS
Baseline Annual Energy Use, kWh/yr
(1)
High Efficiency Annual Energy Use, kWh/yr
[13 empty] | if known | [6 empty] | (2)
[13 empty] | if unknown | [6 empty] | (2a)
Annual Energy Savings, kWh/yr
(3)
Peak Demand Reduction, kW
(4)
Lifetime Energy Savings, kWh
(5)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [10 empty] | Value |  | Unit | Source/Notes
kWhbase |  |  |  | Annual energy use of electric resistance cooktop | [10 empty] | 230 |  | kWh | Calculated with Equation 1
IAECESmax |  |  |  | Max Integrated Annual Energy Consumption allowed by ENERGY STAR | [10 empty] | 195 |  | kWh/yr | ENERGY STAR Electric Cooking IAEC requirements1
IAEC% |  |  |  | ENERGY STAR cooktop component reduction in IEAC relative to non-ENERGY STAR electric resistance cooktop | [10 empty] | 17.7% |  | - | California Technical Forum, SWAP015-04, Efficient Electric Cooking Appliances, Residential, ENERGY STAR Improved Efficiency Assumptions table 2
IAECESactual |  |  |  | Integrated Annual Energy Consumption of ENERGY STAR cooktop. It is the sum of the conventional electric cooking top annual active mode energy consumption and the annual combined low-power mode energy consumption of a conventional electric cooking top or any conventional electric cooking top component of a combined electric cooking product. | [10 empty] | Actual |  | kWh/yr | ENERGY STAR Electric Cooking Qualified Products List 3
IAECESaverage |  |  |  | Average Integrated Annual Energy Consumption for ENERGY STAR-certified non-induction cooktop products (4 or 5 burners); this is used in deemed savings | [10 empty] | 195 |  | kWh/yr | Analysis of ENERGY STAR Electric Cooking Qualified Products List,3 accessed April 1, 2026
|  |  |  | Average Integrated Annual Energy Consumption for ENERGY STAR-certified induction cooktop products (4 or 5 burners); this is used in deemed savings | [10 empty] | 191.24 |  | kWh/yr
EFLH | HOURS | HOURS | HOURS | Equivalent full load hours, defined here as the sum of the 8760 hourly loads (kWh) from an average single family cooking load shape divided by the maximum hourly load (kW) from the same load shape | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | 2588 |  | hrs | Results of cooking load shape analysis.4
CF | CF | CF | CF | Peak demand coincidence factor, defined here as the average hourly load (kW) for cooking during the average weekday peak period divided by the maximum hourly load (kW) for cooking during the year. The CF is calculated using the same load shape used for the EFLH calculation. | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0.6 |  | - | Results of cooking load shape analysis using Hawaii's peak demand period of non-holiday weekdays, from 5 to 9 pm.4
EULee | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 16 |  | yrs | US DOE Energy Conservation Standards for Residential Conventional Cooking Products5
1 ENERGY STAR. 2023. "ENERGY STAR® Program Requirements Product Specification for Residential Electric Cooking Products - Eligibility Criteria Version 1.0." Effective September 25, 2023. <https://www.energystar.gov/sites/default/files/2024-08/ENERGY%20STAR%20Residential%20Electric%20Cooking%20Products%20V1.0%20Final%20Specification%20Rev.%20October%20-%202023.pdf>
2 California Technical Forum, SWAP015-04, Induction Cooking with or without Electric Range, CPUC Approved October 11, 2024. <https://www.caetrm.com/measure/SWAP015/04/>.
3 ENERGY STAR Electric Cooking Qualified Products List <https://www.energystar.gov/productfinder/product/certified-residential-electric-cooking-products/results>
4 AEG's analysis of an average cooking load shape for a single family house using the Hawaii peak demand period of non-holiday weekdays, from 5 to 9 pm: "Load_shape_by_segment_110519_Cooking 09192023.xlsx." The source of the cooking load shape data is the California Energy Commission. The load shape was compiled along with other load shapes during the 2020 Market Potential Study for Hawaii. The cooking load shape analysis provides EFLH=2588 hours and CF=0.60. See "SF_Cooking" tab in AEG's 2023 Analysis File titled "Mid-year PY23 TRM - Residential Induction Cooktop - Analysis File." This analysis assumes the cooking load shape is a reasonable proxy for the cooktop savings shape. Note: The EFLH value is not intended to represent the operating hours of a single cooktop. This EFLH value must be paired with the CF value to yield meaningful peak demand savings.
5 U.S. Department of Energy (DOE), Energy Efficiency and Renewable Energy Office (EERE). 2016. 2016 SNOPR Analytical Tools: Life-Cycle Cost and Payback Period Analysis Spreadsheet. "Cooking_Pds_LCC_SNOPR_DOE_2016_publication.xlsm." Docket EERE-2014-BT-STD-0005. <https://www.caetrm.com/media/reference-documents/Cooking_Pds_LCC_SNOPR_DOE_2016_publication.xlsm>
SAVINGS
Deemed Savings (based on default values for key parameters)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings |  |  | Lifetime Energy Savings
Residential Non-Induction Cooktop | [7 empty] | 0.008 | [7 empty] | 35 |  |  | 560
Residential Induction Cooktop | [7 empty] | 0.009 | [7 empty] | 38.76 |  |  | 620.16
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Enter the actual Annual Energy Consumption (kWh/year) of the ENERGY STAR cooktop. This value can be obtained from the ENERGY STAR qualified products list or manufacturer specifications.
|  | IAECESactual |  |  |  | 195
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings |  |  | Lifetime Energy Savings
Residential Cooktop | [7 empty] | 0.008 | [7 empty] | 35 |  |  | 560
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Cooktops - Analysis File."
• | AEG's 2023 Analysis File titled "Mid-year PY23 TRM - Residential Induction Cooktop - Analysis File."
• | AEG's Load Shape Analysis File titled "Load_shape_by_segment_110519_Cooking 09192023."
• | California Technical Forum, SWAP015-04, Induction Cooking with or without Electric Range, CPUC Approved October 11, 2024. <https://www.caetrm.com/measure/SWAP015/04/>.
• | 2021-2022 ENERGY STAR® Emerging Technology Award Winning Residential Induction Cooking Top Models. <https://www.energystar.gov/sites/default/files/asset/document/2021%202022%20ETA%20QPL%20Residential%20Induction%20Cooking%20Tops%206.23.2022.xlsx>.
• | ENERGY STAR. 2023. "ENERGY STAR® Program Requirements Product Specification for Residential Electric Cooking Products - Eligibility Criteria Version 1.0." Effective September 25, 2023. <https://www.energystar.gov/sites/default/files/2024-08/ENERGY%20STAR%20Residential%20Electric%20Cooking%20Products%20V1.0%20Final%20Specification%20Rev.%20October%20-%202023.pdf>.
• | ENERGY STAR Electric Cooking Qualified Products List, accessed 4/1/2026. <https://www.energystar.gov/productfinder/product/certified-residential-electric-cooking-products/results>.
• | U.S. Energy Information Administration (EIA). 2023. Updated Buildings Sector Appliance and Equipment Costs and Efficiencies. “Appendix A: EIA – Technology Forecast Updates – Residential and Commercial Building Technologies – Reference Case.” Prepared by Guidehouse and Leidos. March. <https://www.caetrm.com/media/reference-documents/EIA_Updated_Buidlings_Sector_Appliance_and_Equipment_Costs_and_Efficiencies.pdf>.
• | U.S. Department of Energy (DOE), Energy Efficiency and Renewable Energy Office (EERE). 2016. 2016 SNOPR Analytical Tools: Life-Cycle Cost and Payback Period Analysis Spreadsheet. "Cooking_Pds_LCC_SNOPR_DOE_2016_publication.xlsm." Docket EERE-2014-BT-STD-0005. <https://www.caetrm.com/media/reference-documents/Cooking_Pds_LCC_SNOPR_DOE_2016_publication.xlsm>.
∆𝑘𝑊=∆𝑘𝑊ℎ/𝐸𝐹𝐿𝐻∗𝐶𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝑒𝑒
)
〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒=〖𝐼𝐴𝐸𝐶〗_𝐸𝑆𝑚𝑎𝑥∗(1+𝐼𝐴𝐸𝐶%)
〖𝑘𝑊ℎ〗_𝑒𝑒=〖𝐼𝐴𝐸𝐶〗_𝐸𝑆𝑎𝑐𝑡𝑢𝑎𝑙
=〖𝐼𝐴𝐸𝐶〗_𝐸𝑆𝑎𝑣𝑒𝑟𝑎𝑔𝑒
∆𝑘𝑊ℎ=(〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊ℎ〗_𝑒𝑒 )

## R_BEnvelope_Cool Wall
RESIDENTIAL: Cool Wall
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM to refer to the current Hawaii State Energy Code.
MEASURE DETAILS
Description
Solar reflective "cool walls" save energy by increasing the solar reflectance (also known as albedo) of exterior above-grade wall surfaces over conventional walls. Solar reflectance (albedo) is defined as the fraction of incident solar radiation that is reflected by a surface. Increasing solar reflectance (alone or in combination with increasing thermal emittance) decreases the amount of solar radiation absorbed by the walls, which in turn reduces air conditioning and HVAC fan loads. Though cool walls also increase space heating loads by reducing the amount of solar radiation absorbed by walls, space heating energy use is assumed to be negligible in the average Hawaii home. (The 2019 Hawaii Statewide Baseline Energy Use Study found that 93% of Hawaii homes do not have space heating.)
The savings for this measure are based on results from a solar reflective cool wall study conducted by Lawrence Berkeley National Laboratory (LBNL) for the California Energy Commission (CEC). As part of the study, LBNL/CEC developed building energy simulation models for various locations and ASHRAE climate zones. The savings included here are derived from simulations for Miami, FL, which has the same ASHRAE climate zone as Hawaii: USCZ 1A.
Program Criteria
| 1. | New construction.
| 2. | Single family home.
| 3. | Home has room or central AC system(s).
| 4. | Because the Hawaii State Energy Code Amendments to the 2018 International Energy Conservation Code (IECC) has options to use reflective walls (among other measures) as a means to eliminate continuous insulation in above-grade walls, the cool wall measure only qualifies for a program incentive if it is being implemented to exceed minimum efficiency requirements from other code compliancy measures.
| 5. | The color and type of the cool wall paint or spectrally selective pigments and materials should be documented.
Unit of Measure
Per home, where the net exterior surface area (ft2) of the above-grade solar reflective walls is a custom entry.
Baseline Equipment
Conventional walls with assumed solar reflectance (albedo) of 0.25. This level of solar reflectance is associated with darker, less reflective coatings and materials. The solar reflectance value of 0.25 is the baseline value used in the LBNL/CEC building energy simulations.
High Efficiency Equipment
"Cool walls" with a minimum initial solar reflectance (albedo) of 0.60. This level of solar reflectance is associated with light-colored conventional paints and materials (e.g., dull white or off-white at a minimum, or bright white for a higher solar reflectance) or non-white spectrally selective pigments and materials with solar reflectance ≥ 0.6. The wall surfaces are assumed to weather and soil over time, reducing the solar reflectance from an initial value of 0.60 to an aged value of 0.58 after the first year. The solar reflectance value of 0.60 is the high efficiency value used in the LBNL/CEC building energy simulations.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  |  | Value |  |  |  |  | Unit |  | Source/Notes
ΔWHVAC |  |  | Annual HVAC site peak power demand absolute savings intensity |  |  |  | See Table 1 |  |  |  |  | W/ft2 |  | LBNL/CEC simulations for USCZ 1A, Vintage group = new, Building category = single-family home, Modified surface = N E S W, Base wall albedo = 0.25, and Albedo of modified wall(s) = 0.6. 1
ΔkWhcool |  |  | Annual cooling site energy absolute savings intensity |  |  |  | See Table 1 |  |  |  |  | kWh/ft2
ΔkWhfan |  |  | Annual fan site energy absolute savings intensity |  |  |  | See Table 1 |  |  |  |  | kWh/ft2
NSA |  |  | Net surface area |  |  |  | User entry |  |  |  |  | ft2 |  | Gross area of above-grade exterior walls (height x width for each above-grade exterior cool wall of home) minus openings for doors and windows.
SAF |  |  | Solar availability factor |  |  |  | See Table 2 |  |  |  |  | - |  | This factor scales the incident solar radiation by accounting for shading and reflection effects from neighboring buildings. Estimates in Table 2 are derived from LBNL/CEC, Appendix P, Table 31 for USCZ 1A. 1
CF |  |  | Coincidence factor |  |  |  | Room AC |  |  | 0.36 |  | - |  | CF corresponding with system peak of 5-9pm on non-holiday weekdays. Determined based on Hawaii-specific EnergyPlus prototype simulations with Room AC and Central AC systems.
[7 empty] | Central AC |  |  | 0.27
PF |  |  | Persistence factor |  |  |  | 0.97 |  |  |  |  | - |  | Adjustment to account for change of solar reflectance over lifetime due to natural exposure (i.e., weather and soiling). Assumes solar reflectance loss of 0.02 once aged; (0.02/0.60) = 3%. 2
EULEE |  |  | Effective useful life of measure |  |  |  | 10 |  |  |  |  | yrs |  | Assumes the coat of paint will last 10 years per LBNL/CEC, Appendix P, pg. P-39. 1
1 [LBNL/CEC]. Levinson et al. 2019. Solar-Reflective “Cool” Walls: Benefits, Technologies, and Implementation. California Energy Commission. Publication Number: CEC-500-2019-040, <https://ww2.energy.ca.gov/2019publications/CEC-500-2019-040/>. See also Appendix P: Cool Wall Application Guidelines, <https://ww2.energy.ca.gov/2019publications/CEC-500-2019-040/CEC-500-2019-040-APP.pdf>. The tool named "Savings explorer v033.xlsm" and database named "Cool surface savings database_2018-06-27.csv" are available in a ZIP archive online: <http://bit.ly/2Kwvtpu>.
2 Estimated using field data for cool wall coatings after 12 months of exposure in Miami, FL. See LBNL/CEC, Appendix P, Figure 8. For an initial albedo of ~0.60, the albedo loss is ~0.02.
Table 1: Unadjusted Savings per Unit of Net Surface Area
Building orientation (long axis of home) |  |  |  |  | Annual cooling site energy absolute savings intensity, ΔkWhcool [kWh/ft2] |  |  |  | Annual fan site energy absolute savings intensity, ΔkWhfan [kWh/ft2] | [5 empty] | Annual HVAC site peak power demand absolute savings intensity, ΔWHVAC [W/ft2]
East-West |  |  |  |  | 0.28679 |  |  |  | 0.072186 | [5 empty] | 0.080361
North-South |  |  |  |  | 0.29803 |  |  |  | 0.07553 | [5 empty] | 0.084821
Mean |  |  |  |  | 0.29246 |  |  |  | 0.073951 | [5 empty] | 0.082591
Source: [LBNL/CEC]. Levinson et al. 2019. "Savings explorer v033.xlsm" and database named "Cool surface savings database_2018-06-27.csv." Simulations for USCZ 1A, Vintage group = new, Building category = single-family home, Modified surface = N E S W, Base wall albedo = 0.25, and Albedo of modified wall(s) = 0.6. The LBNL/CEC values were converted from per-unit of m2 to per-unit of ft2 using the following conversion factor: 1 m2 = 10.7639 ft2.
Table 2: Solar Availability Factor, SAF
Neighbor Building Proximity | [5 empty] | SAF |  | Assumption
Isolated | [5 empty] | 1 |  | Adjacent buildings are more than 100 ft apart. There is negligible effect from neighboring buildings.
Close | [5 empty] | 0.61 |  | Adjacent buildings are within 10 ft of each other. *
Average | [5 empty] | 0.81 |  | Adjacent buildings are between 10 and 100 ft apart.
* The SAF for "Close" proximity was calculated by averaging the mean SAF values for R=0.2, R=1, R=2, and R=2 from LBNL/CEC Appendix P, Table 31, USCZ 1A. R is the canyon aspect ratio and is equal to the cool wall height divided by the distance to the neighboring building. There are four R values to represent four sides of the home.
SAVINGS
Semi-Prescriptive Savings Calculator (based on customer-specific data)
Enter Net Surface Area for Cool Walls, ft2
Net surface area = Gross area of above-grade exterior walls (height x width for each above-grade exterior cool wall of home) minus openings for doors and windows. Use units of ft2.
1000
Select Home Orientation
The long axis of home is mainly in this direction… (where the “Mean” option is the average of east-west and north-south and should be used for homes that have the long axis in between the east-west and north-south orientations).
East-West
Select Neighbor Building Proximity
The "isolated" option assumes adjacent buildings are more than 100 ft apart. The "close" proximity option assumes adjacent buildings are within 10 ft of each other. The "average" proximity option should be selected when adjacent buildings are between 10 and 100 ft apart.
|  |  |  | Close | [6 empty] | Solar Availability Factor, SAF |  | 0.61
Select AC Type
|  |  |  | Central AC | [6 empty] | Coincidence Factor, CF |  | 0.27
Measure Name |  |  |  |  | Peak Demand Savings |  |  |  | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Residential Cool Wall |  |  |  |  | 0.013 |  |  |  | 218.98 | [5 empty] | 2124.11
Note: Savings shown in blue result from sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's PY26 analysis file named "PY26 TRM - Res Cool Wall and Chiller IECC Edits - Analysis File".
• | AEG's PY21 analysis file named "AEG HPUC PY21 TRM - Res Cool Walls - Analysis File." In addition, the file named "AEG HPUC Update - Ductless Systems - Analysis file," worksheet tab named "Res_HVAC Key Parameters," includes Hawaii-specific simulation results for determining CF for Room AC and Window AC systems.
• | State Building Council, Hawai‘i State Energy Code Amendments to the 2018 International Energy Conservation Code. Effective Date: December 15, 2020. Refer to Paragraph 9 (Above-Grade Walls), Paragraph 21 (Insulation and Fenestration Requirements by Components), and Paragraph 27 (Points Option).
• | Levinson, Ronnen, Haley Gilbert, Jiachen Zhang, George Ban-Weiss, Jan Kleissl, Matteo Pizzicotti, Weilong Zhang, Nathalie Dumas, Benjamin Kurtz, Yan Long, Negin Nazarian, Arash Mohegh, Yun Li, Xiaochen Tang, Sharon Chen, Marion Russell, Sébastien Houzé de l’Aulnoit, Paul Berdahl, Pablo Rosado, Jonathan Slack, Howdy Goudey, and Hugo Destaillats. 2019. Solar-Reflective “Cool” Walls: Benefits, Technologies, and Implementation. California Energy Commission. Publication Number: CEC-500-2019-040, <https://ww2.energy.ca.gov/2019publications/CEC-500-2019-040/>. See also Appendix P: Cool Wall Application Guidelines, <https://ww2.energy.ca.gov/2019publications/CEC-500-2019-040/CEC-500-2019-040-APP.pdf>. The tool named "Savings explorer v033.xlsm" and database named "Cool surface savings database_2018-06-27.csv" are available in a ZIP archive online: <http://bit.ly/2Kwvtpu>.
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
∆𝑘𝑊=(∆𝑊_𝐻𝑉𝐴𝐶∗𝑁𝑆𝐴∗𝑆𝐴𝐹∗𝐶𝐹)/(1000 𝑊/𝑘𝑊)
∆𝑘𝑊ℎ=(∆𝑘〖𝑊ℎ〗_𝐶𝑜𝑜𝑙+∆𝑘〖𝑊ℎ〗_𝐹𝑎𝑛 )∗𝑁𝑆𝐴∗𝑆𝐴𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝑃𝐹∗〖𝐸𝑈𝐿〗_𝐸𝐸

## R_Electronics_Television
RESIDENTIAL: Television
Return to TOC
UPDATE STATUS
Updated in Winter 2020-2021 for PY21 TRM.
MEASURE DETAILS
Description
ENERGY STAR V8.0 televisions. This measure is for a midstream incentive to retailers to stock, promote, and sell televisions that meet or exceed ENERGY STAR V8.0.
Program Criteria
ENERGY STAR V8.0 certified.
Unit of Measure
One Television.
Baseline Equipment
Non-ENERGY STAR V8.0 certified television.
High Efficiency Equipment
ENERGY STAR V8.0 certified television
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
4K Wattage Calculation
(3)
Lifetime Energy Savings, kWh
(4)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit | Source/Notes
On_Mode_ Watts_base |  |  |  | Baseline Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | User Input |  |  |  | W | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. 1 | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”.
On_Mode_ Watts_ee | Watts_ee | Watts_ee | Watts_ee | Energy efficient Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | User Input |  |  |  | W | ENERGY STAR V8.0 Program Requirements. 2 | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements.
Standby_ Mode_Watts_base |  |  |  | Baseline Watts (standby) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | = Baseline connected Watts (active) | User Input |  |  |  | W | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. 1 | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”.
Standby_ Mode_Watts_ee | Watts_ee | Watts_ee | Watts_ee | Energy efficient Watts (standby) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | = Energy efficient connected Watts (active) | User Input |  |  |  | W | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. 1 | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”.
4K Wattage |  |  |  | Wattage Multiplier for 4K TVs | [11 empty] | 1.5 |  |  |  | - | ENERGY STAR V8.0 Program Requirements. 2 ENERGY STAR requirements give a 50% wattage allowance for high resolution TVs. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements. | ENERGY STAR V7.0 Program Requirements.
CF | CF | CF | CF | Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | = Demand Coincidence Factor | 0.55971 | 0.22 | 0.22 | 0.22 | - | Based on usage during Hawaii's peak period. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM. | Based on Efficiency Vermont TRM, 2015 for coincident usage between 5-7PM.
HRS_Active | HOURS_Active | HOURS_Active | HOURS_Active | Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | 5 | 5 | 5 | 5 | hrs | Average hours drawn from ENERGY STAR “Consumer Electronics Calculator”. 1 | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”.
HRS_Standby | HOURS_Active | HOURS_Active | HOURS_Active | Average hours of use per day in Standby Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | = Average hours of use per day in Active Mode | 19 | 5 | 5 | 5 | hrs | Average hours drawn from ENERGY STAR “Consumer Electronics Calculator”. 1 | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”. | Baseline power consumption is drawn from ENERGY STAR “Consumer Electronics Calculator”.
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 6 | 6 years | 6 years | 6 years | yrs | Average of several TRMs and secondary sources.
Notes: |  | 1. "Consumer_Electronics_Calculator Dec 2015_26-Jan-21 18-15-29.xlsx" 2. https://www.energystar.gov/sites/default/files/ Final%20V8.0%20TVs%20Program%20Requirements_0.pdf
|  | Table 1 |  |  |  |  | Standby Wattages (Non 4K)
|  | Size |  |  |  |  | Baseline | [6 empty] | ENERGY STAR v8.0
|  | 20" and under |  |  |  |  | 0.39333 | [6 empty] | 0.31897
|  | 21" - 23" |  |  |  |  | 0.35393 | [6 empty] | 0.32273
|  | 24" - 29" |  |  |  |  | 0.32905 | [6 empty] | 0.3175
|  | 30" - 34" |  |  |  |  | 0.32226 | [6 empty] | 0.30455
|  | 35" - 39" |  |  |  |  | 0.33796 | [6 empty] | 0.3
|  | 40" - 44" |  |  |  |  | 0.33187 | [6 empty] | 0.32083
|  | 45" - 49" |  |  |  |  | 0.30683 | [6 empty] | 0.2987
|  | 50" - 54" |  |  |  |  | 0.29864 | [6 empty] | 0.30926
|  | 55" - 59" |  |  |  |  | 0.29679 | [6 empty] | 0.24915
|  | 60" - 64" |  |  |  |  | 0.30517 | [6 empty] | 0.28
|  | 65" or greater |  |  |  |  | 0.33133 | [6 empty] | 0.24412
Baseline standby and ENERGY STAR standby wattages for Non 4K TV are from the ENERGY STAR Calculator ("Consumer_Electronics_Calculator Dec 2015_26-Jan-21 18-15-29.xlsx"). 4K wattage values are calculated by multiplying these wattages by 1.5 as documented in equation 3.
|  | Table 2 |  |  |  |  | On Mode Wattages (Non 4K)
|  | Size |  |  |  |  | Baseline | [6 empty] | ENERGY STAR v8.0
|  | 20" and under |  |  |  |  | 22.9533 | [6 empty] | 18.1926
|  | 21" - 23" |  |  |  |  | 25.0843 | [6 empty] | 18.8779
|  | 24" - 29" |  |  |  |  | 28.6358 | [6 empty] | 21.1287
|  | 30" - 34" |  |  |  |  | 34.7282 | [6 empty] | 26.4757
|  | 35" - 39" |  |  |  |  | 45.5613 | [6 empty] | 31.7224
|  | 40" - 44" |  |  |  |  | 53.8176 | [6 empty] | 37.5729
|  | 45" - 49" |  |  |  |  | 68.9369 | [6 empty] | 43.869
|  | 50" - 54" |  |  |  |  | 73.9136 | [6 empty] | 50.4072
|  | 55" - 59" |  |  |  |  | 87.3622 | [6 empty] | 56.9505
|  | 60" - 64" |  |  |  |  | 87.6741 | [6 empty] | 63.252
|  | 65" or greater |  |  |  |  | 160.341 | [6 empty] | 69.0846
For the non 4K ENERGY STAR On Mode wattage, AEG first determined screen area with this equation and an assumed aspect ratio of 16:9. Screen Area=(((diagonal length^2)/(16^2+9^2))*(16*9)). Then, AEG determined on mode wattage with this equation: On Mode Power (W) =78.5*TANH(0.0005*(Screen Area-140)+0.038)+14. This equation is from the ENERGY STAR Program requirements V8. <https://www.energystar.gov/sites/default/files/Final%20V8.0%20TVs%20Program%20Requirements_0.pdf>. Equation 3 was utilized to calculate 4K wattages.
|  | Table 3 |  |  |  |  | Annual kWh Savings
|  | Size |  |  |  |  | ENERGY STAR non-4K | [6 empty] | ENERGY STAR 4K
|  | 20" and under |  |  |  |  | 9.2041 | [6 empty] | 13.8061
|  | 21" - 23" |  |  |  |  | 11.543 | [6 empty] | 17.3144
|  | 24" - 29" |  |  |  |  | 13.7806 | [6 empty] | 20.6709
|  | 30" - 34" |  |  |  |  | 15.1837 | [6 empty] | 22.7756
|  | 35" - 39" |  |  |  |  | 25.5192 | [6 empty] | 38.2787
|  | 40" - 44" |  |  |  |  | 29.7231 | [6 empty] | 44.5847
|  | 45" - 49" |  |  |  |  | 45.8053 | [6 empty] | 68.7079
|  | 50" - 54" |  |  |  |  | 42.8255 | [6 empty] | 64.2382
|  | 55" - 59" |  |  |  |  | 55.8317 | [6 empty] | 83.7475
|  | 60" - 64" |  |  |  |  | 44.745 | [6 empty] | 67.1175
|  | 65" or greater |  |  |  |  | 167.1476 | [6 empty] | 250.7215
|  | Table 4 |  |  |  |  | Annual kW Savings
|  | Size |  |  |  |  | ENERGY STAR non-4K | [6 empty] | ENERGY STAR 4K
|  | 20" and under |  |  |  |  | 0.0026646 | [6 empty] | 0.0039969
|  | 21" - 23" |  |  |  |  | 0.0034737 | [6 empty] | 0.0052106
|  | 24" - 29" |  |  |  |  | 0.0042018 | [6 empty] | 0.0063027
|  | 30" - 34" |  |  |  |  | 0.004619 | [6 empty] | 0.0069285
|  | 35" - 39" |  |  |  |  | 0.0077457 | [6 empty] | 0.011619
|  | 40" - 44" |  |  |  |  | 0.0090923 | [6 empty] | 0.013638
|  | 45" - 49" |  |  |  |  | 0.014031 | [6 empty] | 0.021046
|  | 50" - 54" |  |  |  |  | 0.013157 | [6 empty] | 0.019735
|  | 55" - 59" |  |  |  |  | 0.017022 | [6 empty] | 0.025532
|  | 60" - 64" |  |  |  |  | 0.013669 | [6 empty] | 0.020504
|  | 65" or greater |  |  |  |  | 0.051077 | [6 empty] | 0.076615
Table 5. Data from 2019 Hawaii Statewide Baseline Energy Use Study
|  | Size |  |  |  |  | Market Share
|  | 49" and under |  |  |  |  | 67.13%
|  | 50" or greater |  |  |  |  | 32.87%
Source: 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020, Volume 2: Appendices: Questionnaires, Ancillary Research Materials and Crosstabs, page 314.
Table 6. Data Adapted from 2015 EIA Residential Energy Consumption Survey
|  | Size |  |  |  |  | Market Share
|  | 29'' and under |  |  |  |  | 12.05%
|  | 29" - 39" | 32.8 | 0 | 0 | 0 | 26.34%
|  | 40" - 49" | 23 | 0 | 0 | 0 | 25.45%
|  | 50" - 59" | 23 | 0 | 0 | 0 | 25.45%
|  | 60" or greater | 2.4 | 0 | 0 | 0 | 10.71%
Note: AEG mapped the EIA data to different size bins for the Hawaii analysis. See "PY21 R_Electronics_Television Analysis File" for details on the mapping.
Source: U.S. Energy Information Administration, Office of Energy Consumption and Efficiency Statistics, Forms EIA-457A and EIA-457C of the 2015 Residential Energy Consumption Survey, May 2018, Table HC4.6 Electronics in homes by climate region (Hot-Humid), Retrieved February 22, 2021, <https://www.eia.gov/consumption/residential/data/2015/hc/hc4.6.xlsx>.
Table 7. Estimated Shares for Hawaii
|  | Size |  |  |  |  | Market Share
|  | 20" and under |  |  |  |  | 4.225%
|  | 21" - 23" |  |  |  |  | 4.225%
|  | 24" - 29" |  |  |  |  | 4.225%
|  | 30" - 34" |  |  |  |  | 13.85%
|  | 35" - 39" |  |  |  |  | 13.85%
|  | 40" - 44" |  |  |  |  | 13.38%
|  | 45" - 49" |  |  |  |  | 13.38%
|  | 50" - 54" |  |  |  |  | 11.57%
|  | 55" - 59" |  |  |  |  | 11.57%
|  | 60" - 64" |  |  |  |  | 4.87%
|  | 65" or greater |  |  |  |  | 4.87%
Note: Table 7 values approximate the sizes of TVs currently installed in peoples' homes, but do not necessarily reflect current purchasing trends. In general, TV sizes are trending upwards so the deemed savings values presented below are likely to be conservative.
Source: AEG utilized Hawaii Baseline Data and secondary EIA data to fill in the gaps. AEG assumed market share was evenly split when data was not available.
SAVINGS
Deemed Savings (based on weighted average of TVs by size)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Non-4K Television | [7 empty] | 0.012 | [7 empty] | 38.93 | [6 empty] | 233.58
4K Television | [7 empty] | 0.018 | [7 empty] | 58.39 | [6 empty] | 350.34
Semi-Prescriptive Savings Calculator (based on equivalent TV wattage)
| Enter Type |  |  |  | ENERGY STAR non-4K | [10 empty] | Enter Size | 35" - 39"
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
ENERGY STAR non-4K 35" - 39" | [7 empty] | 0.008 | [7 empty] | 25.52 | [6 empty] | 153.12
RESOURCES
• | AEG's 2021 Analysis File titled "PY21 R_Electronics_Television Analysis File."
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020, Volume 2: Appendices: Questionnaires, Ancillary Research Materials and Crosstabs.
• | U.S. Energy Information Administration, Office of Energy Consumption and Efficiency Statistics, Forms EIA-457A and EIA-457C of the 2015 Residential Energy Consumption Survey, May 2018, Table HC4.6 Electronics in homes by climate region (Hot-Humid), Retrieved February 22, 2021, <https://www.eia.gov/consumption/residential/data/2015/hc/hc4.6.xlsx>.
• | ENERGY STAR. (2019, March 1). V8 Program Requirements for Televisions. Retrieved February 22, 2021, from <https://www.energystar.gov/sites/default/files/Final%20V8.0%20TVs%20Program%20Requirements_0.pdf>.
• | Consumer_Electronics_Calculator Dec 2015_26-Jan-21 18-15-29.xlsx.
• | NEEP (2020, March). MARYLAND/MID-ATLANTIC TECHNICAL REFERENCE MANUAL VERSION 10. Retrieved from <https://neep.org/sites/default/files/resources/Maryland-MidAtlantic%20TRMv10.pdf>.
• | ERS. (2017). CMUA SAVINGS ESTIMATION TECHNICAL REFERENCE MANUAL. Retrieved from <https://www.cmua.org/files/CMUA-POU-TRM_2017_FINAL_12-5-2017%20-%20Copy.pdf>.
• | Massachusetts Technical Reference Manual. (n.d.). Retrieved from <https://fileservice.eea.comacloud.net/FileService.Api/file/FileRoom/9234826. 2013.>.
∆𝑘𝑊ℎ=(𝑂𝑛_(𝑀𝑜𝑑𝑒_(𝑊𝑎𝑡𝑡𝑠_𝑏𝑎𝑠𝑒 ) )−𝑂𝑛_(𝑀𝑜𝑑𝑒_(𝑊𝑎𝑡𝑡𝑠_𝑒𝑒 ) ))/1000∗𝐻𝑅𝑆_𝐴𝑐𝑡𝑖𝑣𝑒∗365+(𝑆𝑡𝑎𝑛𝑑𝑏𝑦_(𝑀𝑜𝑑𝑒_(𝑊𝑎𝑡𝑡𝑠_𝑏𝑎𝑠𝑒 ) )−𝑆𝑡𝑎𝑛𝑑𝑏𝑦_(𝑀𝑜𝑑𝑒_(𝑊𝑎𝑡𝑡𝑠_𝑒𝑒 ) ))/1000∗𝐻𝑅𝑆_𝑆𝑡𝑎𝑛𝑑𝑏𝑦∗365
∆𝑘𝑊=((𝑂𝑛_(𝑀𝑜𝑑𝑒_(𝑊𝑎𝑡𝑡𝑠_𝑏𝑎𝑠𝑒 ) )− 𝑂𝑛_(𝑀𝑜𝑑𝑒_(𝑊𝑎𝑡𝑡𝑠_𝑒𝑒 ) ) ))/1000∗𝐶𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
4𝐾 𝑊𝑎𝑡𝑡𝑎𝑔𝑒=(𝑁𝑜𝑛 4𝐾 𝑊𝑎𝑡𝑡𝑎𝑔𝑒∗1.5)

## R_Electronics_Soundbar
RESIDENTIAL: Soundbar
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the PY25 TRM. This measure reached its sunset date at the end of PY25.
MEASURE DETAILS
Description
This measure is for a midstream incentive to retailers to stock, promote, and sell soundbars that meet or exceed ENERGY STAR Version 3.0.
Program Criteria
ENERGY STAR certified
Unit of Measure
One soundbar
Baseline Equipment
Non-ENERGY STAR v3.0 certified soundbar
High Efficiency Equipment
ENERGY STAR v3.0 certified soundbar
This measure has a sunset date of June 30, 2026, which is the end of PY25.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  | Value | Unit | Source/Notes
Watts_bs,active |  |  | Baseline Watts (active) |  | 13.7 | W | ICF analysis of non-ENERGY STAR soundbar-only power measurements from Fraunhofer 2017 report,1 Tables 8-3 and 8-7.
Watts_bs,idle |  |  | Baseline Watts (idle) |  | 7.5 | W
Watt_bs,sleep |  |  | Baseline Watts (sleep) |  | 2.2 | W
Watt_ee,active |  |  | Energy efficient watts (active) |  | 7.2 | W | Analysis of ENERGY STAR Product Finder data for soundbars, accessed Apr. 22, 2025.
Watt_ee,idle |  |  | Energy efficient watts (idle) |  | 4.6 | W
Watt_ee,sleep |  |  | Energy efficient watts (sleep) |  | 1.3 | W
HRS_active |  |  | Hours per year in active mode |  | 1345 | hrs | Fraunhofer 2017 report,1 Table 8-8.
HRS_idle |  |  | Hours per year in idle mode |  | 2025 | hrs
HRS_sleep |  |  | Hours per year in sleep mode |  | 5390 | hrs
CF |  |  | Coincidence factor |  | 0.56 | - | Assumes same CF as Televisions.
PF |  |  | Persistence factor |  | 100% | -
EUL |  |  | Effective useful life of measure |  | 4 | yrs | DEER 2020.
Notes: |  | 1. Fraunhofer USA Center for Sustainable Energy Systems, Energy Consumption of Consumer Electronics in Homes in 2017, Final Report to the Consumer Electronics Association, Dec. 2017, Available here: <https://cdn.cta.tech/cta/media/media/advocacy/pdfs/energy-consumption-of-consumer-electronics-in-u-s-homes-in-2017-(fraunhofer-usa,-commissioned-by-cta,-december-2017).pdf>
2. See ICF analysis file named "PY25 TRM - Residential Soundbar - Analysis File."
SAVINGS (Applicable through June 30, 2026)
Measure Name |  |  |  | Peak Demand Savings | Annual Energy Savings |  |  | Lifetime Energy Savings
Soundbar |  |  |  | 0.004 | 19.47 |  |  | 77.88
RESOURCES
• | ICF's PY25 Analysis File named "PY25 TRM - Residential Soundbar - Analysis file."
• | California Public Utilities Commission, Database of Energy Efficiency Resources, 2020 update, (DEER2020), READI v.2.5.0, Ex Ante Database Support Table Export, EUL_basis, created on 8/24/2018, available here: www.deeresources.com/index.php/homepage. Spreadsheet.
• | ENERGY STAR Product Finder, available here: <https://www.energystar.gov/productfinder/product/certified-audio-video/results>, accessed Apr. 22, 2025.
• | ENERGY STAR Version 3.0 Audio/Visual Specification, available here: <https://www.energystar.gov/sites/default/files/2024-08/Final%20Version%203.0%20AV%20Program%20Requirements%20Rev%20Dec-2014.pdf>.
• | Fraunhofer USA Center for Sustainable Energy Systems, Energy Consumption of Consumer Electronics in Homes in 2017, Final Report to the Consumer Electronics Association, Dec. 2017, Available here: <https://cdn.cta.tech/cta/media/media/advocacy/pdfs/energy-consumption-of-consumer-electronics-in-u-s-homes-in-2017-(fraunhofer-usa,-commissioned-by-cta,-december-2017).pdf>.
∆𝑘𝑊=𝑃𝐹∗[((〖𝑊𝑎𝑡𝑡𝑠〗_(𝑏𝑠,𝑎𝑐𝑡𝑖𝑣𝑒)−〖𝑊𝑎𝑡𝑡𝑠〗_(𝑒𝑒,𝑎𝑐𝑡𝑖𝑣𝑒) ))/1000]∗𝐶𝐹
∆𝑘𝑊ℎ=𝑃𝐹∗[█((〖𝑊𝑎𝑡𝑡𝑠〗_(𝑏𝑠,𝑎𝑐𝑡𝑖𝑣𝑒)−〖𝑊𝑎𝑡𝑡𝑠〗_(𝑒𝑒,𝑎𝑐𝑡𝑖𝑣𝑒) )∗〖𝐻𝑅𝑆〗_𝑎𝑐𝑡𝑖𝑣𝑒+@█((〖𝑊𝑎𝑡𝑡𝑠〗_(𝑏𝑠,𝑖𝑑𝑙𝑒)−〖𝑊𝑎𝑡𝑡𝑠〗_(𝑒𝑒,𝑖𝑑𝑙𝑒) )∗〖𝐻𝑅𝑆〗_𝑖𝑑𝑙𝑒+@(〖𝑊𝑎𝑡𝑡𝑠〗_(𝑏𝑠,𝑠𝑙𝑒𝑒𝑝)−〖𝑊𝑎𝑡𝑡𝑠〗_(𝑒𝑒,𝑠𝑙𝑒𝑒𝑝) )∗〖𝐻𝑅𝑆〗_𝑠𝑙𝑒𝑒𝑝 ))]/1000
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿

## R_HVAC_Window AC
RESIDENTIAL: Window AC
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM.
MEASURE DETAILS
Description
The early removal and recycling of a pre-existing inefficient window air conditioning unit and replacement with a new ENERGY STAR qualifying unit, or the installation of a new ENERGY STAR unit without recycling a previous unit through the program. This measure applies to ENERGY STAR dual inverter driven window AC systems.
Program Criteria
For early replacement with recycling projects, documentation must be provided to show that the pre-existing unit was operating and had a meaningful remaining useful life prior to replacement. The new unit must be ENERGY STAR-certified and must meet or exceed the ENERGY STAR requirements that are in effect during the given program year.
Special note for PY26: For projects involving the installation of a new ENERGY STAR unit without recycling a previous unit through the program, the new unit must be ENERGY STAR-certified and must meet or exceed ENERGY STAR Version 7.0 minimum standards. If ENERGY STAR Version 7.0 is not finalized before PY26 and/or if there are no ENERGY STAR-certified products available that meet the Version 7.0 standards, the portion of the measure allowing purchase and installation of a new ENERGY STAR unit without recycling a previous unit will be on hold until such products become available.
Unit of Measure
One window AC unit.
Baseline Equipment
Equipment is assumed to be a window AC unit without reverse cycle, with louvered sides, and a capacity range of less than 28,000 Btu/h. For window AC units not meeting this type or capacity range, confirm program eligibility with Hawai'i Energy and use a custom approach to calculate impacts.
For early replacement with recycling, a dual baseline is required to estimate impacts. The efficiency during the first baseline period corresponds to federal minimum requirements for units manufactured from June 1, 2014 through May 25, 2026 and the efficiency during the second baseline period corresponds to federal minimum requirements for units manufactured as of May 26, 2026. (See Table 1.)
For addition of new systems without recycling a previous unit, or for replacement on burnout of a pre-existing unit, a single baseline that corresponds to federal minimum requirements for units manufactured as of May 26, 2026 is used. (See Table 1.)
High Efficiency Equipment
High efficiency equipment is a new ENERGY STAR-certified dual inverter window AC unit without reverse cycle, with louvered sides, and with a capacity range of less than 28,000 Btu/h. The efficiency of the unit must meet or exceed the minimum ENERGY STAR requirements that are in effect during the given program year. As of April 2026, Version 5.0 is in effect, and Versions 6.0 and 7.0 are in draft form. Version 6.0 will address the heating mode efficiency for room heat pumps without changing other requirements. Version 7.0 will update all requirements in response to the new federal minimum standards going into effect on May 26, 2026. Version 7.0 will apply to this measure. (See Table 1.)
Table 1: Baseline and ENERGY STAR Specifications
| Capacity Bin (Btu/h) |  |  |  |  | 1st Baseline1 |  |  |  | 2nd Baseline2 | [6 empty] | ENERGY STAR
[6 empty] | CEERBL,1 |  | EERBL,1 |  | CEERBL,2 |  |  |  | EERBL,2 |  |  | Version 5.0 3 CEERMin | Version 7.0 4 (Draft 1) CEERMin
| < 6,000 |  |  |  |  | 11 |  | 11.1 |  | 13.1 |  |  |  | 13.2 |  |  | 13.1 | 14.4
| 6,000 to 7,999 |  |  |  |  | 11 |  | 11.1 |  | 13.7 |  |  |  | 13.8 |  |  | 13.7 | 15.1
| 8,000 to 13,999 |  |  |  |  | 10.9 |  | 11 |  | 16 |  |  |  | 16.2 |  |  | 14.7 | 17.6
| 14,000 to 19,999 |  |  |  |  | 10.7 |  | 10.8 |  | 16 |  |  |  | 16.2 |  |  | 14.4 | 17.6
| 20,000 to 27,999 |  |  |  |  | 9.4 |  | 9.5 |  | 13.8 |  |  |  | 13.9 |  |  | 12.7 | 15.2
1 See federal minimum CEERBL,1 requirements for units manufactured between June 1, 2014 and May 26, 2026 at <https://www.govinfo.gov/content/pkg/CFR-2025-title10-vol3/pdf/CFR-2025-title10-vol3-sec430-32.pdf>, paragraph (b) on page 882. EERBL,1 is assumed to be CEERBL,1 * 1.01.
2 See federal minimum CEERBL,2 requirements for units manufactured as of May 26, 2026 at <https://www.govinfo.gov/content/pkg/CFR-2025-title10-vol3/pdf/CFR-2025-title10-vol3-sec430-32.pdf>, paragraph (b) on page 883. EERBL,2 is assumed to be CEERBL,2 * 1.01.
3 See ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Version 5.0, available here: <https://www.energystar.gov/products/room_air_conditioner_specification_version_5_2>. There are no minimum EER requirements. Note that some of the Version 5.0 CEER values are lower than the federal minimum CEER values effective as of May 26, 2026. This is true for capacities of 8,000 Btu/h and higher.
4 See ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Draft 1, Version 7.0, available here: <https://www.energystar.gov/room_air_conditioner_specification_version_7_0_pd>. There are no minimum EER requirements.
ALGORITHMS
First Baseline Peak Demand Reduction, kW (Early Replacement Only)
(1)
Second Baseline Peak Demand Reduction, kW (or, Single Baseline for Replace on Burnout)
(2)
First Baseline Annual Energy Savings, kWh/yr (Early Replacement Only)
(3)
Second Baseline Annual Energy Savings, kWh/yr (or, Single Baseline for Replace on Burnout)
(4)
Early Replacement Lifetime Energy Savings, kWh
(5)
Replace on Burnout Lifetime Energy Savings, kWh
(6)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [5 empty] | Value |  |  |  | Unit |  | Source/Notes
Capacity | PY15_small | PY15_small | PY15_small | Rated cooling capacity of installed window AC unit | From a review of PY2015 rebates processed, the average size of a small unit | From a review of PY2015 rebates processed, the average size of a small unit | From a review of PY2015 rebates processed, the average size of a small unit | From a review of PY2015 rebates processed, the average size of a small unit | From a review of PY2015 rebates processed, the average size of a small unit | Based on installed unit | 1.28 | 1.28 | 1.28 | Btu/h |  | Assumes rated capacity of < 28,000 Btu/h.1
EERBL,1 | (S)EER_b | (S)EER_b | (S)EER_b | Energy efficiency ratio of baseline unit for first baseline period (early replacement) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Assumed to be CEERBL,1 * 1.01 per ENERGY STAR data.2
EERBL,2 | (S)EER_b | (S)EER_b | (S)EER_b | Energy efficiency ratio of baseline unit for second baseline period (early replacement) or for single baseline (replace on burnout) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Assumed to be CEERBL,2 * 1.01 per ENERGY STAR data.2
EEREE | (S)EER_ee | (S)EER_ee | (S)EER_ee | Energy efficiency ratio of installed high efficiency unit | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | As installed | see table 1 | see table 1 | see table 1 | Btu/Wh |  | If the EEREE value is unknown, it is assumed to be CEEREE * 1.01 per ENERGY STAR data.2
CEERBL,1 | (S)EER_b | (S)EER_b | (S)EER_b | Combined energy efficiency ratio of baseline unit for first baseline period (early replacement) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Federal minimum requirement for units manufactured from June 1, 2014 through May 25, 2026.
CEERBL,2 | (S)EER_b | (S)EER_b | (S)EER_b | Combined energy efficiency ratio of baseline unit for second baseline period (early replacement) or for single baseline (replace on burnout) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Federal minimum requirement for units manufactured as of May 26, 2026.
CEEREE | (S)EER_ee | (S)EER_ee | (S)EER_ee | Combined energy efficiency ratio of installed high efficiency unit | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | As installed | see table 1 | see table 1 | see table 1 | Btu/Wh |  | The new unit for projects that include early replacement and recycling of a pre-existing unit must be ENERGY STAR-certified, with a CEER value that also meets or exceeds the minimum federal standard effective as of May 26, 2026. The new unit for projects that do NOT include early replacement and recycling of a pre-existing unit must meet or exceed minimum ENERGY STAR Version 7.0 CEER standards. Table 1 shows minimum CEER requirements for ENERGY STAR Versions 5.0 (Final) and 7.0 (Draft 1), as well as minimum federal standards.
CF | CF | CF | CF | Coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0.36 | 0.5 | 0.5 | 0.5 | - | Deemed value; 50% VRFs operational between 5-9 pm | CF corresponding with system peak of 5-9pm on non-holiday weekdays. Determined based on EnergyPlus prototype simulations with room AC systems.
EFLH | HOURS | HOURS | HOURS | Equivalent full load cooling hours | equivalent full load cooling hours | equivalent full load cooling hours | equivalent full load cooling hours | equivalent full load cooling hours | equivalent full load cooling hours | 2528 | 1825 | 1825 | 1825 | hrs/yr | Deemed value; 5 hrs per day cooling | EFLH determined as average of residential EnergyPlus prototype simulations with room AC cooling system by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
PF | PF | PF | PF | Persistence factor | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | 1 | 1 | 1 | 1 | -
Constant |  |  |  | Watt/kilowatt conversion | [5 empty] | 1000 |  |  |  | W/kW
RUL |  |  |  | Remaining useful life of measure | [5 empty] | 3 |  |  |  | yrs |  | Assumed to be 1/3 EUL.
EUL |  |  |  | Effective useful life of measure | [5 empty] | 9 |  |  |  | yrs |  | California eTRM.
1 For window AC units outside of this capacity range, use a custom approach to calculate impacts.
2 The Version 3.1 ENERGY STAR specification provided equivalent EER and CEER ratings. For the most popular size band, the EER rating is approximately 1% higher than the CEER. See ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Version 3.1, available here: <https://www.energystar.gov/products/spec/room_air_conditioners_specification_version_3_0_pd>.
SAVINGS
See the accompanying AC worksheet:
R_HVAC_AC_WKST
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Window AC and Residential Central AC Retrofit - Analysis File."
• | ICF's PY25 Analysis File named "PY25 TRM - Residential Window AC - Analysis File."
• | AEG's Analysis file, "AEG HPUC Update—Ductless Systems—Analysis file," and the worksheet tab, "Res_HVAC Key Parameters," include Hawai‘i-specific simulation results for determining Room AC EFLH and CF.
• | California eTRM. CPUC Support Tables. Effective Useful Life and Remaining Useful Life, available here: https://www.caetrm.com/cpuc/table/effusefullife/
• | Code of Federal Regulations, 10 CFR 430.32, Subpart C, Energy and Water Conservation Standards and Their Effective Dates, (b) Room Air Conditioners, pages 882-883, available here: <https://www.govinfo.gov/content/pkg/CFR-2025-title10-vol3/pdf/CFR-2025-title10-vol3-sec430-32.pdf>.
• | ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Version 3.1, available here: <https://www.energystar.gov/products/spec/room_air_conditioners_specification_version_3_0_pd>.
• | ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Version 5.0, available here: <https://www.energystar.gov/products/room_air_conditioner_specification_version_5_2>.
• | ENERGY STAR Program Requirements, Product Specification for Room Air Conditioners, Draft 1, Version 7.0, available here: <https://www.energystar.gov/room_air_conditioner_specification_version_7_0_pd>.
• | Hawai‘i-specific energy simulations of single family home prototypes in BEopt™ with EnergyPlus v8.8 as the simulation engine.
• | 2020 Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 8.0, Volume 3: Residential Measures, FINAL, Oct. 17, 2019, page 37.
• | Oversizing of HVAC System: Signatures and Penalties, University of Idaho, Integrated Design Lab-Boise, available here: <http://www.idlboise.com/pdf/papers/ENB_3018_RTU_Measurement_accepted.pdf>. Used to determine correct HVAC oversizing adjustment for EFLH and CF analysis.
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒, 𝐸𝑅)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(𝐸𝑈𝐿−𝑅𝑈𝐿)
〖∆𝑘𝑊〗_1𝑠𝑡=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅〗_(𝐵𝐿,1)−〗 1∕〖〖𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐶𝐹∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐶𝐸𝐸𝑅〗_(𝐵𝐿,1)−〗 1∕〖〖𝐶𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻∗𝑃𝐹
〖∆𝑘𝑊〗_2𝑛𝑑=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅〗_(𝐵𝐿,2)−〗 1∕〖〖𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐶𝐹∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐶𝐸𝐸𝑅〗_(𝐵𝐿,2)−〗 1∕〖〖𝐶𝐸𝐸𝑅〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒, 𝑅𝑂𝐵)=〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗𝐸𝑈𝐿

## R_HVAC_Ductless
RESIDENTIAL: Ductless Split Systems
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. The SEER and EER values were converted to SEER2 and EER2 values.
MEASURE DETAILS
Description
Ductless split systems are inverter-driven direct expansion AC and heat pump systems that use distributed refrigerant technology for cooling and heating. These systems consist of: an outdoor unit with a single variable speed compressor or multiple staged compressors, indoor evaporator unit(s) with variable speed fans designed for single zone air distribution, and zone temperature controls. Per the Air Conditioning, Heating, and Refrigeration Institute (AHRI), residential ductless split systems can be classified as: - Ductless One-to-One (Single) Split Systems - Space Constrained Ductless-Split Systems - Ductless Multi-Split Systems - Variable Refrigerant Flow (VRF) Ductless Split Systems - Heat Recovery Multi-Split Systems This measure addresses ductless split systems for space cooling.
Program Criteria
SEER2 rating of 15.3 or higher for ≥8,000 Btu/h and <65,000 Btu/h.
Unit of Measure
Savings are calculated per split system unit.
Baseline Equipment
The assumed baseline for capacities < 28 kBtu/h is a louvered, non-reverse cycle room AC unit. The assumed baseline for capacities ≥ 28 kBtu/h is an air-cooled split-system central AC unit. The baseline equipment must meet or exceed current federal and state minimum efficiency standards in effect on the installation date (see Table 1.)
Table 1: Baseline Efficiency Specifications1
| Capacity Bin |  |  |  | Baseline
[5 empty] | CEER or SEER2 |  | EER or EER2
| ≥8,000 Btu/h and <14,000 Btu/h |  |  |  | 10.9 | CEER | 11 |  | EER
| ≥14,000 Btu/h and <20,000 Btu/h |  |  |  | 10.7 | CEER | 10.8 |  | EER
| ≥20,000 Btu/h and <28,000 Btu/h |  |  |  | 9.4 | CEER | 9.5 |  | EER
| ≥28,000 Btu/h and <45,000 Btu/h |  |  |  | 14.3 | SEER2 | 11.7 |  | EER2
| ≥45,000 Btu/h and <65,000 Btu/h |  |  |  | 13.8 | SEER2 | 11.2 |  | EER2
1. For minimum CEER and SEER2 requirements effective as of Jan. 1, 2023, see <https://www.govinfo.gov/content/pkg/CFR-2022-title10-vol3/pdf/CFR-2022-title10-vol3-sec430-32.pdf>. For Hawaii, there is no federal or state minimum EER or EER2 requirement. For Room AC units, EER is assumed to be CEER * 1.01. For Central AC units, AEG's research of the AHRI database (Nov. 7, 2022 extract) showed that 11.7 EE2 is the most common EER2 value for the 14.3 SEER2 minimum requirement and 11.2 EER2 is the most common EER2 value for 13.8 SEER2 minimum requirement.
High Efficiency Equipment
The installed equipment must meet the 15.3 SEER2 minimum requirement and will reflect the actual efficiency of the unit.
ALGORITHMS
Peak Demand Reduction, kW
Capacity < 28 kBtu/h:
(1)
Capacity ≥ 28 kBtu/h:
(2)
Annual Energy Savings, kWh/yr
Capacity < 28 kBtu/h:
(3)
Capacity ≥ 28 kBtu/h:
(4)
Lifetime Energy Savings, kWh
(5)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  |  |  | Value |  | Unit | Source/Notes
Capacity |  |  | Rated capacity, in Btu/h, of installed unit |  |  |  |  | Based on installed unit |  | Btu/h | As installed.
EERBL |  |  | Full load energy efficiency ratio of baseline unit for capacities < 28 kBtu/h |  |  |  |  | See Table 1 |  | Btu/Wh | See footnote 1 under Table 1.
EER2BL |  |  | Full load energy efficiency ratio 2 of baseline unit for capacities ≥ 28 kBtu/h |  |  |  |  | See Table 1 |  | Btu/Wh | See footnote 1 under Table 1.
EER2EE |  |  | Full load energy efficiency ratio 2 of installed high efficiency unit |  |  |  |  | As installed |  | Btu/Wh | There is no minimum EER2EE requirement.
CEERBL |  |  | Combined energy efficiency ratio of baseline unit for capacities < 28 kBtu/h |  |  |  |  | See Table 1 |  | Btu/Wh | See footnote 1 under Table 1.
SEER2BL |  |  | Seasonal energy efficiency ratio 2 of baseline unit for capacities ≥ 28 kBtu/h |  |  |  |  | See Table 1 |  | Btu/Wh | See footnote 1 under Table 1.
SEER2EE |  |  | Seasonal energy efficiency ratio 2 of installed high efficiency unit |  |  |  |  | As installed |  | Btu/Wh | Must meet 15.3 SEER2 minimum.
CF |  |  | Coincidence Factor for < 28 kBtu/h units |  |  |  |  | 0.36 |  | - | CF corresponding with system peak of 5-9pm on non-holiday weekdays. Determined based on EnergyPlus prototype simulations with Room AC systems.
|  |  | Coincidence Factor for ≥ 28 kBtu/h units |  |  |  |  | 0.27 |  | - | CF corresponding with system peak of 5-9pm on non-holiday weekdays. Determined based on EnergyPlus prototype simulations with Central AC systems.
EFLH |  |  | Equivalent full load cooling hours for < 28 kBtu/h units |  |  |  |  | 2528 |  | hrs/yr | EFLH determined as median of residential EnergyPlus prototype simulations with room AC systems by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
|  |  | Equivalent full load cooling hours for ≥ 28 kBtu/h units |  |  |  |  | 1884 |  | hrs/yr | EFLH determined as median of residential EnergyPlus prototype simulations with central AC systems by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
PF |  |  | Persistence Factor |  |  |  |  | 1 |  | -
Constant |  |  | Watt/kilowatt conversion |  |  |  |  | 1000 |  | W/kW
EUL |  |  | Effective useful life of measure |  |  |  |  | 15 |  | yrs | No change from PY18 TRM; EUL was verified during AEG's 2018 benchmarking.
SAVINGS
See the accompanying AC worksheet:
R_HVAC_AC_WKST
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Window AC and Residential Central AC Retrofit - Analysis File."
• | AEG's 2022 Analysis File named "Mid-year PY22 TRM - Residential HVAC - Analysis File."
• | AEG's PY20 file named "AEG HPUC - HVAC Measures - Analysis File_Jan 2021."
• | AEG's PY19 Analysis Files named "AEG HPUC Update - Ductless Systems - Analysis File" and "AEG HPUC Res HVAC Calculator - Analysis File."
• | Air-Conditioning, Heating, & Refrigeration Institute (AHRI), Database of Certified Products, accessed Nov. 7 2022, available here: <https://www.ahridirectory.org/>.
• | Code of Federal Regulations, 10 CFR 430.32, Subpart C, Energy and Water Conservation Standards and Their Effective Dates, (c) Central Air Conditioners and Heat Pumps, available here: <https://www.govinfo.gov/content/pkg/CFR-2022-title10-vol3/pdf/CFR-2022-title10-vol3-sec430-32.pdf>.
• | Hawai‘i-specific energy simulations of single family home prototypes in BEopt™ with EnergyPlus v8.8 as the simulation engine.
• | Oversizing of HVAC System: Signatures and Penalties, University of Idaho, Integrated Design Lab-Boise, available here: <http://www.idlboise.com/pdf/papers/ENB_3018_RTU_Measurement_accepted.pdf>. Used to determine correct HVAC oversizing adjustment for EFLH and CF analysis.
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿
∆𝑘𝑊=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅〗_𝐵𝐿−〗 1∕〖〖𝐸𝐸𝑅2〗_𝐸𝐸)/1000)〗∗𝐶𝐹∗𝑃𝐹
∆𝑘𝑊ℎ=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐶𝐸𝐸𝑅〗_𝐵𝐿−〗 1∕〖〖𝑆𝐸𝐸𝑅2〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻∗𝑃𝐹
∆𝑘𝑊=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅2〗_𝐵𝐿−〗 1∕〖〖𝐸𝐸𝑅2〗_𝐸𝐸)/1000)〗∗𝐶𝐹∗𝑃𝐹
∆𝑘𝑊ℎ=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝑆𝐸𝐸𝑅2〗_𝐵𝐿−〗 1∕〖〖𝑆𝐸𝐸𝑅2〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻∗𝑃𝐹

## R_HVAC_Central AC Retrofit
RESIDENTIAL: Central AC Retrofit
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. The update removes the pre-2006 early replacement baseline option.
MEASURE DETAILS
Description
Early removal of an existing inefficient central air conditioning unit from service, prior to its measure and natural end of life, and replacement with a higher efficiency unit.
Program Criteria
Contact Hawai'i Energy's residential team for more information. For early replacement, the pre-existing unit must be less than 20 years old and documentation must be provided to show that the pre-existing unit was operating and had a meaningful remaining useful life prior to replacement. Examples of acceptable documentation include a signed statement from the homeowner or a video showing the pre-existing unit in operation. In addition, a photo of the nameplate is required, even if it is corroded or otherwise illegible. In cases where the nameplate is missing and/or the age is unknown, both a video of the pre-existing unit in operation and a signed statement from the homeowner verifying that it is operational are required.
Unit of Measure
One central AC unit.
Baseline Equipment
Baseline equipment is assumed to be an air-cooled split-system or single-package central AC unit with a capacity of <65,000 Btu/h. For early replacement, a dual baseline is required to estimate impacts. Federal and state requirements stipulate minimum SEER and SEER2 values that vary depending on the vintage and type of the AC equipment. For Hawaii, there are no federal or state minimum EER or EER2 requirements for AC systems. Instead, we determined proxy baseline values to estimate peak demand impacts for the Hawai'i Energy program. See Table 1 below for a summary of the baseline efficiency metrics. SEER2 and EER2 are currently the preferred efficiency metrics for residential-scale central AC units.
During the first baseline period, pre-existing equipment is assumed to be 13 SEER per the minimum federal requirement in effect between 2006 and 2015.
After the first baseline period ends, the second baseline must meet or exceed the federal and state minimum SEER2 requirement in effect on the installation date (see Table 1).
EER and SEER are legacy cooling efficiency metrics, while EER2 and SEER2 are updated versions using more realistic test conditions introduced by DOE in 2023. EER and EER2 measure peak efficiency at a single hot condition, while SEER and SEER2 measure average efficiency over a cooling season. SEER2 and EER2 ratings are numerically lower but better represent real‑world performance and are now required for federal compliance, ENERGY STAR certification, and utility programs.
Table 1: Baseline Efficiency Specifications*
| System Type | [7 empty] | Early Replacement 1st Baseline |  |  | Early Replacement 2nd Baseline or Replace-on-Burnout Single Baseline (as of Jan. 1, 2023)
[9 empty] | SEER |  | EER | SEER2 |  | EER2
| Split System, <45 kBtu/h | [7 empty] | 13 |  | 10 | 14.3 |  | 11.7
| Split System, ≥45 kBtu/h | [7 empty] | 13 |  | 10 | 13.8 |  | 11.2
| Single-Package | [7 empty] | 13 |  | 10 | 13.4 |  | 10.6
* Refer to Definitions & Assumptions for the sources of these values.
High Efficiency Equipment
The high efficiency equipment is a new split-system or single-package central AC unit (<65,000 Btu/h) with at least 15.2 SEER2.
ALGORITHMS
First Baseline Peak Demand Reduction, kW
(1)
Second Baseline Peak Demand Reduction, kW
(also applies to the replace-on-burnout single baseline approach)
(2)
First Baseline Annual Energy Savings, kWh/yr
(3)
Second Baseline Annual Energy Savings, kWh/yr
(also applies to the replace-on-burnout single baseline approach)
(4)
Early Replacement Lifetime Energy Savings, kWh
(5)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [6 empty] | Value |  | Unit |  | Sources/Notes
Capacity |  |  |  | Rated cooling capacity of installed central AC unit | [6 empty] | Based on installed unit |  | Btu/h |  | As installed (< 65,000 Btu/h).
ConvEER2 |  |  |  | Ratio of EER-to-EER2 | [6 empty] | See Table 2 below |  | - |  | AEG analysis of AHRI extract on Nov. 7, 2022
EERBL,1 |  |  |  | Energy efficiency ratio of baseline unit for first (early replacement) baseline period | [6 empty] | 10 |  | Btu/Wh |  | See Note 1.
EER2BL,2 | (S)EER_b | (S)EER_b | (S)EER_b | Energy efficiency ratio 2 of baseline unit for second baseline period (also used for single baseline for replace-on-burnout projects) | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. | See Table 1 above |  | Btu/Wh |  | See Note 2.
EER2EE |  |  |  | Energy efficiency ratio 2 of installed high efficiency unit | [6 empty] | As installed |  | Btu/Wh |  | There is no minimum EER2EE requirement.
SEERBL,1 |  |  |  | Seasonal energy efficiency ratio of baseline unit for first (early replacement) baseline period | [6 empty] | 13 |  | Btu/Wh |  | See Note 3.
ConvSEER2 |  |  |  | Ratio of SEER-to-SEER2 | [6 empty] | See Table 2 below |  | - |  | AEG analysis of AHRI extract on Nov. 7, 2022
SEER2BL,2 |  |  |  | Seasonal energy efficiency ratio 2 of baseline unit for second baseline period (also used for single baseline for replace-on-burnout projects) | [6 empty] | See Table 1 above |  | Btu/Wh |  | See Note 4.
SEER2EE |  |  |  | Seasonal energy efficiency ratio 2 of installed high efficiency unit | [6 empty] | As installed |  | Btu/Wh |  | Must meet 15.2 SEER2 minimum. See Note 5.
CF |  |  |  | Coincidence factor | [6 empty] | 0.27 |  | - |  | CF corresponding with system peak of 5-9pm on non-holiday weekdays. Determined based on EnergyPlus prototype simulations with Central AC systems.
EFLH |  |  |  | Equivalent full load cooling hours | [6 empty] | 1884 |  | hrs/yr |  | EFLH determined as average of residential EnergyPlus prototype simulations with central AC cooling system by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
PF |  |  |  | Persistence Factor | [6 empty] | 1 |  | -
Constant |  |  |  | Watt/kilowatt conversion | [6 empty] | 1000 |  | W/kW
RUL |  |  |  | Remaining useful life of measure | [6 empty] | 5 |  | yrs |  | Assumed to be 1/3 EUL.
EUL |  |  |  | Effective useful life of measure | [6 empty] | 15 |  | yrs |  | DEER 2020.
1. AEG's research of the AHRI database (Oct 2018 extract) showed that 10.0 EER represents the minimum EER value corresponding to 13 SEER for residential AC systems. (Data filters for AHRI Rating Conditions: Model Type = Systems; Status = Active, Location = USA; Region = All, SEER = 13; Cooling Capacity = 30,000-65,000 Btu/h.)
2. There is no federal or state minimum EER2 requirement for Hawaii. AEG's research of the AHRI database (Nov. 7, 2022 extract) showed that each EER2 value in Table 1 represents the most common EER2 value for the given SEER2 minimum requirement. Refer to AEG's 2022 Analysis File named "Mid-year PY22 TRM - Residential HVAC - Analysis File" for more information.
3. The minimum is 13.0 SEER for split-system central AC and single-package central AC systems manufactured after Jan. 23, 2006 and before Jan. 1, 2015 and installed in Hawai'i. See <https://www.govinfo.gov/content/pkg/CFR-2012-title10-vol3/pdf/CFR-2012-title10-vol3-sec430-32.pdf>, paragraph (2) on page 473.
4. Table 1 shows the minimum SEER2 values for split-system central AC and single-package central AC systems installed in Hawaii on or after Jan. 1, 2023. See <https://www.govinfo.gov/content/pkg/CFR-2022-title10-vol3/pdf/CFR-2022-title10-vol3-sec430-32.pdf>.
5. The 15.2 SEER2 requirement is consistent with ENERGY STAR V6.1 standards for central AC systems.
Table 2: Conversion Factors**
| System Type | [7 empty] | "ConvSEER2" |  |  | "ConvEER2"
[9 empty] | (SEER/SEER2) |  |  | (EER/EER2)
| Split System, <45 kBtu/h | [7 empty] | 1.049 |  |  | 1.043
| Split System, ≥45 kBtu/h | [7 empty] | 1.034 |  |  | 1.034
| Single-Package | [7 empty] | 1.053 |  |  | 1.107
** These values represent the weighted average of the ratios of average SEER-to-SEER2 (and EER-to-EER2) across discrete SEER2 (and EER2) values in the AHRI dataset as of 11/7/2022. Refer to AEG's 2022 Analysis File named "Mid-year PY22 TRM - Residential HVAC - Analysis File" for more information.
SAVINGS
See the accompanying AC worksheet:
R_HVAC_AC_WKST
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Window AC and Residential Central AC Retrofit - Analysis File."
• | AEG's 2022 Analysis File named "Mid-year PY22 TRM - Residential HVAC - Analysis File."
• | AEG's PY20 file named "AEG HPUC - HVAC Measures - Analysis File_Jan 2021."
• | AEG's PY19 Analysis Files named "AEG HPUC Res HVAC Calculator - Analysis File" and "AEG HPUC Mid-Year PY19 TRM Updates_Analysis File." In addition, the file named "AEG HPUC Update - Ductless Systems - Analysis file," worksheet tab named "Res_HVAC Key Parameters," includes Hawai‘i-specific simulation results for determining Central AC EFLH and CF.
• | Air-Conditioning, Heating, & Refrigeration Institute (AHRI), Database of Certified Products, accessed Oct. 2018, Nov. 2020, and Nov. 7, 2022, available here: <http://www.ahrinet.org/Contractors-Specifiers/Certified-Products>.
• | California Public Utilities Commission, Database of Energy Efficiency Resources, 2020 update, (DEER2020), READI v.2.5.0, Ex Ante Database Support Table Export, EUL_basis, created on 8/24/2018, available here: www.deeresources.com/index.php/homepage. Spreadsheet.
• | Code of Federal Regulations, 10 CFR 430.32, Subpart C, Energy and Water Conservation Standards and Their Effective Dates, (c) Central Air Conditioners and Heat Pumps, available here: <https://www.govinfo.gov/content/pkg/CFR-2022-title10-vol3/pdf/CFR-2022-title10-vol3-sec430-32.pdf>.
• | ENERGY STAR Program Requirements, Product Specifications for Central Air Conditioner and Heat Pump Equipment, Eligibility Criteria, Version 6.1, available here: <https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Central%20Air%20Conditioner%20and%20Heat%20Pump%20Version%206.1%20Final%20Specification.pdf>.
• | Hawaii-specific energy simulations of single family home prototypes in BEopt™ with EnergyPlus v8.8 as the simulation engine.
• | Oversizing of HVAC System: Signatures and Penalties, University of Idaho, Integrated Design Lab-Boise, available here: <http://www.idlboise.com/pdf/papers/ENB_3018_RTU_Measurement_accepted.pdf>. Used to determine correct HVAC oversizing adjustment for EFLH and CF analysis.
〖∆𝑘𝑊ℎ〗_(𝑙𝑖𝑓𝑒, 𝐸𝑅)=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(𝐸𝑈𝐿−𝑅𝑈𝐿)
〖∆𝑘𝑊〗_1𝑠𝑡=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖(〖𝐶𝑜𝑛𝑣〗_𝐸𝐸𝑅2∗(1〗∕〖〖𝐸𝐸𝑅〗_(𝐵𝐿,1))−〗 1∕〖〖𝐸𝐸𝑅2〗_𝐸𝐸)/1000)〗∗𝐶𝐹∗𝑃𝐹
〖∆𝑘𝑊〗_2𝑛𝑑=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝐸𝐸𝑅2〗_(𝐵𝐿,2)−〗 1∕〖〖𝐸𝐸𝑅2〗_𝐸𝐸)/1000)〗∗𝐶𝐹∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖(〖𝐶𝑜𝑛𝑣〗_𝑆𝐸𝐸𝑅2∗(1〗∕〖〖𝑆𝐸𝐸𝑅〗_(𝐵𝐿,1))−〗 1∕〖〖𝑆𝐸𝐸𝑅2〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦∗〖((1〗∕〖〖𝑆𝐸𝐸𝑅2〗_(𝐵𝐿,2)−〗 1∕〖〖𝑆𝐸𝐸𝑅2〗_𝐸𝐸)/1000)〗∗𝐸𝐹𝐿𝐻∗𝑃𝐹

## R_HVAC_AC_WKST
RESIDENTIAL: HVAC Savings Calculator
Return to TOC
| Step 1: Enter AC nameplate data |  |  | Step 2: Determine if it qualifies |  |  |  | Step 3: Calculate savings
| Enter AC Type: | Ductless (<28,000 Btu/h) | [5 empty] | CF: | 0.36
| Enter Rated AC Capacity of New Unit (Btu/h): | 14000 |  | SEER2EE,Min or CEEREE,Min | 15.3 | Pass |  | EFLH: | 2528
| Enter Full Load Efficiency with Applicable Metric (EER or EER2): | 15.3 | Enter EER2 for Central and Ductless AC | EER2BL,2 or EERBL,2 | 10.8 |  |  | PF: | 1
| Enter Part-Load Efficiency with Applicable Metric (SEER2 or CEER): | 15.3 | Enter SEER2 for Central and Ductless AC | SEER2BL,2 or CEERBL,2 | 10.7 |  |  | kW reduction: | 0.137
| Note: Enter EER2 and SEER2 for Ductless AC and for Central AC. Enter EER and CEER for Room AC. If a value is unknown, check AHRI Directory (www.ahridirectory.org). If product is not listed, use EER2 = 0.9 * SEER2, EER = 1.01 * CEER, SEER2 = EER2 / 0.9, or CEER = EER / 1.01. |  |  | EERBL,1 |  | Only for early replacement |  | kW reduction (ER): | 0 | Only for early replacement; this is savings during first baseline period
|  |  |  | SEERBL,1 or CEERBL,1 |  | Only for early replacement |  | kWh/yr savings: | 994.46
|  |  |  | ConvSEER2 | 1 |  |  | kWh/yr savings (ER): | 0 | Only for early replacement; this is savings during first baseline period
| Baseline Specifications |  |  | ConvEER2 | 1 |  |  | Lifetime kWh (ROB): | 14916.9
|  | Replace on Burnout (Single Baseline) | [5 empty] | Lifetime kWh (ER): | 0 | Only for early replacement
| Ductless Split System by Capacity Bin | CEERBL or SEER2BL | EERBL or EER2BL
8000 | ≥8,000 Btu/h and <14,000 Btu/h | 10.9 | 11
14000 | ≥14,000 Btu/h and <20,000 Btu/h | 10.7 | 10.8
20000 | ≥20,000 Btu/h and <28,000 Btu/h | 9.4 | 9.5
28000 | ≥28,000 Btu/h and <45,000 Btu/h | 14.3 | 11.7
45000 | ≥45,000 Btu/h and <65,000 Btu/h | 13.8 | 11.2
|  | Replace on Burnout (or, Second Baseline for Early Replacement) |  | Early Replacement (First Baseline)
65000 | Central AC and Room AC | SEER2BL,2 or CEERBL,2 | EER2BL,2 or EERBL,2 | SEERBL,1 or CEERBL,1 | EERBL,1
| Central AC Split-System (<45,000 Btu/h) | 14.3 | 11.7 | 13 | 10
| Central AC Split-System (45,000-64,999 Btu/h) | 13.8 | 11.2 | 13 | 10
| Central AC Single-Package (<65,000 Btu/h) | 13.4 | 10.6 | 13 | 10
| Room AC w/ recycling (< 6,000 Btu/h) | 13.1 | 13.2 | 11 | 11.1
| Room AC w/o recycling (< 6,000 Btu/h) | 13.1 | 13.2
| Room AC w/ recycling (6,000-7,999 Btu/h) | 13.7 | 13.8 | 11 | 11.1
| Room AC w/o recycling (6,000-7,999 Btu/h) | 13.7 | 13.8
| Room AC w/ recycling (8,000-13,999 Btu/h) | 16 | 16.2 | 10.9 | 11
| Room AC w/o recycling (8,000-13,999 Btu/h) | 16 | 16.2
| Room AC w/ recycling (14,000-19,999 Btu/h) | 16 | 16.2 | 10.7 | 10.8
| Room AC w/o recycling (14,000-19,999 Btu/h) | 16 | 16.2
| Room AC w/ recycling (20,000-27,999 Btu/h) | 13.8 | 13.9 | 9.4 | 9.5
| Room AC w/o recycling (20,000-27,999 Btu/h) | 13.8 | 13.9
Minimum EE Qualifications and Parameters Table
| System Type | SEER2EE,Min or CEEREE,Min | EER2EE,Min or EEREE,Min | EFLH | CF | PF | EUL | ConvSEER2 | ConvEER2
| Ductless (<28,000 Btu/h) | 15.3 | NA | 2528 | 0.36 | 1 | 15 | 1 | 1
| Ductless (≥28,000 Btu/h) | 15.3 | NA | 1884 | 0.27 | 1 | 15 | 1 | 1
| Room AC w/ recycling (< 6,000 Btu/h) | 13.1 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/o recycling (< 6,000 Btu/h) | 14.4 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/ recycling (6,000-7,999 Btu/h) | 13.7 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/o recycling (6,000-7,999 Btu/h) | 15.1 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/ recycling (8,000-13,999 Btu/h) | 16 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/o recycling (8,000-13,999 Btu/h) | 17.6 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/ recycling (14,000-19,999 Btu/h) | 16 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/o recycling (14,000-19,999 Btu/h) | 17.6 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/ recycling (20,000-27,999 Btu/h) | 13.8 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Room AC w/o recycling (20,000-27,999 Btu/h) | 15.2 | NA | 2528 | 0.36 | 1 | 9 | 1 | 1
| Central AC Split-System (<45,000 Btu/h) | 15.2 | NA | 1884 | 0.27 | 1 | 15 | 1.049 | 1.043
| Central AC Split-System (45,000-64,999 Btu/h) | 15.2 | NA | 1884 | 0.27 | 1 | 15 | 1.034 | 1.034
| Central AC Single-Package (<65,000 Btu/h) | 15.2 | NA | 1884 | 0.27 | 1 | 15 | 1.053 | 1.107
Notes:
1. CEER applies to Room AC. SEER2 applies to Ductless AC and Central AC.
Note on C42: KP: ESTAR v5.0
Note on C43: KP: ESTAR v7.0
Note on C44: KP: ESTAR v5.0
Note on C45: KP: ESTAR v7.0
Note on C46: KP: Min Fed Stds
Note on C47: KP: ESTAR v7.0
Note on C48: KP: Min Fed Stds
Note on C49: KP: ESTAR v7.0
Note on C50: KP: Min Fed Stds
Note on C51: KP: ESTAR v7.0

## R_HVAC_Central AC Tune Up
RESIDENTIAL: Central A/C Tune Up
Return to TOC
MEASURE DETAILS
Description
Maintenance of a residential central A/C system.
Program Criteria
Contact Hawai'i Energy's residential team for more information.
Unit of Measure
One tune up
Baseline Equipment
Pre-tune up central air conditioning unit
High Efficiency Equipment
Post-tune up central air conditioning unit
ALGORITHMS
ΔE |  |  | = [(CAP.avg / η.avg) * HRS * AF.op] / 1000
ΔP |  |  | = (P.avg * CF) - (P.avg * CF * AF.rt)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Value | Unit | Notes
ΔE |  | Annual energy reduction |  |  | Calculated | kWh
ΔP |  | Peak power demand reduction |  |  | Calculated | kW
CAP.avg |  | Average AC unit cooling capacity |  |  | 36000 | BTU/hr | 3 ton of cooling
P.avg |  | Average AC unit power demand |  |  | 2.77 | kW
η.avg |  | Average AC unit EER |  |  | 13 | EER
AF.op |  | Adjustment factor for operational problems1 |  |  | 8% | -
HRS |  | Annual hours of operation |  |  | 1460 | hrs
AF.rt |  | Adjustment factor for post tune-up run time2 |  |  | 92% | -
Constant |  | Conversion from W to kW |  |  | 1000 | -
CF |  | Coincidence factor |  |  | 33% | -
Measure Life |  | Expected duration of savings |  |  | 3 | yrs
1 Accounts for impacts to performance due to incorrect refrigerant charge, clogged AHU filter, dirty condenser coil.
2 A reduction in run time will occur once tune up is completed, lowering coincidence factor.
SAVINGS
Measure Name |  |  |  | Peak Demand Savings | Annual Energy Savings
Residential AC Tune Up |  |  |  | 0.073 | 323.45

## R_HVAC_Ceiling Fan
RESIDENTIAL: Ceiling Fan
Return to TOC
UPDATE STATUS
This measure is designated "inactive" as of PY22. Before it can be reinstated for a future program year, a full update of the savings approach will be needed.
MEASURE DETAILS
Description
ENERGY STAR ceiling fan with high efficiency motor and CFL bulbs, replacing fan with standard efficiency motor and (three) integral incandescent bulbs.
Program Criteria
Ceiling fan must have an ENERGY STAR label and include lighting.
Unit of Measure
One unit
Baseline Equipment
Standard efficiency motor with three integral incandescent bulbs.
High Efficiency Equipment
ENERGY STAR high efficiency motor with CFL bulbs.
ALGORITHMS
peak kW savings/fan | [7 empty] | = [(%.low * (Low.kW,base - Low.kW,ee) + %.med * (Med.kW,base - Med.kW,ee) + %.high * (High.kW,base - High.kW,ee)) + ((Inc.kW - CFL.kW) * WHF.d)] * CF
annual kWh savings/fan | [7 empty] | = [(%.low * (Low.kW,base - Low.kW,ee) + %.med * (Med.kW,base - Med.kW,ee) + %.high * (High.kW,base - High.kW,ee)) * HRS.fan + ((Inc.kW - CFL.kW) * WHF.e) * HRS.light] * CF
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit | Notes
%.low | %low | %low | %low | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | percent of time on low speed | 40% | 40% | 40% | 40% | -
%.med | %med | %med | %med | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | percent of time on medium speed | 40% | 40% | 40% | 40% | -
%.high | %high | %high | %high | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | percent of time on high speed | 20% | 20% | 20% | 20% | -
Low.kW,base | Low_kW_base | Low_kW_base | Low_kW_base | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | low speed baseline fan motor wattage | 0.0152 | 0.0152 | 0.0152 | 0.0152 | kW
Low.kW,ee | Low_kW_ee | Low_kW_ee | Low_kW_ee | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | low speed efficient fan motor wattage | 0.0117 | 0.0117 | 0.0117 | 0.0117 | kW | 0.008 kW per current ENERGY STAR criteria and min air flow setting | 0.008 kW per current ENERGY STAR criteria and min air flow setting | 0.008 kW per current ENERGY STAR criteria and min air flow setting | 0.008 kW per current ENERGY STAR criteria and min air flow setting | 0.008 kW per current ENERGY STAR criteria and min air flow setting | 0.008 kW per current ENERGY STAR criteria and min air flow setting | 0.008 kW per current ENERGY STAR criteria and min air flow setting | 0.008 kW per current ENERGY STAR criteria and min air flow setting | 0.008 kW per current ENERGY STAR criteria and min air flow setting
Med.kW,base | Med_kW_base | Med_kW_base | Med_kW_base | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | medium speed baseline fan motor wattage | 0.0348 | 0.0348 | 0.0348 | 0.0348 | kW
Med.kW,ee | Med_kW_ee | Med_kW_ee | Med_kW_ee | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | medium speed efficient fan motor wattage | 0.0314 | 0.0314 | 0.0314 | 0.0314 | kW | 0.030 kW per current criteria and min air flow setting | 0.030 kW per current criteria and min air flow setting | 0.030 kW per current criteria and min air flow setting | 0.030 kW per current criteria and min air flow setting | 0.030 kW per current criteria and min air flow setting | 0.030 kW per current criteria and min air flow setting | 0.030 kW per current criteria and min air flow setting | 0.030 kW per current criteria and min air flow setting | 0.030 kW per current criteria and min air flow setting
High.kW,base | High_kW_base | High_kW_base | High_kW_base | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | high speed baseline fan motor wattage | 0.0725 | 0.0725 | 0.0725 | 0.0725 | kW
High.kW,ee | High_kW_ee | High_kW_ee | High_kW_ee | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | high speed efficient fan motor wattage | 0.0715 | 0.0715 | 0.0715 | 0.0715 | kW | 0.067 kW per current criteria and min air flow setting | 0.067 kW per current criteria and min air flow setting | 0.067 kW per current criteria and min air flow setting | 0.067 kW per current criteria and min air flow setting | 0.067 kW per current criteria and min air flow setting | 0.067 kW per current criteria and min air flow setting | 0.067 kW per current criteria and min air flow setting | 0.067 kW per current criteria and min air flow setting | 0.067 kW per current criteria and min air flow setting
Inc.kW | Inc_kW | Inc_kW | Inc_kW | baseline wattage of 3 incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | baseline wattage of three incandescent bulbs | 0.129 | 0.129 | 0.129 | 0.129 | kW | EISA baseline effective 2014 | EISA general purpose baseline effective 2014 | EISA general purpose baseline effective 2014 | EISA general purpose baseline effective 2014 | EISA general purpose baseline effective 2014 | EISA general purpose baseline effective 2014 | EISA general purpose baseline effective 2014 | EISA general purpose baseline effective 2014 | EISA general purpose baseline effective 2014
CFL.kW | CFL_kW | CFL_kW | CFL_kW | wattage of 3 efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | wattage of three efficient CFL bulbs | 0.06 | 0.06 | 0.06 | 0.06 | kW
CF | CF | CF | CF | Coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 11% | 11% | 11% | 11% | -
HRS.fan | HOURS_fan | HOURS_fan | HOURS_fan | Hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | hours of fan operation per year | 1022 | 1022 | 1022 | 1022 | hrs | 2.8 hours per day, 365 days per year | 2.8 hours per day, 365 days per year | 2.8 hours per day, 365 days per year | 2.8 hours per day, 365 days per year | 2.8 hours per day, 365 days per year | 2.8 hours per day, 365 days per year | 2.8 hours per day, 365 days per year | 2.8 hours per day, 365 days per year | 2.8 hours per day, 365 days per year
HRS.light | HOURS_light | HOURS_light | HOURS_light | Hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | hours of light operation per year | 839.5 | 839.5 | 839.5 | 839.5 | hrs | 2.3 hours per day, 365 days per year | 2.3 hours per day, 365 days per year | 2.3 hours per day, 365 days per year | 2.3 hours per day, 365 days per year | 2.3 hours per day, 365 days per year | 2.3 hours per day, 365 days per year | 2.3 hours per day, 365 days per year | 2.3 hours per day, 365 days per year | 2.3 hours per day, 365 days per year
WHF.d | WHFd | WHFd | WHFd | Waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | waste heat factor to account for cooling load savings from efficent lighting | 1.21 | 1.21 | 1.21 | 1.21 | -
WHF.e | WHFee | WHFee | WHFee | Waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | waste heat factor to account for cooling energy savings from efficent lighting | 1.07 | 1.07 | 1.07 | 1.07 | -
Measure Life | Measure Life | Measure Life | Measure Life | Expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 5 | 5 years | 5 years | 5 years | yrs
Source: |  | Hawai‘i Energy Efficiency Program Technical Reference Manual, PY 2015. Measure Savings Calculations, pp. 43
SAVINGS
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings
Ceiling Fan | [7 empty] | 0.01 | [7 empty] | 65.01
Review ENERGY STAR standard at https://www.energystar.gov/products/lighting_fans/ceiling_fans/ceiling_fans_key_product_criteria for updated efficiency criteria. At minimum allowed airflows, qualifying low, medium, high fan wattages are lower than assumed above--see notes.

## R_HVAC_Smart Thermostat
RESIDENTIAL: Smart Thermostat
Return to TOC
UPDATE STATUS
Updated in Winter 2021-2022 for PY22 TRM.
MEASURE DETAILS
Description
An ENERGY STAR smart thermostat replacing a manual or programmable thermostat serving a residential ducted central AC system. ENERGY STAR smart thermostats are Wi-Fi-enabled, allowing customers to control temperature settings wirelessly while at home or away with smart phones and other smart devices. Designs and components vary, but common features include the ability to learn temperature preferences, establish schedules that automatically adjust to energy-saving temperatures when occupants are away or asleep, use geofencing to determine when occupants are on the way home and to adjust temperatures accordingly, and provide information for tracking and managing equipment use and temperature data.
Savings are provided for two types of program delivery: 1) self-install (purchased through Hawai'i Energy's upstream program or through the online marketplace), and 2) for direct install.
Program Criteria
Smart thermostat with ENERGY STAR label
Unit of Measure
One thermostat
Baseline Equipment
Manual or programmable thermostat (savings assume a mix of both)
High Efficiency Equipment
ENERGY STAR smart thermostat
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description |  | Value |  |  |  | Unit | Sources/Notes
ΔkW |  |  |  | Peak demand reduction |  | 0 |  |  |  | kW | Assumes zero peak demand savings in Hawaii.1
CAP.cool | CAP(cool) | CAP(cool) | CAP(cool) | Cooling capacity of central AC unit |  | 45000 |  |  |  | BTU/hr | Assumes 3.75 tons is the average installed capacity for central AC systems in Hawaii.2
EFLH.cool |  |  |  | Equivalent full load cooling hours for existing central air conditioner |  | 1884 |  |  |  | hrs | Hawaii-specific EFLH determined as average of residential EnergyPlus prototype simulations with central AC cooling system by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
ESF.cool | ESF(cool) | ESF(cool) | ESF(cool) | Energy savings factor for cooling, Self-Install |  | 0.05 | 0.02 | 0.02 | 0.02 | - | AEG Benchmarking.3
|  |  |  | Energy savings factor for cooling, Direct-Install |  | 0.11 |  |  |  | -
ISR | PF | PF | PF | In-service rate |  | 0.9 | 1 | 1 | 1 | - | AEG Benchmarking.4
SEER | SEER | SEER | SEER | Seasonal Energy Efficiency Ratio |  | 13.9 | 11.9 | 11.9 | 11.9 | BTU/hr/W | Assumed to be average SEER of installed central AC systems in Hawaii.5
EULEE | Measure Life (yrs) | Measure Life (yrs) | Measure Life (yrs) | Effective useful life of measure |  | 7 | 11 | 11 | 11 | yrs | AEG Benchmarking.6
1. Hawaii's peak period of 5-9 pm on non-holiday weekdays coincides with hours people are generally expected to be home and awake. Therefore, in the absence of targeted education, time-of-use rates, and/or a demand response program, meaningful peak demand savings are not expected from this measure in Hawaii.
2. From AEG 2019 Baseline Study: The average capacity of central AC systems was derived from nameplate data from participants of the residential phone audit who provided photos (N=11).
3. See AEG's 2022 Analysis File titled "PY22 R_HVAC_Smart Thermostat - Analysis File."
4. The ISR is from benchmarking using two sources in particular: 1) PG&E Smart Thermostat Study: Second Year Findings, Prepared by Applied Energy Group, March 20, 2018, ET Project Number ET14PGE8661 (90% of smart thermostats were still installed and connected to Wi-Fi after two years), and 2) Illinois 2021 TRM, Version 9.0 (energy savings algorithm uses ISR of 90%).
5. From AEG 2019 Baseline Study: The average SEER of central AC systems was derived by averaging 1) nameplate SEER data from participants of the residential phone audit who provided photos (N=11) and 2) determination of minimum required SEER based on age of AC systems (N=70). See Appendices from AEG 2019 Baseline Study, Q52F. See also AEG's 2022 Analysis File titled "PY22 R_HVAC_Smart Thermostat - Analysis File."
6. The 7-yr EUL is the average value from several sources with EULs ranging from 3 to 11 years.
SAVINGS
Measure Name |  |  |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  |  |  | Lifetime Energy Savings
Smart Thermostat, Upstream or Online Marketplace |  |  |  |  | 0 |  | 274.47 |  |  |  |  | 1921.29
Smart Thermostat, Direct-Install |  |  |  |  | 0 |  | 603.83 |  |  |  |  | 4226.81
RESOURCES
• | AEG's 2022 Analysis File titled "PY22 R_HVAC_Smart Thermostat - Analysis File."
• | Arkansas Technical Reference Manual, Version 8.1, Arkansas Public Service Commission, August 31, 2019.
• | California eTRM, Residential Smart Thermostat, Measure ID: SWHC039, effective dates: Jan 1 - Dec. 31, 2021
• | Connecticut's 2021 Program Savings Document, 18th Edition, Filed on March 1, 2021.
• | DEER 2020 "SupportTable-EUL2020.xlsx", accessed by AEG January 14, 2022.
• | Energy Impacts of Smart Home Technologies, Jen King, ACEEE, April 2018, Report A1801.
• | ENERGY STAR Smart Thermostats, <https://www.energystar.gov/products/smart_thermostats>.
• | Federal Standards: 10 CFR 430.32 (c).
• | Hawai‘i-specific energy simulations of single family home prototypes in BEopt™ with EnergyPlus v8.8 as the simulation engine.
• | Illinois Statewide Technical Reference Manual, 2021, Version 9.0, Volume 3: Residential Measures, Final, September 25, 2020.
• | Maryland/Mid-Atlantic Technical Reference Manual, Version 10, Final, May 2020.
• | PG&E Smart Thermostat Study: First Year Findings, Prepared by Applied Energy Group, December 21, 2016, ET Project Number ET13PGE1462, available for download: <https://www.etcc-ca.com/reports/smart-thermostat-study?dl=1642447625>.
• | PG&E Smart Thermostat Study: Second Year Findings, Prepared by Applied Energy Group, March 20, 2018, ET Project Number ET14PGE8661, available for download: <https://www.etcc-ca.com/reports/smart-thermostat-study?dl=1642447625>.
• | Public Utility Commission of Texas, Texas TRM, Version 8.0, Volume 2: Residential Measures, Program Year 2021.
• | Regional Technical Forum, Residential Connected Thermostats, April 10, 2018, "ResConnectedTstats_v1.3.xlsm," accessed here: <https://rtf.nwcouncil.org/measure/connected-thermostats>.
• | State of Pennsylvania Technical Reference Manual, Volume 2: Residential Measures, Revised February 2021, <https://www.puc.pa.gov/filing-resources/issues-laws-regulations/act-129/technical-reference-manual/>.
• | 2014 Evergreen Economics Hawaii Baseline Study, Appendices C and D, C.2 Percent by Home Type (page 127) and D.1 Percent by Home Type (page 147).
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | Wisconsin Focus on Energy 2020 Technical Reference Manual, Public Service Commission of Wisconsin.
∆𝑘𝑊=0
∆𝑘𝑊ℎ=(〖𝐶𝐴𝑃〗_𝑐𝑜𝑜𝑙∗〖𝐸𝐹𝐿𝐻〗_𝑐𝑜𝑜𝑙∗〖𝐸𝑆𝐹〗_𝑐𝑜𝑜𝑙∗𝐼𝑆𝑅)/(𝑆𝐸𝐸𝑅∗1000 𝑊⁄𝑘𝑊)
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## R_HVAC_Solar Attic Fan
RESIDENTIAL: Solar Attic Fan
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the Mid-Year PY24 TRM. The update adds a savings table for single family attached homes, including duplexes and townhomes; the effective date for the single family attached homes portion of the measure is July 1, 2025. The update also clarified the descriptions of CEER and SEER in the "Definitions & Assumptions" table.
MEASURE DETAILS
Description
Solar-powered attic fans reduce the existing air conditioning (AC) load and energy usage by reducing the attic temperature. Single family attached homes (including duplexes and townhomes) and single family detached homes are eligible for rebates from this measure if they have pre-existing AC systems.
Program Criteria
Contact Hawai'i Energy's residential team for more information.
Unit of Measure
Solar Attic Fan sized to attic
Baseline Equipment
(1) No fan system installed and a pre-existing Central AC system. (2) No fan system installed and pre-existing Room ACs. (3) No fan system installed and pre-existing Ductless Mini Splits. (4) No fan system installed and an unknown pre-existing cooling system.
High Efficiency Equipment
Solar-powered attic fan in an air-conditioned home
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  | Sources/Notes
%.svgs,ac |  |  |  | Percent of AC load reduced by solar attic fan in a house built before 2010 | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | 7.768% | 20% | 20% | 20% | - |  | AEG Research.1 Values differ due to varying Attic Insulation values in each model. Default uses weighted average based on home vintage data in Table 2 below. | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf
|  |  |  | Percent of AC load reduced by solar attic fan in a house built 2010 and after | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | 3.366% | 20% | 20% | 20% | -
AC.cap |  |  |  | Average cooling capacity in home with Room ACs or a Ductless Mini Split AC | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | 24000 | 8500 | 8500 | 8500 | Btu/h |  | Assumed two 12,000 Btu/h Room ACs per home or one 24,000 Btu/h Ductless Mini Split AC per home. | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy
|  |  |  | Average sizing of a central AC system. | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | 36000 | 8500 | 8500 | 8500 | Btu/hr |  | Assumed a 36,000 Btu/h (3 Ton) system in the average home in Hawaii. | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy
Constant |  |  |  | Conversion factor | [11 empty] | 1000 |  |  |  | W/kW
SEER |  |  |  | Seasonal energy efficiency ratio of existing central air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | 13 | 9.8 | 9.8 | 9.8 | Btu/Wh |  | The minimum is 13.0 SEER for split-system central AC and single-package central AC systems manufactured after Jan. 23, 2006 and before Jan. 1, 2015 and installed in Hawai'i.2
CEER |  |  |  | Combined energy efficiency ratio of an average Ductless Mini-Split AC |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | 9.4 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Federal minimum requirement for 20,000-29,000 Btu/h room AC units manufactured as of Jun. 1, 2014.3
|  |  |  | Combined energy efficiency ratio of baseline unit for existing Room ACs |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | 9.7 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Assumed to be EERBL,1 / 1.01 per ENERGY STAR data.4
EFLH |  |  |  | Equivalent full load cooling hours for existing central air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | 1884 | 1825 | 1825 | 1825 | hrs |  | EFLH determined as average of residential EnergyPlus prototype simulations with central AC cooling system by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
|  |  |  | Equivalent full load cooling hours of a Room AC and Ductless Mini Split |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | 2528 | 1825 | 1825 | 1825 | hrs/yr | Deemed value; 5 hrs per day cooling | EFLH determined as average of residential EnergyPlus prototype simulations with room AC/ductless mini split cooling system by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
CF | CF | CF | CF | Coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0.011586 | 0 | 0 | 0 | - |  | Calculated by analyzing the savings load shape specific to this measure.1
PF | PF | PF | PF | Persistence factor | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | 1 | 1 | 1 | 1 | -
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 20 | 20 years | 20 years | 20 years | yrs
Table 1: Distribution of AC Type for Homes with AC System
Cooling System Distribution
|  | Type of AC System | [9 empty] | Single Family Detached |  |  |  |  | Single Family Attached
|  | Central AC Homes: | [9 empty] | 15.38% |  |  |  |  | 10.53%
|  | Room AC Homes: | [9 empty] | 51.92% |  |  |  |  | 82.46%
|  | Ductless Mini Split AC Homes: | [9 empty] | 32.69% |  |  |  |  | 7.018%
Source: 2019 Baseline Study5
Table 2: Distribution of Homes by Vintage
Housing Vintage Distribution
|  | Time Period | [9 empty] | Single Family Detached |  |  |  |  | Single Family Attached
|  | Before 2010 | [9 empty] | 94.2% |  |  |  |  | 91.7%
|  | 2010 and after | [9 empty] | 5.8% |  |  |  |  | 8.3%
Source: 2019 Baseline Study5
Notes: |  | 1. AEG created a Hawaii-specific 8760 hourly heat transfer model to calculate the effect that attic temperature has on the cooling load. See AEG's 2020 Analysis File titled "WHF SAF and HPWH PY20 Updates. 2. AEG's research of the AHRI database (Oct 2018 extract) showed that 11.0 EER represents the 1st quartile (and median) of EER values corresponding to 13 SEER. Since it is reasonable to want all high efficiency systems to be more efficient than the 1st quartile (or median) EER value, 11.0 EER was used for 13 SEER baseline units. 3. Federal Standard Specifications. https://www.govinfo.gov/content/pkg/CFR-2012-title10-vol3/pdf/CFR-2012-title10-vol3-sec430-32.pdf 4. ENERGY STAR specification provided equivalent EER and CEER ratings. For the most popular size band (8,000-13,999 Btu/h), the EER rating is approximately 1% higher than the CEER. See ENERGY STAR Version 3.0 Room Air Conditioners Program Requirements and IL TRM v6.0 Vol. 3, Feb 8, 2017, pg. 35. 5. 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. This data is used in the unknown scenario to average the savings between the three cooling types.
SAVINGS
Single Family Detached Homes
Deemed Savings (based on default values for key parameters)
AC Type | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Central AC | [7 empty] | 0.002 | [7 empty] | 391.97 | [6 empty] | 7839.4
Room AC | [7 empty] | 0.002 | [7 empty] | 469.93 | [6 empty] | 9398.6
Ductless Mini Split | [7 empty] | 0.002 | [7 empty] | 484.93 | [6 empty] | 9698.6
Unknown AC | [7 empty] | 0.002 | [7 empty] | 462.84 | [6 empty] | 9256.8
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
|  | Enter Type of Cooling System: | [16 empty] | Central AC
|  | Enter Year of Construction: | [16 empty] | Unknown
|  | Enter Cooling System Capacity (Btu/hr): | [16 empty] | 36000
|  | Enter Existing Efficiency Rating (SEER/CEER): | [16 empty] | 13
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Attic Fan (Single Family Detached Homes) | [7 empty] | 0.002 | [7 empty] | 391.97 | [6 empty] | 7839.4
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
Single Family Attached Homes (Duplexes and Townhomes); Effective as of July 1, 2025
Deemed Savings (based on default values for key parameters)
AC Type | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Central AC | [7 empty] | 0.002 | [7 empty] | 386.23 | [6 empty] | 7724.6
Room AC | [7 empty] | 0.002 | [7 empty] | 463.05 | [6 empty] | 9261
Ductless Mini Split | [7 empty] | 0.002 | [7 empty] | 477.83 | [6 empty] | 9556.6
Unknown AC | [7 empty] | 0.002 | [7 empty] | 456 | [6 empty] | 9120
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
|  | Enter Type of Cooling System: | [16 empty] | Ductless Mini Split
|  | Enter Year of Construction: | [16 empty] | Unknown
|  | Enter of Cooling System Capacity (Btu/hr): | [16 empty] | 24000
|  | Enter Existing Efficiency Rating (SEER/CEER): | [16 empty] | 9.4
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Attic Fan (Single Family Attached Homes) | [7 empty] | 0.002 | [7 empty] | 477.83 | [6 empty] | 9556.6
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's 2025 Analysis File named "Mid-Year PY24 TRM - Solar Attic Fan - Analysis File."
• | AEG's 2020 Analysis File titled "AEG HPUC WHF SAF and HPWH PY20 Updates - Analysis File."
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | Performance Assessment of Photovoltaic Attic Ventilator Fans. Danny S. Parker, John R. Sherwin. Florida Solar Energy Center. http://www.fsec.ucf.edu/en/publications/html/fsec-gp-171-00/
• | Hawaii Energy - Technical Resource Manual No. 2014. Section 8.3.4 Solar Attic Fans.
• | Principles of Attic Ventilation. Air Vent Inc. http://www.airvent.com/index.php/ventilation-resources/literature-sales-tools/professionals/121-principles-of-attic-ventilation-course/file.
• | About Attic Ventilation. ENERGY STAR Website. https://www.energystar.gov/campaign/seal_insulate/do_it_yourself_guide/about_attic_ventilation.
• | AEG Cooling Loadshape for Hawaii. "HI_1681S_ACH7_CAC13_ltg1000.csv"
• | Hawaii Energy Building Code. https://energy.hawaii.gov/hawaii-energy-building-code/pre-2015-iecc.
• | Heat Transfer Equation Sheet. https://faculty.utrgv.edu/constantine.tarawneh/Heat%20Transfer/HeatTransferBooklet.pdf.
• | Electronic Code of Federal Regulations: Title 10: Energy, Part 430 - Energy Conservation Program for Consumer Products. Subpart C - Energy and Water Conservation Standards. Section 6d. https://www.ecfr.gov/cgi-bin/text-idx?SID=80dfa785ea350ebeee184bb0ae03e7f0&mc=true&node=se10.3.430_132&rgn=div8].
∆𝑘𝑊ℎ=〖𝐴𝐶〗_𝑐𝑎𝑝/ 1000 ∗ (1 / (𝐶𝐸𝐸𝑅 𝑜𝑟 𝑆𝐸𝐸𝑅)) ∗ %_(𝑠𝑣𝑔𝑠,𝑎𝑐) ∗ 𝑃𝐹 ∗ 𝐸𝐹𝐿𝐻
* CF
∆𝑘𝑊=〖𝐴𝐶〗_𝑐𝑎𝑝/ 1000 ∗ (1 / (𝐶𝐸𝐸𝑅 𝑜𝑟 𝑆𝐸𝐸𝑅)) ∗ %_(𝑠𝑣𝑔𝑠,𝑎𝑐) ∗ 𝑃𝐹* CF
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## R_HVAC_Whole House Fan
RESIDENTIAL: Whole-House Fan
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the Mid-Year PY24 TRM V2. The update clarifies the descriptions of CEER and SEER in the "Definitions & Assumptions" table.
MEASURE DETAILS
Description
This measure involves the installation of a whole house fan. The fan draws cool outdoor air inside through open windows and exhausts hot indoor air through the attic to the outside. Running a whole house fan whenever outdoor temperatures are lower than indoor temperatures will cool a house. This measure results in savings by replacing the cooling load with the whole house fan load when the outside air temperature is below the set point temperature of the AC system. Measure savings are calculated from two baselines. The first being a single family home with a cooling system installed and the second being a home with no AC system installed. Savings from the second baseline are the load that would be displaced if the home were to install a cooling system. In both cases there was no whole house fan installed previously. Only single family homes are eligible for rebates from this measure.
Program Criteria
Contact Hawai'i Energy's residential team for more information.
Unit of Measure
One fan.
Baseline Equipment
(1) No fan and no cooling system installed. (2) No fan system installed and a pre-existing Central AC system. (3) No fan system installed and pre-existing Room ACs. (4) No fan system installed and pre-existing Ductless Mini Splits. (5) No fan system installed and an unknown pre-existing cooling system.
High Efficiency Equipment
Fan installed.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  | Sources/Notes
%svgs,ac | %svgs_ac | %svgs_ac | %svgs_ac | Percent of AC load reduced by a whole house fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | percent of a/c load savings from solar attic fan | 17.75% | 20% | 20% | 20% | - |  | AEG looked at hourly TMY3 data for Honolulu, HI and calculated the wetbulb temperature of 68°F at an interior setpoint of 76°F and a relative humidity of 65% (ASHRAE-recommended limit). It was then assumed that air could be brought into the home at or below this wetbulb temperature via the whole house fan and replace the cooling load while still providing the same comfort.1 | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf | reference: KEMA-Xenergy, Inc. Impact Evaluation of the 2001 Statewide Low Income Energy Efficiency (LIEE) Program. April 8, 2003. calmac.org/publications/2001_LIEE_Impact_Evaluation.pdf
ACcap | AC_cap | AC_cap | AC_cap | Average cooling capacity in home with Room ACs or a Ductless Mini Split AC | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | 24000 | 8500 | 8500 | 8500 | Btu/h |  | Assumed two 12,000 Btu/h Room ACs per home or one 24,000 Btu/h Ductless Mini Split ACs per home. | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy
|  |  |  | Average sizing of a central AC system. | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | cooling capacity of existing air conditioner | 36000 | 8500 | 8500 | 8500 | Btu/h |  | Assumed a 36,000 Btu/h (3 Ton) system in the average home in Hawaii. | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy | average of PY14 window A/C units incentivized by Hawaii Energy
Constant |  |  |  | Conversion factor | [11 empty] | 1000 |  |  |  | W/kW
SEER |  |  |  | Seasonal energy efficiency ratio of existing central air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | 13 | 9.8 | 9.8 | 9.8 | Btu/Wh |  | The minimum is 13.0 SEER for split-system central AC and single-package central AC systems manufactured after Jan. 23, 2006 and before Jan. 1, 2015 and installed in Hawai'i.2
|  |  |  | Minimum federal standard of seasonal energy efficiency ratio for a new central air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | full load cooling efficiency of existing air conditioner | 14 | 9.8 | 9.8 | 9.8 | Btu/Wh |  | The minimum is 14.0 SEER for split-system central AC and single-package central AC systems manufactured on or after Jan. 1, 2015 and installed in Hawai'i.3
CEER |  |  |  | Combined energy efficiency ratio of an average Ductless Mini-Split AC |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | 9.4 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Federal minimum requirement for 20,000-29,000 Btu/h room AC units manufactured as of Jun. 1, 2014.
|  |  |  | Combined energy efficiency ratio of baseline unit for existing Room ACs |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | 9.7 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Assumed to be EERBL,1 / 1.01 per ENERGY STAR data.4 Federal standard for pre-Jun 1 2014 value for 8000-13999 Btu/h systems.
|  |  |  | Minimum federal standard of the combined energy efficiency ratio of new Room ACs |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | baseline rated efficiency, BTU/hr-W, which depends on cooling capacity of proposed equipment. |  | 10.9 | see table 1 | see table 1 | see table 1 | Btu/Wh |  | Federal minimum requirement for 8,000-13,999 Btu/h units manufactured as of Jun. 1, 2014.
EFLH |  |  |  | Equivalent full load cooling hours for existing central air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | equivalent full load cooling hours for existing air conditioner | 1884 | 1825 | 1825 | 1825 | hrs |  | EFLH determined as average of residential EnergyPlus prototype simulations with central AC cooling system by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
|  |  |  | Equivalent full load cooling hours of a Room AC and Ductless Mini Split |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | 2528 | 1825 | 1825 | 1825 | hrs/yr | Deemed value; 5 hrs per day cooling | EFLH determined as average of residential EnergyPlus prototype simulations with room AC/ductless mini split cooling system by dividing total cooling kWh by maximum kW (proxy for capacity, adjusted for oversizing).
kWhWHF | HOURS | HOURS | HOURS | Whole House Fan Annual Energy Usage |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | 321.1758 | 1825 | 1825 | 1825 | kWh | Deemed value; 5 hrs per day cooling | Calculated based on HOU of whole house fan in Hawaii and wattage's of standard fans installed in Hawaii.
kWWHF | HOURS | HOURS | HOURS | Whole House Fan Wattage |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | equivalent full load cooling hours |  | 0.10898 | 1825 | 1825 | 1825 | kW | Deemed value; 5 hrs per day cooling | Calculated based on HOU of whole house fan in Hawaii and wattage's of standard fans installed in Hawaii.
CF | CF | CF | CF | Coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0.096013 | 0.59 | 0.59 | 0.59 | - |  | Calculated by analyzing the savings load shape specific to this measure.1
PF | PF | PF | PF | Persistence factor | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | 1 | 1 | 1 | 1 | -
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 20 | 20 years | 20 years | 20 years | yrs
Table 1: Distribution of AC Type for Homes with AC System
|  | Central AC Homes: | [9 empty] | 15.38%
|  | Room AC Homes: | [9 empty] | 51.92%
|  | Ductless Mini Split AC Homes: | [9 empty] | 32.69%
Source: 2019 Baseline Study5
Notes: |  | 1. AEG created a Hawaii-specific 8760 hourly model to calculate the savings effect of the whole house fan measure. See AEG's Analysis File titled "WHF SAF and HPWH PY20 Updates." 2. AEG's research of the AHRI database (Oct 2018 extract) showed that 11.0 EER represents the 1st quartile (and median) of EER values corresponding to 13 SEER. Since it is reasonable to want all high efficiency systems to be more efficient than the 1st quartile (or median) EER value, 11.0 EER was used for 13 SEER baseline units. 3. AEG's research of the AHRI database (Oct 2018 extract) showed that 11.5 EER represents the 1st quartile of EER values corresponding to 14 SEER. Since it is reasonable to want all high efficiency systems to be more efficient than the 1st quartile EER value, 11.5 EER was used for 14 SEER baseline units. 4. ENERGY STAR specification provided equivalent EER and CEER ratings. For the most popular size band (8,000-13,999 Btu/h), the EER rating is approximately 1% higher than the CEER. See ENERGY STAR Version 3.0 Room Air Conditioners Program Requirements and IL TRM v6.0 Vol. 3, Feb 8, 2017, pg. 35. 5. 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. This data is used in the unknown scenario to average the savings between the three cooling types.
SAVINGS
Deemed Savings (based on default values for key parameters)
AC Type | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Central AC | [7 empty] | 0.037 | [7 empty] | 605 | [6 empty] | 12100
Room AC | [7 empty] | 0.032 | [7 empty] | 789.2 | [6 empty] | 15784
Ductless Mini Split | [7 empty] | 0.033 | [7 empty] | 824.63 | [6 empty] | 16492.6
Unknown AC | [7 empty] | 0.033 | [7 empty] | 772.44 | [6 empty] | 15448.8
No AC | [7 empty] | 0.03 | [7 empty] | 698.79 | [6 empty] | 13975.8
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
|  | Enter Type of Cooling System: | [16 empty] | Central AC
|  | Enter Cooling System Capacity (Btu/hr): | [16 empty] | 36000
|  | Enter Existing Efficiency Rating (SEER/CEER): | [16 empty] | 13
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Whole House Fan | [7 empty] | 0.037 | [7 empty] | 605 | [6 empty] | 12100
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's 2025 Analysis File named "Mid-Year PY24 TRM - Whole House Fan - Analysis File."
• | AEG's 2020 Analysis File titled "AEG HPUC WHF SAF and HPWH PY20 Updates - Analysis File."
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | AEG Cooling Loadshape for Hawaii. "HI_1681S_ACH7_CAC13_ltg1000.csv."
• | D. Springer, B. Dakin, and A. German, Measure Guideline: Ventilation Cooling, Energy Efficiency & Renewable Energy, U.S. Department of Energy, April 2012, https://www.nrel.gov/docs/fy12osti/54241.pdf.
• | Electronic Code of Federal Regulations: Title 10: Energy, Part 430 - Energy Conservation Program for Consumer Products. Subpart C - Energy and Water Conservation Standards. Section 6d. https://www.ecfr.gov/cgi-bin/text-idx?SID=80dfa785ea350ebeee184bb0ae03e7f0&mc=true&node=se10.3.430_132&rgn=div8].
• | "HSEO's EEB - Suggestions for Hawaii Energy PY 2020 TRM Update (002)," Word document containing update ideas for the PY20 TRM.
• | Savings Estimation Technical Reference Manual 2017, Third Edition, California Municipal Utilities Association, https://www.cmua.org/files/CMUA-POU-TRM_2017_FINAL_12-5-2017%20-%20Copy.pdf.
• | Whole House Fan, Technology Fact Sheet, NREL, DOE/GO-10099-745, March 1999, https://www.nrel.gov/docs/fy99osti/26291.pdf.
• | Whole House Fan, Work Paper PGECOHVC134, Revision #3, Pacific Gas & Electric Company, Customer Energy Solutions, June 21, 2012.
∆𝑘𝑊ℎ=〖𝐴𝐶〗_𝑐𝑎𝑝/ 1000 ∗ (1 / (𝐶𝐸𝐸𝑅 𝑜𝑟 𝑆𝐸𝐸𝑅)) ∗ %_(𝑠𝑣𝑔𝑠,𝑎𝑐) ∗ 𝑃𝐹 ∗ 𝐸𝐹𝐿𝐻 − 〖𝑘𝑊ℎ〗_𝑊𝐻𝐹
) * CF
∆𝑘𝑊=〖(𝐴𝐶〗_𝑐𝑎𝑝/ 1000 ∗ (1 / (𝐶𝐸𝐸𝑅 𝑜𝑟 𝑆𝐸𝐸𝑅)) ∗ %_(𝑠𝑣𝑔𝑠,𝑎𝑐) ∗ 𝑃𝐹 − 〖𝑘𝑊〗_𝑊𝐻𝐹) * CF
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸

## R_HVAC_Dehumidifier
RESIDENTIAL: Dehumidifier
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the PY25 TRM.
MEASURE DETAILS
Description
The deployment of an energy efficient domestic dehumidifier, portable or whole-home. ENERGY STAR (ES) versions update mid-year 2025. Use V5.0 criteria prior to October 1, 2025 and V6.0 after.
Program Criteria
Dehumidifier must be ENERGY STAR certified.
Unit of Measure
One dehumidifier, portable or whole-home.
Baseline Equipment
Non-ENERGY STAR dehumidifier.
High Efficiency Equipment
ENERGY STAR certified dehumidifier.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  |  | Value | Unit | Source/Notes
CAP |  |  | Capacity |  |  |  | See Tables 1 through 4 | pints/day | ES Qualified Product List (QPL)
ηbs |  |  | Baseline efficiency rating |  |  |  | See Tables 1 through 4 | L/kWh | Residential dehumidifiers must meet the energy conservation standards specified in the Code of Federal Regulations at 10 CFR 430.32(v).
ηhe |  |  | High efficiency rating |  |  |  | See Tables 1 through 4 | L/kWh | ENERGY STAR V5.0: Averages by capacity bin from May 8, 2025 qualified product list ENERGY STAR V6.0: Final Specifications
CF |  |  | Coincidence factor, percent of time equipment load corresponds with utility peak. |  |  |  | 0.476 | - | In absence of a dehumidifier load shape, the CF was calculated by using HVAC fan load shape as a proxy. See ICF's 2025 analysis file named "Load_shape_by_segment_110519_Dehumidifier_05132025."
HRS |  |  | Equipment annual operating hours |  |  |  | 3185 | hrs/yr | NREL: Measure Guideline: Supplemental Dehumidification in Warm-Humid Climates. Miami (Climate Zone 1) hours at 60% set point.
Constant |  |  | Liters/pints conversion |  |  |  | 0.473 | L/pt
EULp |  |  | Effective useful life of portable dehumidifiers |  |  |  | 10 | yrs | FederalRegister.gov - Energy Conservation Standards for Dehumidifiers
EULwh |  |  | Effective useful life of whole-home dehumidifiers |  |  |  | 12 | yrs
SAVINGS - ENERGY STAR V5.0, effective before October 1, 2025
Table 1: Performance Criteria for ENERGY STAR V5.0 Certified Portable Dehumidifiers
Capacity (pints/day) |  |  | Average Capacity 1 (pints/day) | PY23 Rebate Product % 2 |  | Baseline Efficiency 3 (≥ L/kWh) | Enhanced Efficiency 4 (≥ L/kWh) | kW Savings |  | kWh Savings
≤25 |  |  | 24.61 | 51.22% |  | 1.3 | 1.6817 | 0.040311 |  | 269.7249
> 25 to ≤50 |  |  | 45.233 | 48.78% |  | 1.6 | 1.8704 | 0.038335 |  | 256.5076
> 50 |  |  | - | 0% |  | 2.8 | NA | - |  | -
Wtd. Average |  |  | 34.67 |  |  |  |  | 0.039347 |  | 263.2774
Notes: |  | 1,2. Weighted averages of capacities based on units that were provided rebates in PY23. 3. Federal minimum standard efficiency. 4. Averages by capacity bin from ENERGY STAR qualified product list, accessed May 8, 2025. All ENERGY STAR certified units greater than 50 pints/day in the qualified product list are whole home dehumidifiers.
Table 2: Performance Criteria for ENERGY STAR V5.0 Certified Whole-home Dehumidifiers
Product Case Volume (cu.ft.) |  |  | Average Capacity 1 (pints/day) | ENERGY STAR Product % 2 |  | Baseline Efficiency 3 (≥ L/kWh) | Enhanced Efficiency 4 (≥ L/kWh) | kW Savings |  | kWh Savings
≤ 8 |  |  | 86.8436 | 100% |  | 1.77 | 2.3829 | 0.11838 |  | 792.1091
> 8 |  |  | - | 0% |  | 2.41 | NA | - |  | -
Wtd. Average |  |  | 86.8436 |  |  |  |  | 0.11838 |  | 792.1091
Notes: |  | 1,2. Weighted average of capacities based on units listed in ENERGY STAR Certified Product List. Accessed 2025/05/08. 3. Federal minimum standard efficiency. 4. Averages by capacity bin from ENERGY STAR qualified product list, accessed May 8, 2025. There are no ENERGY STAR certified units greater than 8 cu.ft. in the qualified product list.
Note: Sunset date for ENERGY STAR V5.0 savings is September 30, 2025
Measure Name |  |  |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Portable Dehumidifier, ENERGY STAR V5.0 |  |  |  |  | 0.039 |  | 263.28 |  |  | 2632.8
Whole-home Dehumidifier, ENERGY STAR V5.0 |  |  |  |  | 0.118 |  | 792.11 |  |  | 9505.32
SAVINGS - ENERGY STAR V6.0, effective on October 1, 2025 and after
Table 3: Performance Criteria for ENERGY STAR V6.0 Certified Portable Dehumidifiers
Capacity (pints/day) |  |  | Avg. Capacity 1 (pints/day) | Rebate Product % 2 |  | Baseline Efficiency 3 (≥ L/kWh) | Enhanced Efficiency 4 (≥ L/kWh) | kW Savings |  | kWh Savings
≤25 |  |  | 24.61 | 51.22% |  | 1.3 | 1.7 | 0.041787 |  | 279.601
> 25 to ≤50 |  |  | 45.233 | 48.78% |  | 1.6 | 2.01 | 0.054098 |  | 361.9783
> 50 |  |  | - | 0% |  | 2.8 | 3.3 | - |  | -
Wtd. Average |  |  | 34.67 |  |  |  |  | 0.047792 |  | 319.785
Notes: |  | 1,2. Weighted averages of capacities based on units that were provided rebates in PY23. 3. Federal minimum standard efficiency. 4. ENERGY STAR program criteria efficiency.
Table 4: Performance Criteria for ENERGY STAR V6.0 Certified Whole-home Dehumidifiers
Product Case Volume (cu.ft.) |  |  | Avg. Capacity 1 (pints/day) | ENERGY STAR Product % 2 |  | Baseline Efficiency 3 (≥ L/kWh) | Enhanced Efficiency 4 (≥ L/kWh) | kW Savings |  | kWh Savings
≤ 8 |  |  | 86.8436 | 100% |  | 1.77 | 2.22 | 0.0933 |  | 624.2856
> 8 |  |  | - | 0% |  | 2.41 | 3.81 | - |  | -
Wtd. Average |  |  | 86.8436 |  |  |  |  | 0.0933 |  | 624.2856
Notes: |  | 1,2. Weighted average of capacities based on units listed in ENERGY STAR Certified Product List. Accessed 2025/05/08. 3. Federal minimum standard efficiency. 4. ENERGY STAR program criteria efficiency.
Note: Effective date for ENERGY STAR V6.0 savings is October 1, 2025
Measure Name |  |  |  |  | Peak Demand Savings |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Portable Dehumidifier, ENERGY STAR V6.0 |  |  |  |  | 0.048 |  | 319.79 |  |  | 3197.9
Whole-home Dehumidifier, ENERGY STAR V6.0 |  |  |  |  | 0.093 |  | 624.29 |  |  | 7491.48
RESOURCES
• | ICF's 2025 Analysis Files named "PY25 TRM - Residential Dehumidifier - Analysis File" and "Load_shape_by_segment_110519_Dehumidifier_05132025."
• | AEG's 2019 Analysis File titled "New Residential Measures Summary - AEG Analysis file."
• | Code of Federal Regulations, Title 10, Part 430, Subpart C, https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32#p-430.32(v).
• | Energy Conservation Standards for Dehumidifiers, Section F, Table IV.4, https://www.federalregister.gov/documents/2023/11/06/2023-24106/energy-conservation-program-energy-conservation-standards-for-dehumidifiers.
• | ENERGY STAR, Dehumidifiers, https://www.energystar.gov/products/appliances/dehumidifiers.
• | ENERGY STAR, Dehumidifier Qualified Product List, https://www.energystar.gov/productfinder/download/certified-dehumidifiers/.
• | ENERGY STAR Dehumidifiers V5.0 Final Specification, https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Dehumidifiers%20Version%205.0%20Program%20Requirements_0.pdf.
• | ENERGY STAR Dehumidifiers V6.0 Final Specification, https://www.energystar.gov/sites/default/files/2024-08/ENERGY%20STAR%20Dehumidifiers%20V6.0%20Final%20Specification%20with%20Partner%20Commitments.pdf.
• | U.S. Department of Energy, Energy Efficiency & Renewable Energy, Building Technologies Office, Measure Guideline: Supplemental Dehumidification in Warm-Humid Climates, Armin Rudd, Building Science Corporation, October 2014, available here: https://www.nrel.gov/docs/fy15osti/62677.pdf.
• | PY23 Dehumidifier Rebates provided by Hawai'i Energy on 5/16/2025. See file named "PY23_IceMachineDehumidifiersEStarFields_20250516.csv."
∆𝑘𝑊=((𝐶𝐴𝑃∗0.473))/24∗(1/𝜂_𝑏𝑠 −1/𝜂_ℎ𝑒 )∗𝐶𝐹
∆𝑘𝑊ℎ=((𝐶𝐴𝑃∗0.473))/24∗(1/𝜂_𝑏𝑠 −1/𝜂_ℎ𝑒 )∗𝐻𝑅𝑆
∆〖𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=Δ𝑘𝑊ℎ∗𝐸𝑈𝐿

## R_Light_LED
RESIDENTIAL: LED
Return to TOC
UPDATE STATUS
Updated in Spring 2025 for the Mid-Year PY24 TRM V2. This update adds a new set of deemed savings values that applies to direct install LED lighting through the Energy Smart for Homes (ES4H) program, which supports Accessibility & Affordability (A&A) customers. The new set of savings is applicable for PY25 through PY28, with a sunset date of June 30, 2029. The previous deemed savings values are only applicable through December 31, 2024 for the REEM portion of the measure, and through June 30, 2025 for the ES4H portion of the measure.
MEASURE DETAILS
Description
The replacement of an EISA-compliant omni-directional, medium screw base lamp with an LED lamp of comparable brightness (lumens) in both Residential Single Family and Multifamily homes. This measure is implemented through REEM and RHTR, which includes ES4H.
Program Criteria
This measure is applicable to both residential and commercial programs, provided the LEDs are for residential end-use applications.
The replacement LED lamp must meet program minimum requirements.
The REEM portion of this measure has a sunset date of December 31, 2024, which is the day before Hawaii's ban on screw-base fluorescent lamps takes effect. The ES4H portion of the measure has a sunset date of June 30, 2029, which is the end of PY28. The extra four years for the ES4H portion of the measure allows for early replacement of pre-existing CFLs, which have an RUL of four years.
Unit of Measure
One lamp.
Baseline Equipment
This baseline approach applies the expanded GSL definition and Tier 2 backstop of 45 lumens per Watt reinstated by the U.S. Department of Energy in final rulings published on May 9, 2022 (Federal Register 87FR27461 and 87FR27439).
High Efficiency Equipment
The high efficiency case is an omni-directional LED lamp that meets program minimum requirements. As an alternative to more traditional LED bulbs or tubes, LED retrofit kit engines qualify as applicable LED replacement lighting, as long as the LED retrofit kit engines have appropriate form factors compared to the baseline lighting.
There are two sets of deemed savings values. The first set uses the effective useful life (EUL) of the LED replacement lighting to calculate the lifetime energy savings. The first set is applicable to REEM through December 31, 2024 and to ES4H through June 30, 2025. The second set uses the remaining useful life (RUL) of pre-existing lighting, which is assumed to be a compact fluorescent lamp (CFL), to calculate lifetime energy savings. The second set is only applicable to ES4H, with savings valid for PY25 through PY28.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
Applicable through Dec. 31, 2024 for REEM, and through Jun. 30, 2025 for ES4H:
(3a)
Applicable through Jun. 30, 2029 for ES4H only:
(3b)
Waste Heat Factors due to Interaction with Space Cooling System
(4)
(5)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  | Source/Notes
kWbase | kW_b | kW_b | kW_b | Baseline Wattage - EISA Tier 2 (calculated for middle of lumen range) | [11 empty] | See Table 1 | see Table 1 | see Table 1 | see Table 1 | kW |  | U.S. Department of Energy, final rulings, May 9, 2022 (Federal Register 87FR27461 and 87FR27439)
kWLED | kW_led | kW_led | kW_led | Wattage of LED lamp that meets program minimum requirements (typical values from Hawai‘i Energy program data) | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | See Table 1 | see Table 2 | see Table 2 | see Table 2 | kW |  | No change from PY18 TRM
ISR |  |  |  | Lifetime in-service rate | [11 empty] | 0.97 |  |  |  | - |  | AEG's Fall 2018 Benchmarking
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | See Table 2 | 0.12 | 0.12 | 0.12 | - |  | AEG's Hawai‘i-specific simulation modeling
HOU |  |  |  | Average hours of use per day | [11 empty] | See Table 2 | 0.12 | 0.12 | 0.12 | hr/day |  | No change from PY18 TRM; values confirmed with AEG's Fall 2018 Benchmarking
WHC,D |  |  |  | Waste heat factor due to lighting interaction with space cooling system demand | [11 empty] | Varies |  |  |  | - |  | See Equation 7; applicable to lighting installed in locations with space cooling
WHC,E |  |  |  | Waste heat factor due to lighting interaction with space cooling system energy use | [11 empty] | Varies |  |  |  | - |  | See Equation 8; applicable to lighting installed in locations with space cooling
%Cool |  |  |  | Share of homes with electric cooling | [11 empty] | See Table 2 |  |  |  | - |  | 2019 Hawaii Statewide Baseline Energy Use Study1
%Int |  |  |  | Share of interior light bulbs | [11 empty] | 85% |  |  |  | - |  | DOE 2012 Residential Lighting End-Use Consumption Study2
IEC,D |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting | [11 empty] | 1.3 |  |  |  | - |  | AEG's Hawai‘i-specific simulation modeling
IEC,E |  |  |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting | [11 empty] | 1.35 |  |  |  | - |  | AEG's Hawai‘i-specific simulation modeling
PF | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 1 | 0.96 | 0.96 | 0.96 | - |  | Footnote 3
EULLED | Measure Life | Measure Life | Measure Life | Effective useful life of LED | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | See Table 2 | 0.12 | 0.12 | 0.12 | yrs |  | Based on average lamp life of 15,000 hours 4
RUL | Measure Life | Measure Life | Measure Life | Remaining useful life of baseline lamp | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | See Table 2 | 0.12 | 0.12 | 0.12 | yrs |  | Based on average lamp life of 9,000 hours for a CFL 4
1 2019 Hawaii Statewide Baseline Energy Use Study, Final Report, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020, Figure 3-9.
2 Residential Lighting End-Use Consumption Study: Estimation Framework and Initial Estimates, Prepared by DNV KEMA Energy and Sustainability, Pacific Northwest National Laboratory, Prepared for Solid-State Lighting Program, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, U.S. Department of Energy, December 2012. Table 4.4 shows that 15% of CFLs are installed in garages and exterior locations. AEG assumes CFLs are reasonable proxy for LEDs.
3 Use value of PF=1 until more data is available on PF of LEDs relative to new EISA Tier 2 baseline (CFL).
4 Sources of rated lamp life include DEER2020 and other benchmarking.
Table 1. Baseline and Energy Efficient Wattages
| Traditional Incandescent Equivalent (W) |  |  |  |  | EISA Lumen Bin |  |  |  |  | EISA Tier 2 Baseline1 (kWbase) |  |  |  |  | Average Omni-directional LED2 (kWLED) |  |  |  |  | % Breakdown by Wattage2
| 40 |  |  |  |  | 310 - 749 lm |  |  |  |  | 0.012 |  |  |  |  | 0.006 |  |  |  |  | 6%
| 60 |  |  |  |  | 750 - 1049 lm |  |  |  |  | 0.02 |  |  |  |  | 0.008 |  |  |  |  | 57%
| 75 |  |  |  |  | 1050 - 1489 lm |  |  |  |  | 0.028 |  |  |  |  | 0.013 |  |  |  |  | 29%
| 100 |  |  |  |  | 1490 - 2600 lm |  |  |  |  | 0.045 |  |  |  |  | 0.017 |  |  |  |  | 8%
| Weighted average (default) | [9 empty] | 0.02384 |  |  |  |  | 0.01005 |  |  |  |  | -
1 EISA Tier 2 wattages area calculated based on 45 lumen/W and midpoint of lumen range
2 LED wattages and % breakdowns by lighting type are from actual Hawai‘i Energy Program Data (per description in PY15-PY18 TRMs)
Table 2. Key Parameters for Non-Military and Military Homes
[6 empty] | CF |  |  |  |  | %Cool |  |  |  |  | HOU1 |  |  |  |  | EULLED |  |  | RUL
| Non-Military |  |  |  |  | 0.16 |  |  |  |  | 48% |  |  |  |  | 2.3 |  |  |  |  | 18 |  |  | 4
| Military |  |  |  |  | 0.24 |  |  |  |  | 100% |  |  |  |  | 3.5 |  |  |  |  | 12
1 Per the approach in previous versions of the Hawai‘i TRM, the Non-Military HOU has been multiplied by a factor of 1.5 to obtain the Military HOU .
SAVINGS
Original Set of Savings: Applicable through Dec. 31, 2024 for REEM, and through Jun. 30, 2025 for ES4H
Deemed Savings (based on default values for wattages)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
LED (non-military) | [7 empty] | 0.002 | [7 empty] | 12.83 | [6 empty] | 230.94
LED (military) | [7 empty] | 0.004 | [7 empty] | 22.17 | [6 empty] | 266.04
Semi-Prescriptive Savings Calculator (based on equivalent traditional incandescent wattage)
Enter Equivalent Incandescent Wattage
|  |  | 60 | [9 empty] | kWbase= |  |  | 0.02 |  |  |  |  | kWLED= |  | 0.008
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
LED (non-military) | [7 empty] | 0.002 | [7 empty] | 11.17 | [6 empty] | 201.06
LED (military) | [7 empty] | 0.004 | [7 empty] | 19.29 | [6 empty] | 231.48
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
New Set of Savings: Applicable Jul. 1, 2025 through Jun. 30, 2029 (PY25-PY28) for ES4H only:
Deemed Savings (based on default values for wattages)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
LED (non-military) | [7 empty] | 0.002 | [7 empty] | 12.83 | [6 empty] | 51.32
Semi-Prescriptive Savings Calculator (based on equivalent traditional incandescent wattage)
Enter Equivalent Incandescent Wattage
|  |  | 60 | [9 empty] | kWbase= |  |  | 0.02 |  |  |  |  | kWLED= |  | 0.008
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
LED (non-military) | [7 empty] | 0.002 | [7 empty] | 11.17 | [6 empty] | 44.68
Note: Savings in blue result from the sample entry above. They are for illustrative purposes only.
RESOURCES
• | ICF's 2025 Analysis File named "Mid-Year PY24 TRM - Residential Lighting - Analysis File."
• | AEG's 2024 Analysis File named "PY24 TRM - Residential LED Lighting - Analysis File."
• | AEG's 2022 Analysis Files named "Mid-year PY22 TRM - LED Retrofit Kit Language - Analysis File" and "Mid-year PY22 TRM - Molokai-Lanai LED Updates - Analysis File."
• | AEG's 2020 Analysis File named "AEG HPUC - PY20 v2.0 Lighting Baselines - Analysis." AEG's 2018 Analysis Files titled "AEG HPUC Update of Residential Measures - Analysis file" and "HI - Res Lighting IEF Analysis."
• | Recommendations for Addressing EISA in the Potential Study and PY20 TRM, Memorandum, Prepared by AEG, Submitted to EEM and HPUC, January 26, 2020.
• | 2019 Hawaii Statewide Baseline Energy Use Study, Final Report, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | AEG's 2018 Hawai‘i-specific building energy simulations of single family home prototypes in BEopt™ with EnergyPlus v8.8 as the simulation engine. Used Hawai‘i weather data and developed prototypes based on a mixture of assumptions from the 2014 State of Hawai‘i Baseline Report, 2014 Building America House Simulation Protocols, and building characteristics from a survey of suburban homes in Google Maps. Homes were simulated with a variety of HVAC system types and four different lighting consumption levels. House leakage was also varied to vary the efficiency of the home. AEG used the analysis to determine coincidence factors (CFs), as well as interactive effects factors (IEFs) that account for cooling demand and energy savings due to reducing waste heat with efficient lighting.
• | Arkansas Technical Reference Manual, Version 7.0, Arkansas Public Service Commission, 2017.
• | Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, November 6, 2013, With errata February 26, 2014, Evergreen Economics.
• | California Public Utilities Commission (CPUC), DEER2020, Ex Ante database Support Table Export, EUL_basis, 1/1/2013 - 1/1/2021, available here: http://www.deeresources.com.
• | Connecticut's 2018 Program Savings Document, 13th Edition, filed December 15, 2017.
• | Hawai‘i PUC LED Baseline Memo, Opinion Dynamics, April 9, 2018.
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0, Volume 3: Residential Measures, FINAL, Feb. 8, 2017.
• | Lighting Research Center, Publications, 061Incandescent, page 114, Halogen A, https://www.lrc.rpi.edu/resources/publications/lpbh/061Incandescent.pdf, accessed 11/7/2018.
• | Mid-Atlantic Technical Reference Manual, Version 8, Final, May 2018.
• | National Renewable Energy Laboratory. Building Energy Optimization (BEopt) Software. Version 2.8.0.0. U.S. Department of Energy. January 2018. Available at: https://beopt.nrel.gov/.
• | New Mexico Technical Resource Manual for the Calculation of Energy Efficiency Savings, 2016.
• | Public Utility Commission of Texas, Texas Technical Reference Manual, Version 5.0, Volume 2: Residential Measures, Program Year (PY) 2018, October 2017.
• | Regional Technical Forum. Residential Lighting - Unit Energy Savings Workbook, Version 6.1 (ResLighting_v6_1). Northwest Power and Conservation Council. April 4, 2018. Spreadsheet.
• | Regulatory Advisory Appliance Efficiency Regulations for Lamps: Effective Dates, California Energy Commission, 2017.
• | Residential Lighting End-Use Consumption Study: Estimation Framework and Initial Estimates, Prepared by DNV KEMA Energy and Sustainability, Pacific Northwest National Laboratory, Prepared for Solid-State Lighting Program, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, U.S. Department of Energy, December 2012, Table 4.4.
• | Rhode Island Technical Reference Manual – 2018 Program Year, National Grid, 2017.
• | RLPNC Study 17-9, 2017-18 Residential Lighting Market Assessment Study, Submitted to the Electric and Gas Program Administrators of Massachusetts, Submitted by NMR Group, March 28, 2018. Table 14, page 38.
• | State of Minnesota, Technical Reference Manual for Energy Conservation Improvement Programs, Version 2.2, May 2, 2018.
• | State of Pennsylvania Technical Reference Manual, Pennsylvania Public Utilities Commission, June 2016.
• | Tennessee Valley Authority Technical Reference Manual, Version 6.0, Oct. 1, 2017.
• | Uniform Methods Project, Chapter 6: Residential Lighting Evaluation Protocol, S. Dimetrosky, K. Parkinson, and N. Lieb, Apex Analytics, C. Kurnik, National Renewable Energy Laboratory, October 2017.
• | U.S. Department of Energy, Final Rulings, May 9, 2022, Federal Register 87FR27461 and 87FR27439, available here: <https://www.federalregister.gov/>.
• | Wilson, E. et. al., 2014 Building America House Simulation Protocols. National Renewable Energy Laboratory. March 2014. Available at: https://www.nrel.gov/docs/fy14osti/60988.pdf.
kW
∆kWℎ=(〖𝑘𝑊〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊〗_𝐿𝐸𝐷 )∗𝐼𝑆𝑅∗𝐻𝑂𝑈∗365𝑑𝑎𝑦/𝑦𝑟∗(1+〖𝑊𝐻〗_(𝐶,𝐸) )∗𝑃𝐹
kW
∆kW =(〖𝑘𝑊〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊〗_𝐿𝐸𝐷 )∗𝐼𝑆𝑅∗𝐶𝐹∗(1+〖𝑊𝐻〗_(𝐶,𝐷) )∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒𝑡𝑖𝑚𝑒 = ∆"kW" ℎ∗〖𝐸𝑈𝐿〗_𝐿𝐸𝐷
〖𝑊𝐻〗_(𝐶,𝐷)=%_𝐶𝑜𝑜𝑙∗%_𝐼𝑛𝑡∗(〖𝐼𝐸〗_(𝐶,𝐷)−1)
〖𝑊𝐻〗_(𝐶,𝐸)=%_𝐶𝑜𝑜𝑙∗%_𝐼𝑛𝑡∗(〖𝐼𝐸〗_(𝐶,𝐸)−1)
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒𝑡𝑖𝑚𝑒 = ∆"kW" ℎ∗𝑅𝑈𝐿

## R_Light_Occupancy Sensor
RESIDENTIAL: Lighting Occupancy Sensor
Return to TOC
UPDATE STATUS
Updated in Fall 2020 for PY20 TRM v2.0. Continue to follow EISA GSL legislation and update the measure entry as needed.
MEASURE DETAILS
Description
This measure is for wall switch sensors that control the use of lighting in areas around the home with variable use, such as laundry, storage, garage, bedrooms or spare areas. The default deemed savings approach assumes each occupancy sensor controls two omni-directional lamps in a non-military home. A semi-prescriptive savings calculator is also provided to allow custom entry of the controlled wattage.
Program Criteria
This measure is applicable to both the REEM and RHTR programs.
All types of wall switch sensors (e.g. infrared, ultrasonic) are eligible.
The occupancy sensors must be UL listed.
Unit of Measure
One unit.
Baseline Equipment
The default deemed base case is assumed to be two omni-directional lightbulbs in operation 2.3 hours per day. The default deemed measure has a dual baseline for PY20 and PY21. The first baseline is two omni-directional halogen-incandescent lamps that comply with Energy Independence and Securities Act (EISA) 2007 legislation that had 2012-2014 effective dates (EISA Tier 1). The second baseline is two lamps that comply with the original EISA Tier 2 Backstop requirement of 45 lumens per Watt. For PY22 and later, there is a single baseline (EISA Tier 2).
The semi-prescriptive calculator allows custom entry of the wattage controlled by the occupancy sensor. However, to use the semi-prescriptive calculator, the efficacy of the controlled lighting must meet or exceed the EISA Tier 2 Backstop requirement of 45 lumens per Watt. For example, LEDs, CFLs, and T5 or T8 fluorescent lamps would all be eligible for the semi-prescriptive calculator, but incandescent and halogen bulbs would not be.
High Efficiency Equipment
The enhanced case is assumed to be the same base case lamps in operation with a 30% reduction in runtime.
ALGORITHMS
First Baseline Peak Demand Reduction, kW
(1)
Second Baseline Peak Demand Reduction, kW
(2)
First Baseline Annual Energy Savings, kWh/yr
(3)
Second Baseline Annual Energy Savings, kWh/yr
(4)
Lifetime Energy Savings, kWh (Applicable through PY21)
(5)
Lifetime Energy Savings, kWh (Applicable to PY22 and later)
(6)
Waste Heat Factors due to Interaction with Space Cooling System
(7)
(8)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit | Source/Notes
kWctrl,1 | kW_b | kW_b | kW_b | EISA Tier 1 Wattage; two (2) 43W bulbs | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | 0.086 | see Table 1 | see Table 1 | see Table 1 | kW | EISA legislation, effective dates of 2012-2014
kWctrl,2 | kW_b | kW_b | kW_b | EISA Tier 2 Wattage; two (2) 20W bulbs (Wattage calculated using middle of 750 - 1049 lm range) | [11 empty] | 0.04 | see Table 1 | see Table 1 | see Table 1 | kW | Original EISA backstop
RTR |  |  |  | Runtime reduction factor from sensor | [11 empty] | 0.3 |  |  |  | - | AEG's Fall 2018 Benchmarking; median of 6 sources
ISR |  |  |  | Lifetime in-service rate | [11 empty] | 0.97 |  |  |  | - | AEG's Fall 2018 Benchmarking
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0.16 | 0.12 | 0.12 | 0.12 | - | AEG's Hawai‘i-specific simulation modeling; non-military home 1
HOU |  |  |  | Average hours of use per day | [11 empty] | 2.3 | 0.12 | 0.12 | 0.12 | hr/day | No change from PY18 TRM; non-military home
WHC,D |  |  |  | Waste heat factor due to lighting interaction with space cooling system demand | [11 empty] | Varies |  |  |  | - | See Equation 7; applicable to lighting installed in locations with space cooling
WHC,E |  |  |  | Waste heat factor due to lighting interaction with space cooling system energy use | [11 empty] | Varies |  |  |  | - | See Equation 8; applicable to lighting installed in locations with space cooling
%Cool |  |  |  | Share of homes with electric cooling | [11 empty] | 48% |  |  |  | - | 2019 Hawaii Statewide Baseline Energy Use Study; non-military home 2
%Int |  |  |  | Share of interior light bulbs | [11 empty] | 85% |  |  |  | - | DOE 2012 Residential Lighting End-Use Consumption Study 3
IEC,D |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting | [11 empty] | 1.3 |  |  |  | - | AEG's Hawai‘i-specific simulation modeling
IEC,E |  |  |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting | [11 empty] | 1.35 |  |  |  | - | AEG's Hawai‘i-specific simulation modeling
PF | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 1 | 0.96 | 0.96 | 0.96 | - | Assumes that savings persistence is accounted for in the EUL
EUL1st |  |  |  | Effective useful life of 1st baseline lamps | [11 empty] | PY20 |  | PY21 |  | yrs | Length of first baseline period. Based on rated lamp life and HOU. Assumes existing EISA Tier 1 lamps have 1/3 of life left upon installation of sensor. 4
[16 empty] | 4 |  | 1
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of occupancy sensor | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 8 | 0.12 | 0.12 | 0.12 | yrs | AEG's Fall 2018 Benchmarking
1 This approach assumes that the occupancy pattern during 5-9 pm is consistent with rest of day.
2 2019 Hawaii Statewide Baseline Energy Use Study, Final Report, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020, Figure 3-9.
3 Residential Lighting End-Use Consumption Study: Estimation Framework and Initial Estimates, Prepared by DNV KEMA Energy and Sustainability, Pacific Northwest National Laboratory, Prepared for Solid-State Lighting Program, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, U.S. Department of Energy, December 2012. Table 4.4 shows that 15% of CFLs are installed in garages and exterior locations. AEG assumes CFLs are reasonable proxy for LEDs.
4 The first baseline period (EUL1st) for PY20 assumes the existing EISA Tier 1 baseline lamps will need to be replaced once prior to the EISA Tier 2 baseline taking effect on June 30, 2022, while the first baseline period for PY21 assumes the EISA Tier 1 lamps will not reach the end of their useful life until after June 30, 2022.
DEEMED SAVINGS (APPLICABLE FOR PY20 AND PY21)
Deemed Savings (based on default values for wattage) - Dual Baseline
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
[8 empty] | 1st BL |  |  |  | 2nd BL |  |  |  | 1st BL |  |  |  | 2nd BL |  | PY20 | PY21
Residential Lighting Occupancy Sensor | [7 empty] | 0.004 |  |  |  | 0.002 |  |  |  | 24.01 |  |  |  | 11.17 |  | 140.72 | 102.2
DEEMED SAVINGS (APPLICABLE FOR PY22 AND LATER)
Deemed Savings (based on default values for wattage) - Single Baseline
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Residential Lighting Occupancy Sensor | [7 empty] | 0.002 | [7 empty] | 11.17 | [5 empty] | 89.36
Note: For PY22 and later, controlled lighting is assumed to meet EISA Tier 2 efficacy.
SEMI-PRESCRIPTIVE SAVINGS
Semi-Prescriptive Savings Calculator (based on user input wattage for energy efficient lamps)
Does the efficacy of the lamps controlled by the occupancy sensor meet or exceed 45 lumen/W? (For example, are they LEDs, CFLs, T5 or T8 lamps?)
Yes
Enter Total Wattage Controlled by Occupancy Sensor in Watts
40
Are the lamps installed in an air-conditioned space?
No
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Residential Lighting Occupancy Sensor | [7 empty] | 0.002 | [7 empty] | 9.77 | [5 empty] | 78.16
RESOURCES
• | AEG's 2020 Analysis File titled "AEG HPUC - PY20 v2.0 Lighting Baselines - Analysis." AEG's 2018 Analysis Files titled "AEG HPUC Update of Residential Measures - Analysis file" and "HI - Res Lighting IEF Analysis."
• | Recommendations for Addressing EISA in the Potential Study and PY20 TRM, Memorandum, Prepared by AEG, Submitted to EEM and HPUC, January 26, 2020.
• | 2019 Hawaii Statewide Baseline Energy Use Study, Final Report, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | AEG's 2018 Hawai‘i-specific building energy simulations of single family home prototypes in BEopt™ with EnergyPlus v8.8 as the simulation engine. Used Hawai‘i weather data and developed prototypes based on a mixture of assumptions from the 2014 State of Hawai‘i Baseline Report, 2014 Building America House Simulation Protocols, and building characteristics from a survey of suburban homes in Google Maps. Homes were simulated with a variety of HVAC system types and four different lighting consumption levels. House leakage was also varied to vary the efficiency of the home. AEG used the analysis to determine coincidence factors (CFs), as well as interactive effects factors (IEFs) that account for cooling demand and energy savings due to reducing waste heat with efficient lighting.
• | Arkansas Technical Reference Manual, Version 7.0, Arkansas Public Service Commission, 2017.
• | Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, November 6, 2013, With errata February 26, 2014, Evergreen Economics.
• | Connecticut's 2018 Program Savings Document, 13th Edition, filed December 15, 2017.
• | Illinois Statewide Technical Reference Manual for Energy Efficiency, Version 6.0, Volume 3: Residential Measures, FINAL, Feb. 8, 2017.
• | Lighting Research Center, Publications, 061Incandescent, page 114, Halogen A, https://www.lrc.rpi.edu/resources/publications/lpbh/061Incandescent.pdf, accessed 11/7/2018.
• | Massachusetts Technical Reference Manual, 2016-2018 Program Years, October 2015.
• | Mid-Atlantic Technical Reference Manual, Version 8, Final, May 2018.
• | National Renewable Energy Laboratory. Building Energy Optimization (BEopt) Software. Version 2.8.0.0. U.S. Department of Energy. January 2018. Available at: https://beopt.nrel.gov/.
• | New Mexico Technical Resource Manual for the Calculation of Energy Efficiency Savings, 2016.
• | Public Utility Commission of Texas, Texas Technical Reference Manual, Version 5.0, Volume 2: Residential Measures, Program Year (PY) 2018, October 2017.
• | Regional Technical Forum. Residential Lighting - Unit Energy Savings Workbook, Version 6.1 (ResLighting_v6_1). Northwest Power and Conservation Council. April 4, 2018. Spreadsheet.
• | Residential Lighting End-Use Consumption Study: Estimation Framework and Initial Estimates, Prepared by DNV KEMA Energy and Sustainability, Pacific Northwest National Laboratory, Prepared for Solid-State Lighting Program, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, U.S. Department of Energy, December 2012, Table 4.4.
• | Rhode Island Technical Reference Manual – 2018 Program Year, National Grid, 2017.
• | State of Minnesota, Technical Reference Manual for Energy Conservation Improvement Programs, Version 2.2, May 2, 2018.
• | State of Pennsylvania Technical Reference Manual, Pennsylvania Public Utilities Commission, June 2016.
• | Tennessee Valley Authority Technical Reference Manual, Version 6.0, Oct. 1, 2017.
• | Wilson, E. et. al., 2014 Building America House Simulation Protocols. National Renewable Energy Laboratory. March 2014. Available at: https://www.nrel.gov/docs/fy14osti/60988.pdf.
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=〖𝑘𝑊〗_(𝑐𝑡𝑟𝑙,1)∗𝑅𝑇𝑅∗𝐼𝑆𝑅∗𝐻𝑂𝑈∗365𝑑𝑎𝑦/𝑦𝑟∗(1+〖𝑊𝐻〗_(𝐶,𝐸) )∗𝑃𝐹
〖∆𝑘𝑊〗_1𝑠𝑡=〖𝑘𝑊〗_(𝑐𝑡𝑟𝑙,1)∗𝑅𝑇𝑅∗𝐼𝑆𝑅∗𝐶𝐹∗(1+〖𝑊𝐻〗_(𝐶,𝐷) )∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_𝐷𝑢𝑎𝑙=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗〖𝐸𝑈𝐿〗_1𝑠𝑡+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(〖𝐸𝑈𝐿〗_𝐸𝐸−〖𝐸𝑈𝐿〗_1𝑠𝑡 )
〖∆𝑘𝑊ℎ〗_(𝑃𝑌22+)=〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗〖𝐸𝑈𝐿〗_𝐸𝐸
〖∆𝑘𝑊〗_2𝑛𝑑=〖𝑘𝑊〗_(𝑐𝑡𝑟𝑙,2)∗𝑅𝑇𝑅∗𝐼𝑆𝑅∗𝐶𝐹∗(1+〖𝑊𝐻〗_(𝐶,𝐷) )∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=〖𝑘𝑊〗_(𝑐𝑡𝑟𝑙,2)∗𝑅𝑇𝑅∗𝐼𝑆𝑅∗𝐻𝑂𝑈∗365𝑑𝑎𝑦/𝑦𝑟∗(1+〖𝑊𝐻〗_(𝐶,𝐸) )∗𝑃𝐹
〖𝑊𝐻〗_(𝐶,𝐷)=%_𝐶𝑜𝑜𝑙∗%_𝐼𝑛𝑡∗(〖𝐼𝐸〗_(𝐶,𝐷)−1)
〖𝑊𝐻〗_(𝐶,𝐸)=%_𝐶𝑜𝑜𝑙∗%_𝐼𝑛𝑡∗(〖𝐼𝐸〗_(𝐶,𝐸)−1)

## R_Light_Linear LED
RESIDENTIAL: Linear LED
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. This update revises the deemed savings values for direct install linear LED lighting through the Energy Smart for Homes (ES4H) program, which supports Accessibility & Affordability (A&A) customers. (The previous REEM portion of the measure reached its sunset date at the end of PY25.)
MEASURE DETAILS
Description
Replacement of linear 4-ft fluorescent lamps with linear LED lamps.
This measure is only applicable to direct install linear LED lighting implemented through the ES4H program, which allows for early replacement of pre-existing linear fluorescent lamps. The REEM portion of this measure reached its sunset date at the end of PY25 due to Hawaii's linear fluorescent lighting ban, which became effective on January 1, 2026.
Program Criteria
Efficient equipment must be Design Light Consortium (DLC) listed.
Unit of Measure
One lamp.
Baseline Equipment
General service linear: One-lamp 4' F32T8 fixture with electronic ballast.
Shop light: Two-lamp 4' F32T8 fixture with electronic ballast.
The lifetime savings use the remaining useful life (RUL) of the pre-existing linear fluorescent lighting. After the RUL, the baseline would transition to linear LED lighting, so there would be no savings during the second baseline period. Savings are only applicable to direct installation through ES4H.
High Efficiency Equipment
General service linear: One (1) 4' T8 LED with Type A, Type B, or Type C installation.*
| • | Type A installation: Ballast left in place; reduced savings due to losses.
| • | Type B installation: Bypassing fluorescent ballast and utilizing internal LED driver.
| • | Type C installation: Removing fluorescent ballast and utilizing an external driver.
*Note: Based on the original program design, installations through the direct install ES4H program are typically Type A. However, deemed savings for all options are included to keep the measure entry as generally applicable as possible in case there are any Type B or Type C installations.
Shop light: One (1) 4' Integrated LED light with equivalent lumen output to a two-lamp 4' F32T8 fixture.
As an alternative to more traditional LED bulbs or tubes, LED retrofit kit engines qualify as applicable LED replacement lighting, as long as the LED retrofit kit engines have appropriate form factors compared to the baseline lighting.
ALGORITHMS
Peak Demand Reduction, kW
(1)
First Baseline Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
Waste Heat Factors due to Interaction with Space Cooling System
(4)
(5)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  | Source/Notes
Wbase | kW_b | kW_b | kW_b | Baseline Wattage | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | See Table 1 |  |  |  | W |  | Appendix B SFW, per lamp averages across fixture types.
WLED | kW_led | kW_led | kW_led | LED Wattage | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | See Table 1 |  |  |  | W |  | Typical values from retailers.
ISR |  |  |  | Lifetime in-service rate | [11 empty] | 0.97 |  |  |  | - |  | AEG's Fall 2018 Benchmarking for Residential LED measure.1
%Cool |  |  |  | General service linear: Share of lamps installed in spaces with electric cooling | [11 empty] | 0.48 |  |  |  | - |  | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Derived from Figure 3-9.
|  |  |  | Shop light: Share of lamps installed in spaces with electric cooling | [11 empty] | 0 |  |  |  | - |  | Assumes shop lights are installed in unconditioned shops and garages.
IEC,D |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting | [11 empty] | 1.3 |  |  |  | - |  | AEG's Hawai‘i-specific simulation modeling.
IEC,E |  |  |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting | [11 empty] | 1.35 |  |  |  | - |  | AEG's Hawai‘i-specific simulation modeling.
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | See Table 1 |  |  |  | - |  | AEG's Hawai‘i-specific simulation modeling. 2
HOU |  |  |  | Annual hours of use | [11 empty] | See Table 1 |  |  |  | hrs |  | Derived from DOE 2012 Residential Lighting End-Use Consumption Study. 4
PF 3 | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 1 | 0.96 | 0.96 | 0.96 | -
RUL | Measure Life | Measure Life | Measure Life | Remaining useful life of baseline lamp | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | See Table 1 |  |  |  | yrs |  | RUL = 1/3 * Lamp Life / HOU, rounded to the nearest year. Based on typical lamp life of 24,000 hours for linear fluorescent lamps, from DEER 20205 and other benchmarking.
1 AEG's ISR benchmarking was done specifically for the Residential LED measure, which applies to omnidirectional LED bulbs. Until further research can be carried out for linear LEDs, assume the ISRs for both measures would be similar.
2 CF for general service linear assumes non-military home (CF=0.16). CF for shop light measure was reduced by 25% relative to general lighting value as a conservative assumption (CF=0.12).
3 Use value of PF=1 until more data is available on PF of LEDs.
4 Residential Lighting End-Use Consumption Study: Estimation Framework and Initial Estimates, Prepared by DNV KEMA Energy and Sustainability, Pacific Northwest National Laboratory, Prepared for Solid-State Lighting Program, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, U.S. Department of Energy (DOE), December 2012, https://www1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf, Table 4.4. Inside homes, general service linear lamps are most often installed in kitchens and offices; AEG calculated a weighted average of 2.2 hours per day using kitchen and office data from Table 4.4 of the DOE report. In addition, AEG used the "Garage" value of 1.1 hours per day for shop lights from Table 4.4.
5 California Public Utilities Commission (CPUC), DEER2020, Ex Ante database Support Table Export, EUL_basis, 1/1/2013 - 1/1/2021, https://cedars.cpuc.ca.gov/deer-resources/deer-versions/2020/.
Table 1: Key Parameters
| Measure Name | [7 empty] | Wbase |  |  |  | WLED |  |  |  | HOU |  |  |  | CF |  |  | RUL
| Linear LED, Type A | [7 empty] | 31 |  |  |  | 18 |  |  |  | 803 |  |  |  | 0.16 |  |  | 10
| Linear LED, Type B or Type C | [7 empty] | 31 |  |  |  | 16 |  |  |  | 803 |  |  |  | 0.16 |  |  | 10
| Shop Light | [7 empty] | 62 |  |  |  | 32 |  |  |  | 402 |  |  |  | 0.12 |  |  | 20
SAVINGS
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Linear LED, Type A (Use if type is unknown) | [7 empty] | 0.002 | [7 empty] | 11.83 | [6 empty] | 118.3
Linear LED, Type B or C | [7 empty] | 0.003 | [7 empty] | 13.65 | [6 empty] | 136.5
Shop Light | [7 empty] | 0.003 | [7 empty] | 11.7 | [6 empty] | 234
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Multiple Lighting Measures - Analysis File."
• | AEG's 2022 Analysis File named "Mid-year PY22 TRM - LED Retrofit Kit Language - Analysis File."
• | AEG's 2020 Analysis File named "AEG HPUC Baseline Study Data - Analysis File."
• | AEG's 2019 Analysis File named "PY19 TRM - Residential Additions - Draft_20191113 AEG reviewed."
• | AEG's 2018 Analysis Files named "AEG HPUC Update of Residential Measures - Analysis file" and "HI - Res Lighting IEF Analysis."
• | AEG's 2018 Analysis File named "AEG HPUC Update of Com-Lighting Measures - Analysis file."
• | AEG's 2018 Hawai‘i-specific building energy simulations of single family home prototypes in BEopt™ with EnergyPlus v8.8 as the simulation engine. Used Hawai‘i weather data and developed prototypes based on a mixture of assumptions from the 2014 State of Hawai‘i Baseline Report, 2014 Building America House Simulation Protocols, and building characteristics from a survey of suburban homes in Google Maps. Homes were simulated with a variety of HVAC system types and four different lighting consumption levels. House leakage was also varied to vary the efficiency of the home. AEG used the analysis to determine coincidence factors (CFs), as well as interactive effects factors (IEFs) that account for cooling demand and energy savings due to reducing waste heat with efficient lighting.
• | California Public Utilities Commission (CPUC), DEER2020, Ex Ante database Support Table Export, EUL_basis, 1/1/2013 - 1/1/2021, https://cedars.cpuc.ca.gov/deer-resources/deer-versions/2020/.
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | Residential Lighting End-Use Consumption Study: Estimation Framework and Initial Estimates, Prepared by DNV KEMA Energy and Sustainability, Pacific Northwest National Laboratory, Prepared for Solid-State Lighting Program, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, U.S. Department of Energy, December 2012, https://www1.eere.energy.gov/buildings/publications/pdfs/ssl/2012_residential-lighting-study.pdf, Table 4.4.
• | 2016 Statewide Customized Offering Procedures Manual for Business. Appendix B: Table of Standard Fixture Wattages. July 2014, Version 6.0.
∆𝑘𝑊ℎ=((𝑊_𝑏𝑎𝑠𝑒−𝑊_𝐿𝐸𝐷 ))/(1,000 𝑊/𝑘𝑊)∗𝐼𝑆𝑅∗𝐻𝑂𝑈∗(1+〖𝑊𝐻〗_(𝐶,𝐸) )∗𝑃𝐹
∆𝑘𝑊=((𝑊_𝑏𝑎𝑠𝑒−𝑊_𝐿𝐸𝐷 ))/(1,000 𝑊/𝑘𝑊)∗𝐼𝑆𝑅∗𝐶𝐹∗(1+〖𝑊𝐻〗_(𝐶,𝐷) )∗𝑃𝐹
∆𝑘𝑊ℎ=∆𝑘𝑊ℎ∗𝑅𝑈𝐿
〖𝑊𝐻〗_(𝐶,𝐷)=%_𝐶𝑜𝑜𝑙∗(〖𝐼𝐸〗_(𝐶,𝐷)−1)
〖𝑊𝐻〗_(𝐶,𝐸)=%_𝐶𝑜𝑜𝑙∗(〖𝐼𝐸〗_(𝐶,𝐸)−1)

## R_Light_Security Light
RESIDENTIAL: Security Light
Return to TOC
UPDATE STATUS
Updated in Spring 2026 for the PY26 TRM. This update revises the deemed savings values for direct install LED lighting through the Energy Smart for Homes (ES4H) program, which supports Accessibility & Affordability (A&A) customers. The revised ES4H savings values are applicable only for PY26, with a sunset date of June 30, 2027. (The previous REEM portion of the measure reached its sunset date on December 31, 2024.)
MEASURE DETAILS
Description
Replacement of an EISA-compliant exterior security/porch light fixture with an LED-based fixture.
This measure is only applicable to direct install LED lighting implemented through the ES4H program. The sunset date for ES4H implementation is June 30, 2027, which is the end of PY26. The REEM portion of this measure reached its sunset date on December 31, 2024 due to Hawaii's CFL ban. The extra time for the ES4H portion of the measure allows for early replacement of pre-existing CFLs, which have an RUL of one year in outdoor security applications.
Program Criteria
Efficient equipment must be ENERGY STAR certified.
Unit of Measure
One fixture.
Baseline Equipment
This baseline approach applies the expanded GSL definition and Tier 2 backstop of 45 lumens per Watt reinstated by the U.S. Department of Energy in final rulings published on May 9, 2022 (Federal Register 87FR27461 and 87FR27439). It includes two types of outdoor lighting:
| ● | Security Lights: Two (2) PAR38 EISA-compliant flood lights rated at 45 lumens/Watt; savings assume an average of 1080 lumens for each bulb (or 24 W)
| ● | Porch Lights: One (1) Omni-directional A19 EISA-compliant bulb rated at 45 lumens/Watt; savings assume an average of 1080 lumens per bulb (or 24 W)
The lifetime savings use the remaining useful life (RUL) of pre-existing lighting, which is assumed to be compact fluorescent lamp(s). After the RUL, the baseline would transition to LED(s), so there would be no savings during the second baseline period. Savings are only applicable to direct installation through ES4H, and savings are only valid for PY26.
High Efficiency Equipment
| ● | Security Lights: Two (2) PAR38 ENERGY STAR LEDs; savings assume an average of 1080 lumens for each bulb
| ● | Porch Lights: One (1) Omni-directional A19 ENERGY STAR LED; savings assume an average of 1080 lumens per bulb
As an alternative to more traditional LED bulbs or tubes, LED retrofit kit engines qualify as applicable LED replacement lighting, as long as the LED retrofit kit engines have appropriate form factors compared to the baseline lighting.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit | Source/Notes
Wbase | kW_b | kW_b | kW_b | Baseline Wattage | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | See Table 1 |  |  |  | W | Wattages assume an average of 1080 lumens per bulb and an efficacy of 45 lumens/Watt (or 24 W)
WLED | kW_led | kW_led | kW_led | LED Wattage | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | See Table 1 |  |  |  | W | Typical values from retailers for bulbs rated at (or near) 1080 lumens.
ISR |  |  |  | Lifetime in-service rate | [11 empty] | 0.97 |  |  |  | - | AEG's Fall 2018 Benchmarking for Residential LED measure.1
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0.62 |  |  |  | - | AEG's analysis of average annual sunset time in Honolulu (6:32 PM) and overlap with the 5-9 PM peak demand period.
HOU |  |  |  | Annual hours of use | [11 empty] | 2475 |  |  |  | hrs | 2026 Illinois Statewide TRM.3 Based on lighting logger study conducted as part of the PY5/6 ComEd Residential Lighting Program evaluation.
PF 2 | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 1 | 0.96 | 0.96 | 0.96 | -
RUL | Measure Life | Measure Life | Measure Life | Remaining useful life of baseline lamp | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | See Table 1 |  |  |  | yrs | RUL = 1/3 * Lamp Life / HOU, rounded to the nearest year. Based on rated lamp life for CFL products.
1 AEG's ISR benchmarking was done specifically for the Residential LED measure, which applies to omnidirectional LED bulbs. Until further research can be carried out for PAR38 LEDs, assume the ISRs for both measures would be similar.
2 Use value of PF=1 until more data is available on PF of LEDs.
3 2026 Illinois Statewide Technical Reference Manual, v14.0, Vol. 3: Residential Measures, Sep. 19, 2025, pg. 383.
Table 1: Wattages and Lifetime Information
Measure Name | [7 empty] | Wbase |  |  |  | WLED |  |  |  | Rated Lamp Life (hrs) |  |  |  | RUL
Security Light (2 bulbs) | [7 empty] | 48 |  |  |  | 26 |  |  |  | 10000 |  |  |  | 1
Porch Light (1 bulb) | [7 empty] | 24 |  |  |  | 10 |  |  |  | 9000 |  |  |  | 1
SAVINGS (This measure has a sunset date of June 30, 2027)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Security Light | [7 empty] | 0.013 | [7 empty] | 52.82 | [5 empty] | 52.82
Porch Light | [7 empty] | 0.008 | [7 empty] | 33.61 | [5 empty] | 33.61
RESOURCES
• | ICF's 2026 Analysis File named "PY26 TRM - Multiple Lighting Measures - Analysis File."
• | AEG's 2024 Analysis File named "PY24 TRM - Residential Security Light - Analysis File."
• | AEG's 2022 Analysis File named "Mid-year PY22 TRM - LED Retrofit Kit Language - Analysis File."
• | AEG's 2020 Analysis file named "AEG HPUC - PY20 v2.0 Lighting Baselines - Analysis."
• | Recommendations for Addressing EISA in the Potential Study and PY20 TRM, Memorandum, Prepared by AEG, Submitted to EEM and HPUC, January 26, 2020.
• | AEG's 2019 Analysis File named "PY19 TRM - Residential Additions - Draft_20191113 AEG reviewed."
• | AEG's 2018 Analysis Files named "AEG HPUC Update of Residential Measures - Analysis file."
• | 2026 Illinois Statewide Technical Reference Manual, v14.0, Vol. 3: Residential Measures, Sep. 19, 2025, pg. 383.
∆𝑘𝑊ℎ=((𝑊_𝑏𝑎𝑠𝑒−𝑊_𝐿𝐸𝐷 ))/(1,000 𝑊/𝑘𝑊)∗𝐼𝑆𝑅∗𝐻𝑂𝑈∗𝑃𝐹
∆𝑘𝑊=((𝑊_𝑏𝑎𝑠𝑒−𝑊_𝐿𝐸𝐷 ))/(1,000 𝑊/𝑘𝑊)∗𝐼𝑆𝑅∗𝐶𝐹∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒𝑡𝑖𝑚𝑒=∆𝑘𝑊ℎ∗𝑅𝑈𝐿

## R_Light_Holiday String Light
RESIDENTIAL: Holiday String Light
Return to TOC
UPDATE STATUS
Introduced in Fall 2019 for PY19 TRM.
MEASURE DETAILS
Description
The replacement of incandescent decorative holiday string lights with LED string lights .
Program Criteria
Efficient equipment must be Design Light Consortium (DLC) listed. Mini bulb count per string should be documented.
Unit of Measure
One bulb.
Baseline Equipment
String lighting with multiple incandescent mini bulbs.
High Efficiency Equipment
String lighting with LED mini bulbs.
ALGORITHMS
Peak Demand Reduction, kW
(1)
First Baseline Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit | Source/Notes
Wbase | kW_b | kW_b | kW_b | Baseline Wattage | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | 0.39 |  |  |  | W | Benchmark of incandescent string lights at retail.
WLED | kW_led | kW_led | kW_led | LED Wattage | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | 0.07 |  |  |  | W | Benchmark of LED string lights at retail.
ISR |  |  |  | Lifetime in-service rate | [11 empty] | 0.97 |  |  |  | - | AEG's Fall 2018 Benchmarking for Residential LED measure.1
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0.78 |  |  |  | - | Average percentage of hours after sunset within 5pm to 9pm peak period. (Assumes average sunset time of 5:54 pm during holiday season.)
HOU |  |  |  | Annual hours of use | [11 empty] | 210 |  |  |  | hrs | Assume average of 6 hours per day for 5 weeks.
PF 2 | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 1 | 0.96 | 0.96 | 0.96 | -
EULLED | Measure Life | Measure Life | Measure Life | Effective useful life of LED | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 5 |  |  |  | yrs | Reasonable estimate of EUL based on typical use and storage.
1 AEG's ISR benchmarking was done specifically for the Residential LED measure, which applies to omnidirectional LED bulbs. Until further research can be carried out for string lights, assume the ISRs for both measures would be similar.
2 Use value of PF=1 until more data is available on PF of LEDs.
SAVINGS
Deemed Savings (per mini bulb)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Holiday String Light, per bulb | [7 empty] | 0.00024211 | [7 empty] | 0.065184 | [5 empty] | 0.32592
Semi-Prescriptive Savings Calculator (based on count of mini bulbs per string)
Number of bulbs/string
|  |  | 100 | [5 empty] | Example only. Hawai'i Energy to fill in based on bulbs in incented strings.
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [5 empty] | Lifetime Energy Savings
Holiday String Light, per string | [7 empty] | 0.024 | [7 empty] | 6.52 | [5 empty] | 32.59
RESOURCES
• | AEG's 2019 Analysis File titled "PY19 TRM - Residential Additions - Draft_20191113 AEG reviewed."
• | AEG's 2018 Analysis Files titled "AEG HPUC Update of Residential Measures - Analysis file."
∆𝑘𝑊ℎ=((𝑊_𝑏𝑎𝑠𝑒−𝑊_𝐿𝐸𝐷 ))/(1,000 𝑊/𝑘𝑊)∗𝐼𝑆𝑅∗𝐻𝑂𝑈∗𝑃𝐹
∆𝑘𝑊=((𝑊_𝑏𝑎𝑠𝑒−𝑊_𝐿𝐸𝐷 ))/(1,000 𝑊/𝑘𝑊)∗𝐼𝑆𝑅∗𝐶𝐹∗𝑃𝐹
∆𝑘𝑊ℎ=∆𝑘𝑊ℎ∗𝐸𝑈𝐿

## R_Light_Solar Tube
RESIDENTIAL: Solar Light Tube
Return to TOC
UPDATE STATUS
Introduced in Winter 2020-2021 for PY21 TRM.
MEASURE DETAILS
Description
A solar light tube with a 10'' to 21'' diameter with a prismatic or translucent lens installed on the roof of a home. The lens reflects light captured from the roof opening through a highly specular reflective tube down to the mounted fixture height. When in use, a solar light tube fixture resembles a metal halide fixture.
Program Criteria
This measure is applicable to single-family retrofit and new construction applications. We have assumed the retrofit would involve redesign of existing lighting system. The solar light tube must have an ENERGY STAR label.
Unit of Measure
One solar light tube.
Baseline Equipment
The baseline equipment is a lighting fixture with comparable brightness (lumens) to that of the solar light tube. The specifications for the baseline fixture depend on the size of the solar light tube (i.e., 10'', 14'', 21'' diameter) and the geographic location (i.e., Honolulu, Kahului, Hilo). This measure has a baseline for PY21 that consists of a mix of 25% CFL, 25% halogen, and 50% LED lamps. For PY22 and later, the baseline consists of a mix of 25% CFL and 75% LED lamps that complies with the original EISA Tier 2 Backstop requirement of 45 lumens per Watt. (Halogen lamps have < 45 lumens/Watt and will be phased out. AEG has assumed they will be replaced with LED lamps.) The baseline lighting fixtures are assumed to be installed at the same time as the solar light tube.
High Efficiency Equipment
The efficient equipment is a solar light tube that concentrates and directs light from the roof to an area inside the home.
ALGORITHMS
First Baseline Peak Demand Reduction, kW
(1)
Second Baseline Peak Demand Reduction, kW
(2)
First Baseline Annual Energy Savings, kWh/yr
(3)
Second Baseline Annual Energy Savings, kWh/yr
(4)
Lifetime Energy Savings, kWh (Applicable through PY21)
(5)
Lifetime Energy Savings, kWh (Applicable to PY22 and later)
(6)
Waste Heat Factors due to Interaction with Space Cooling System
(7)
(8)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  | Source/Notes
kWbase,1 | kW_b | kW_b | kW_b | First Baseline Wattage - Fixture with comparable luminosity - Lamp mix of 25% CFL, 25% halogen, 50% LED | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | baseline wattage of average incandescent bulb | See Table 1 | see Table 1 | see Table 1 | see Table 1 | kW |  | Solatube Lumen Output Use Tables Lamp mix based on 2019 Hawaii Statewide Baseline Energy Use Study EISA legislation, effective dates of 2012-2014
kWbase,2 | kW_b | kW_b | kW_b | Second Baseline Wattage - Fixture with comparable luminosity - Lamp mix of 25% CFL, 75% LED | [11 empty] | See Table 1 | see Table 1 | see Table 1 | see Table 1 | kW |  | Solatube Lumen Output Use Tables Lamp mix based on the assumption that all halogen lamps will be replaced with LED lamps Original EISA backstop
ISR |  |  |  | Lifetime in-service rate | [11 empty] | 1 |  |  |  | - |  | Assumes the solar light tube will not be removed once installed
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0 | 0.12 | 0.12 | 0.12 | - |  | The solar light tube measure can only replace lighting during limited daylight hours that do not coincide with Hawaii's peak demand period of 5-9pm
HOU |  |  |  | Average hours of use per day | [11 empty] | See Table 2 | 0.12 | 0.12 | 0.12 | hr/day |  | Engineering judgement
WHC,D |  |  |  | Waste heat factor due to lighting interaction with space cooling system demand | [11 empty] | Varies |  |  |  | - |  | See Equation 7; applicable to lighting installed in locations with space cooling
WHC,E |  |  |  | Waste heat factor due to lighting interaction with space cooling system energy use | [11 empty] | Varies |  |  |  | - |  | See Equation 8; applicable to lighting installed in locations with space cooling
%Cool |  |  |  | Share of homes with electric cooling | [11 empty] | See Table 2 |  |  |  | - |  | 2019 Hawaii Statewide Baseline Energy Use Study
IEC,D |  |  |  | Interactive effects factor to account for cooling demand savings due to reducing waste heat with efficient lighting | [11 empty] | 1.3 |  |  |  | - |  | AEG's Hawai‘i-specific simulation modeling (from PY21 TRM v1.0, Residential LED measure). Solar light tube has negligible solar heat gain as it filters out most of the infrared rays (>760 nm) and only allows for the visual rays (400-760 nm) to enter into the space
IEC,E |  |  |  | Interactive effects factor to account for cooling energy savings due to reducing waste heat with efficient lighting | [11 empty] | 1.35 |  |  |  | -
PF | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 1 | 0.96 | 0.96 | 0.96 | - |  | Footnote 2
EUL1st | Measure Life | Measure Life | Measure Life | Effective useful life of EISA Tier 1 (i.e., halogen) baseline lamps | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | See Table 2 | 0.12 | 0.12 | 0.12 | yrs |  | Based on average lamp life of 2,500 hours
EULtube | Measure Life | Measure Life | Measure Life | Effective useful life of solar light tube | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 10 | 0.12 | 0.12 | 0.12 | yrs |  | 2021 Illinois TRM v.9.0 Vol. 2, and Solatube product warranty
1 Residential Lighting End-Use Consumption Study: Estimation Framework and Initial Estimates, Prepared by DNV KEMA Energy and Sustainability, Pacific Northwest National Laboratory, Prepared for Solid-State Lighting Program, Building Technologies Program, Office of Energy Efficiency and Renewable Energy, U.S. Department of Energy, December 2012. Table 4.4 shows that 15% of CFLs are installed in garages and exterior locations. AEG assumes CFLs are reasonable proxy for LEDs. 2 Per Solatube Lumen Output Use document, the light loss factor is 0.92 for solar light tube and 0.8 for typical default light fixture. Conservatively, we chose a value of PF=1 for this measure.
Table 1a: Connected Wattage of the light fixture that the solar tube light replaces, for PY21
| Measure Name | [7 empty] | Wconnected Honolulu |  |  |  | Wconnected Kahului |  |  |  | Wconnected Hilo
| Solar Light Tube 21'' | [7 empty] | 267.25 |  |  |  | 254.75 |  |  |  | 188.75
| Solar Light Tube 14'' | [7 empty] | 124.5 |  |  |  | 116.5 |  |  |  | 83
| Solar Light Tube 10'' | [7 empty] | 62.25 |  |  |  | 59.5 |  |  |  | 41.5
Table 1b: Connected Wattage of the light fixture that the solar tube light replaces, for PY22 and later
| Measure Name | [7 empty] | Wconnected Honolulu |  |  |  | Wconnected Kahului |  |  |  | Wconnected Hilo
| Solar Light Tube 21'' | [7 empty] | 152.25 |  |  |  | 144 |  |  |  | 107.25
| Solar Light Tube 14'' | [7 empty] | 64.5 |  |  |  | 65.25 |  |  |  | 43
| Solar Light Tube 10'' | [7 empty] | 32.25 |  |  |  | 30.5 |  |  |  | 21.5
Table 2. Key Parameters for Non-Military and Military Homes
[6 empty] | CF1 |  |  |  |  | %Cool |  |  |  |  | HOU2 |  |  |  |  | EULtube |  |  | EUL1st
| Non-Military |  |  |  |  | 0 |  |  |  |  | 48% |  |  |  |  | 1.5 |  |  |  |  | 10 |  |  | 5
| Military |  |  |  |  | 0 |  |  |  |  | 100% |  |  |  |  | 2.3 |  |  |  |  | 10 |  |  | 3
1 The solar light tube measure can only effectively replace lighting during limited daylight hours. Peak demand period is 5-9pm. Therefore, CF=0. 2 Non-Military HOU based on engineering judgement considering numerous factors including: typical home occupancy patterns; solar light tubes typically installed in interior and darker (often window-less) spaces like hallways, bathrooms, laundry rooms; and solar light tubes only provide savings during daylighting hours. Per the approach in previous versions of the Hawai‘i TRM, the Non-Military HOU has been multiplied by a factor of 1.5 to obtain the Military HOU .
Table 3. Residential Households by County, 2018
| County | [7 empty] | Households |  |  |  | %
| Oahu | [7 empty] | 298888.9871 |  |  |  | 66%
| Hawaii | [7 empty] | 78737.5243 |  |  |  | 18%
| Maui | [7 empty] | 184.5 |  |  |  | 14%
| Military | [7 empty] | 7497.218 |  |  |  | 2%
| Total | [7 empty] | 449595 |  |  |  | 100%
Source: Hawaii 2020 MPS_Appendix A_Final Annual Results.xlsx, "Summary" sheet, "Residential Control Totals by Island, 2018," Cells C26:D35. Revised to remove Kauai homes and to merge the islands of Maui, Molokai, and Lanai into Maui County.
SAVINGS (APPLICABLE FOR PY21)
Deemed Savings for All Single-Family Homes across all Islands (based on tube diameter size)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 163.39 | [6 empty] | 1281.7
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 75.36 | [6 empty] | 574.2
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 37.79 | [6 empty] | 286.7
Note: We have assumed all military homes are on Oahu.
Deemed Savings (based on tube diameter size, geographic location of home, and type of home (i.e., non-military or military)
Non-Military - Honolulu, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 170.9 | [6 empty] | 1341.3
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 79.62 | [6 empty] | 604.33
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 39.81 | [6 empty] | 302.17
Military - Honolulu, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 302.88 | [6 empty] | 2116.48
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 141.1 | [6 empty] | 935
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 70.55 | [6 empty] | 467.5
Non-Military - Kahului, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 162.91 | [6 empty] | 1274.98
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 74.5 | [6 empty] | 581.13
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 38.05 | [6 empty] | 287.77
Military - Kahului, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 288.71 | [6 empty] | 2008.52
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 132.03 | [6 empty] | 913.74
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 67.43 | [6 empty] | 444.25
Non-Military - Hilo, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 120.7 | [6 empty] | 946.42
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 53.08 | [6 empty] | 402.89
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 26.54 | [6 empty] | 201.44
Military - Hilo, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 213.92 | [6 empty] | 1492.6
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 94.07 | [6 empty] | 623.34
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 47.03 | [6 empty] | 311.66
SAVINGS (APPLICABLE FOR PY22 AND LATER)
Deemed Savings for All Single-Family Homes across all Islands (based on tube diameter size)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 92.95 | [6 empty] | 929.5
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 39.48 | [6 empty] | 394.8
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 19.55 | [6 empty] | 195.5
Note: We have assumed all military homes are on Oahu.
Deemed Savings (based on tube diameter size, geographic location of home, and type of home (i.e., non-military or military)
Non-Military - Honolulu, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 97.3608 | [6 empty] | 973.6083
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 41.2465 | [6 empty] | 412.4646
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 20.6232 | [6 empty] | 206.2323
Military - Honolulu, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 172.5487 | [6 empty] | 1725.4873
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 73.0995 | [6 empty] | 730.9946
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 36.5497 | [6 empty] | 365.4973
Non-Military -Kahului, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 92.0851 | [6 empty] | 920.8512
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 41.7261 | [6 empty] | 417.2607
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 19.5041 | [6 empty] | 195.0414
Military - Kahului, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 163.1988 | [6 empty] | 1631.988
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 73.9495 | [6 empty] | 739.4946
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 34.5664 | [6 empty] | 345.6641
Non-Military - Hilo, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 68.5842 | [6 empty] | 685.8423
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 27.4976 | [6 empty] | 274.9764
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 13.7488 | [6 empty] | 137.4882
Military - Hilo, HI
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Solar Light Tube 21'' | [7 empty] | 0 | [7 empty] | 121.5491 | [6 empty] | 1215.4911
Solar Light Tube 14'' | [7 empty] | 0 | [7 empty] | 48.733 | [6 empty] | 487.3298
Solar Light Tube 10'' | [7 empty] | 0 | [7 empty] | 24.3665 | [6 empty] | 243.6649
RESOURCES
• | AEG's 2021 Analysis File titled "PY21 TRM_R_Light_Solar Tube Analysis File."
• | Hawaii Energy - Technical Reference Manual (TRM) No. 2011 Measure Savings Calculations, Residential Daylighting measure, p. 40-41.
• | Illinois Statewide Technical Reference Manual v9.0 Vol. 2_September 25, 2020_FINAL. Section 4.5.11 Solar Light Tubes (p. 545-547).
• | National Oceanic and Atmospheric Administration, National Centers for Environmental Information, Comparative Climatic Data, Data Table: Sunshine - Average Percent of Possible (Cities Listed by Ranking Most to Least).
• | Solatube, Solatube Lumen Output Table, Lumen Output Use Version 4.1 -7/05
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | Hawaii Energy - Technical Reference Manual (TRM) PY 2021 V1.0 Measure Savings Calculations, Residential: LED.
• | State of Hawaii Market Potential Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Appendix A: Final Annual Results, filename: "Hawaii 2020 MPS_Appendix A_Final Annual Results.xlsx."
〖∆𝑘𝑊ℎ〗_1𝑠𝑡=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,1) )∗𝐼𝑆𝑅∗𝐻𝑂𝑈∗365𝑑𝑎𝑦/𝑦𝑟∗(1+〖𝑊𝐻〗_(𝐶,𝐸) )∗𝑃𝐹
〖∆𝑘𝑊〗_1𝑠𝑡=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,1) )∗𝐼𝑆𝑅∗𝐶𝐹∗(1+〖𝑊𝐻〗_(𝐶,𝐷) )∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_𝑃𝑌21=〖∆𝑘𝑊ℎ〗_1𝑠𝑡∗〖𝐸𝑈𝐿〗_1𝑠𝑡+〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗(〖𝐸𝑈𝐿〗_𝑡𝑢𝑏𝑒−〖𝐸𝑈𝐿〗_1𝑠𝑡 )
〖∆𝑘𝑊ℎ〗_2𝑛𝑑=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,2) )∗𝐼𝑆𝑅∗𝐻𝑂𝑈∗365𝑑𝑎𝑦/𝑦𝑟∗(1+〖𝑊𝐻〗_(𝐶,𝐸) )∗𝑃𝐹
〖∆𝑘𝑊〗_2𝑛𝑑=(〖𝑘𝑊〗_(𝑏𝑎𝑠𝑒,2) )∗𝐼𝑆𝑅∗𝐶𝐹∗(1+〖𝑊𝐻〗_(𝐶,𝐷) )∗𝑃𝐹
〖∆𝑘𝑊ℎ〗_(𝑃𝑌22+)=〖∆𝑘𝑊ℎ〗_2𝑛𝑑∗〖𝐸𝑈𝐿〗_𝑡𝑢𝑏𝑒
〖𝑊𝐻〗_(𝐶,𝐷)=%_𝐶𝑜𝑜𝑙∗(〖𝐼𝐸〗_(𝐶,𝐷)−1)
〖𝑊𝐻〗_(𝐶,𝐸)=%_𝐶𝑜𝑜𝑙∗(〖𝐼𝐸〗_(𝐶,𝐸)−1)

## R_PlugProcess_Adv Power Strip
RESIDENTIAL: Advanced Power Strips
Return to TOC
UPDATE STATUS
Updated in Winter 2020-2021 for PY21 TRM.
MEASURE DETAILS
Description
Load sensing and interaction sensing advanced power strips. This measure involves the purchase and installation of a new Tier 1 or Tier 2 load sensing advanced power strip (APS) in place of a power strip with no automated power shutoff function in a home office or entertainment center. This measure can be directly installed or owner installed. Savings are based on the average load of a 6 plug strip.
Program Criteria
Tier 1 or Tier 2 qualified power strip.
Unit of Measure
One power strip.
Baseline Equipment
Code-compliant or standard efficiency power strip.
High Efficiency Equipment
1) Tier 1 (Load or Occupancy Sensing): APS shuts off power to selected peripheral devices when the television or CPU enters sleep mode or is turned off. For Motion-sensing APS, the APS shuts off power to controlled devices when no motion is detected for a set period of time. 2) Tier 2 (Engagement Sensing or Active Controls): In entertainment applications, APS shuts off power to controlled devices (including television) when no user engagement is detected for a set period of time regardless of the level of power draw. All products currently on the market include Infrared (IR) Sensing to monitor remote control inputs. Additional layers of control over IR sensing in this measure application category may include: (1) Occupancy Sensing and (2) Additional Connectivity (ex: Smartphone application/control). In home office applications, APS shuts off power to controlled devices and puts the CPU into a low-energy, sleep mode when no user interaction (typically a combination of key-board, mouse, and/or motion) is detected for a set period of time. APS manages the active energy use of the control device (CPU) and the standby power consumption of peripheral devices.
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  | Source/Notes
KWHBaseline | kWh_plug | kWh_plug | kWh_plug | Average deemed baseline kWh per power strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | See Table 1 | see Table 1 | see Table 1 | see Table 1 | kWh |  | Adapted from RTF analysis.1
% Savings | kWh_plug | kWh_plug | kWh_plug | Savings percentage due to power strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | average deemed kWh per receptacle ("outlet") on the strip | See Table 1 | see Table 1 | see Table 1 | see Table 1 | kWh |  | Adapted from RTF analysis.1
ISR | #plugs | #plugs | #plugs | In Service Rate. For this measure, the ISR represents the % of units properly installed. | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | See Table 1 | see Table 1 | see Table 1 | see Table 1 | - |  | Adapted from RTF analysis.1
PF | #plugs | #plugs | #plugs | Persistence Factor. For this measure, the PF represents the % of units retained within first year. | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | Number of plug outlets per power strip | See Table 1 | see Table 1 | see Table 1 | see Table 1 | - |  | Adapted from RTF analysis.1
HRS | HOURS | HOURS | HOURS | Annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | 8760 | 8760 | 8760 | 8760 | hrs |  | Assumes no manual shutoff of equipment. | assumes no manual shutoff of equipment | assumes no manual shutoff of equipment | assumes no manual shutoff of equipment | assumes no manual shutoff of equipment | assumes no manual shutoff of equipment | assumes no manual shutoff of equipment | assumes no manual shutoff of equipment | assumes no manual shutoff of equipment
CF | CF | CF | CF | Coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 1 | 0.87 | 0.87 | 0.87 | - |  | % of maximum hourly Watt savings on average that were realized from 5-9 pm for residential A/V equipment. Assumed even distribution of savings. | % of maximum hourly watt savings on average that were realized in a 5-9 pm time period for residential A/V equipment (see Valmiki and Corradini). | % of maximum hourly watt savings on average that were realized in a 5-9 pm time period for residential A/V equipment (see Valmiki and Corradini). | % of maximum hourly watt savings on average that were realized in a 5-9 pm time period for residential A/V equipment (see Valmiki and Corradini). | % of maximum hourly watt savings on average that were realized in a 5-9 pm time period for residential A/V equipment (see Valmiki and Corradini). | % of maximum hourly watt savings on average that were realized in a 5-9 pm time period for residential A/V equipment (see Valmiki and Corradini). | % of maximum hourly watt savings on average that were realized in a 5-9 pm time period for residential A/V equipment (see Valmiki and Corradini). | % of maximum hourly watt savings on average that were realized in a 5-9 pm time period for residential A/V equipment (see Valmiki and Corradini). | % of maximum hourly watt savings on average that were realized in a 5-9 pm time period for residential A/V equipment (see Valmiki and Corradini).
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 5 | 5 years | 5 years | 5 years | yrs |  | Average of several TRMs and secondary sources.2
Sources: |  | 1. Adapted from Reginal Technical Forum. (2019, January 24). Residential Advanced Power Strips Version 3.1. Retrieved from <https://rtf.nwcouncil.org/measure/residential-advanced-power-strips>.
2. AEG's Analysis File titled "PY21 R_PlugProcess_Adv Power Strip Analysis File."
Table 1. Deemed Savings Values for Advanced Power Strips
[6 empty] | KWH. Baseline |  |  | % Savings |  |  | ISR |  |  | PF |  |  | kWh Savings |  |  | kW Savings
Direct Install |  | Tier 1: Home Office |  |  |  | 312 |  |  | 13% |  |  | 100% |  |  | 91.28% |  |  | 37.0223 |  |  | 0.0042263
|  | Tier 1: Entertain-ment Center |  |  |  | 465.6037 |  |  | 18.11% |  |  | 100% |  |  | 91.28% |  |  | 76.9628 |  |  | 0.0087857
|  | Tier 2: Home Office |  |  |  | 312 |  |  | 22.53% |  |  | 100% |  |  | 91.28% |  |  | 64.1632 |  |  | 0.0073246
|  | Tier 2: Entertain-ment Center |  |  |  | 465.6037 |  |  | 22.53% |  |  | 100% |  |  | 85% |  |  | 89.1665 |  |  | 0.010179
Owner Install |  | Tier 1: Home Office |  |  |  | 312 |  |  | 13% |  |  | 68.15% |  |  | 90.29% |  |  | 24.9579 |  |  | 0.0028491
|  | Tier 1: Entertain-ment Center |  |  |  | 465.6037 |  |  | 18.11% |  |  | 68.15% |  |  | 90.29% |  |  | 51.8832 |  |  | 0.0059227
|  | Tier 2: Home Office |  |  |  | 312 |  |  | 22.53% |  |  | 68.15% |  |  | 90.29% |  |  | 43.2546 |  |  | 0.0049377
|  | Tier 2: Entertain-ment Center |  |  |  | 465.6037 |  |  | 22.53% |  |  | 61.35% |  |  | 89.88% |  |  | 57.8395 |  |  | 0.0066027
Note: |  | Adapted from Regional Technical Forum. (2019, January 24). Residential Advanced Power Strips Version 3.1. Retrieved from <https://rtf.nwcouncil.org/measure/residential-advanced-power-strips>.
Table 2. Plug Location
|  | Plug Location |  |  |  | %
|  | Home Office |  |  |  | 35.46%
|  | Entertain-ment Center |  |  |  | 64.54%
Note: |  | Equipment counts from Page 312 and 314 of 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Volume 2 Appendices: Questionnaires, Ancillary Research Materials and Crosstabs
SAVINGS
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [6 empty] | Lifetime Energy Savings
Direct Install Tier 1 Average | [7 empty] | 0.007 | [7 empty] | 62.8 | [6 empty] | 314
Direct Install Tier 2 Average | [7 empty] | 0.009 | [7 empty] | 80.3 | [6 empty] | 401.5
Owner Install Tier 1 Average | [7 empty] | 0.005 | [7 empty] | 42.33 | [6 empty] | 211.65
Owner Install Tier 2 Average | [7 empty] | 0.006 | [7 empty] | 52.67 | [6 empty] | 263.35
RESOURCES
• | AEG's Analysis File titled "PY21 R_PlugProcess_Adv Power Strip Analysis File."
• | Regional Technical Forum. (2019, January 24). Residential Advanced Power Strips Version 3.1. Retrieved from https://rtf.nwcouncil.org/measure/residential-advanced-power-strips.
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Volume 2 Appendices: Questionnaires, Ancillary Research Materials and Crosstabs.
• | Valmiki, M. and A. Corradini. Tier 2 Advanced Power Strips in Residential and Commercial Applications. San Diego Gas & Electric Emerging Technologies Program, Technology Assessment Report. April 2015. The test APS used in the study is shown with 6 controlled receptacles.
• | DEER. (2020). SupportTable-EUL2020.xlsx. Retrieved from http://www.deeresources.com/files/DEER2020/download/SupportTable-EUL2020.xlsx.
• | ComEd. (2018). 2018 ComEd Effective Useful Life Research Report. Retrieved from https://www.ilsag.info/evaluation-documents/final-evaluation-reports/https://www.ilsag.info/evaluation-documents/final-evaluation-reports/.
• | CalTF. (2015). Analysis of EULs for Residential Tier 2 Power Strips (WP WPSDGEREHE0004.0).
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
∆𝑘𝑊ℎ=% 𝑆𝑎𝑣𝑖𝑛𝑔𝑠∗〖𝐾𝑊𝐻〗_𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒∗𝐼𝑆𝑅∗𝑃𝐹
∆𝑘𝑊=% 𝑆𝑎𝑣𝑖𝑛𝑔𝑠∗〖𝐾𝑊𝐻〗_𝐵𝑎𝑠𝑒𝑙𝑖𝑛𝑒 ∗𝐼𝑆𝑅∗𝑃𝐹∗CF/HRS

## R_PlugProcess_Switch Plug
RESIDENTIAL: Switch Plug
Return to TOC
UPDATE STATUS
Updated in Spring 2019 for PY19 TRM.
MEASURE DETAILS
Description
A power switch that acts as the interface between the wall outlet and the appliance. It prevents phantom energy drain by disconnecting the attached appliance without having to remove the power cord.
Program Criteria
Unit of Measure
One switch.
Baseline Equipment
No switch installed.
High Efficiency Equipment
Switch plug installed.
ALGORITHMS
peak kW savings | [5 empty] | = (W.stby * CF) / 1000
annual kWh savings | [5 empty] | = kWh.stby
lifetime kWh savings | [5 empty] | = kWh.stby * EUL
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description |  |  | Value |  | Unit | Notes
W.stby |  |  |  | Standby power draw of attached load |  |  | 3.0731 |  | W | Determined based on probability of attached equipment type. 1
kWh.stby |  |  |  | Annual standby energy consumption of attached load |  |  | 26.8503 |  | kWh | Determined based on probability of attached equipment type. 1
Constant |  |  |  | Conversion constant |  |  | 1000 |  | W/kW
CF | CF* | CF* | CF* | Coincidence factor |  |  | 0.82 |  | - | AEG's analysis of DOE's OpenEI load shapes using Hawai‘i-specific prototypes, weather data, and peak demand period.
EUL | Measure Life (yrs) | Measure Life (yrs) | Measure Life (yrs) | Effective useful life of measure |  |  | 5 |  | yrs | DEER 2020 for "Res-Plug-AdvPwrStrip" measure.
Note: |  | 1. Based on data from Lawrence Berkeley National Laboratory: Low-Power Mode Energy Consumption in California Homes, 2008. See accompanying Power Switch Calculation (R_PlugProcess_Power Switch_CALC).
SAVINGS
Measure Name |  |  |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  | Lifetime Energy Savings
Switch Plug |  |  |  |  | 0.003 |  |  | 26.85 |  |  | 134.25
RESOURCES
• | AEG's 2019 Analysis File titled "New Residential Measures Summary - AEG Analysis file."
• | AEG's 2018 Analysis of U.S. Department of Energy's OpenEI Commercial Hourly Load Profiles using Hawai‘i-specific data. OpenEI data files available here: https://openei.org/doe-opendata/dataset/commercial-and-residential-hourly-load-profiles-for-all-tmy3-locations-in-the-united-states. AEG used the residential end-use load profile data for "Miscellaneous" interior equipment for this Switch Plug measure. (See file named "AEG HPUC EFLH and CF Analysis - Non-Holiday Weekdays" for results.)
• | Lawrence Berkeley National Laboratory: Low-Power Mode Energy Consumption in California Homes, 2008.

## R_PlugProcess_Switch_Plug_CALC
Return to TOC |  | Averages: | 3.0731 | 26.8503
Category | Product | Standby Devices per Household | Power (W) | Energy (kWh/yr) | Probability
Appliance | Cooktop,electric | 0.02 | 1 | 9 | 0.07013%
Appliance | Dishwasher | 0.15 | 1.5 | 13 | 0.5259%
Audio | Amplifier | 0.12 | 6.8 | 59 | 0.4208%
Audio | AudioMinisystem | 0.5 | 8.7 | 76 | 1.753%
Audio | CDPlayer | 0.75 | 3.2 | 28 | 2.63%
Audio | CDPlayer,portable | 0.25 | 1.4 | 12 | 0.8766%
Audio | Charger,digitalmusicplayer | 0.34 | 0.3 | 2 | 1.192%
Audio | Equalizer(audio) | 0.01 | 1.6 | 14 | 0.03506%
Audio | Hometheatersystem | 0.05 | 4 | 35 | 0.1753%
Audio | Karaokemachine | 0.03 | 1.1 | 10 | 0.1052%
Audio | Musicalkeyboard | 0.2 | 2.9 | 25 | 0.7013%
Audio | Radio,table | 0.23 | 1.3 | 11 | 0.8065%
Audio | Receiver(audio) | 0.35 | 10.8 | 94 | 1.227%
Audio | Speakers,powered | 0.05 | 3.8 | 33 | 0.1753%
Audio | Speakers,wireless(basestation) | 0.03 | 3.8 | 33 | 0.1052%
Audio | Speakers,wireless(speakers) | 0.03 | 3.8 | 33 | 0.1052%
Audio | Stereo,portable | 0.48 | 1.3 | 12 | 1.683%
Audio | Subwoofer | 0.22 | 8.9 | 78 | 0.7714%
Audio | Tuner | 0.14 | 1 | 8 | 0.4909%
Audio | Turntable(audio) | 0.14 | 1 | 9 | 0.4909%
Computer | Computer,desktop | 0.95 | 4.5 | 39 | 3.331%
Computer | Computer,integrated(all) | 0.02 | 5.2 | 45 | 0.07013%
Computer | Computer,notebook | 0.41 | 4 | 35 | 1.438%
Computer | Dock,notebook | 0.02 | 1 | 9 | 0.07013%
Display | Computerdisplay,LCD | 0.53 | 0.9 | 8 | 1.858%
Display | Projector,video | 0.01 | 1.6 | 14 | 0.03506%
Display | Television,LCD | 2.07 | 1.5 | 13 | 7.258%
Display | Television,plasma | 0.02 | 1.9 | 16 | 0.07013%
Display | Television,rearprojection | 0.09 | 2.4 | 21 | 0.3156%
ElectricHousewares | Clock,alarm | 0.5 | 1 | 9 | 1.753%
ElectricHousewares | Clock,radio | 1.13 | 2.2 | 19 | 3.962%
ElectricHousewares | Coffeemaker,residential | 0.21 | 1.1 | 9 | 0.7363%
ElectricHousewares | Oven,microwave | 1.01 | 3 | 26 | 3.541%
ElectricHousewares | Ricecooker | 0.06 | 0.5 | 4 | 0.2104%
ElectricHousewares | Toaster | 0.02 | 0.9 | 8 | 0.07013%
ElectricHousewares | Toasteroven | 0.12 | 0.9 | 8 | 0.4208%
ElectricHousewares | Vacuum,central | 0.07 | 3 | 26 | 0.2454%
ElectricHousewares | Vacuum,rechargeable | 0.16 | 2.1 | 19 | 0.561%
Hobby/leisure | Exerciseequipment | 0.05 | 1.8 | 15 | 0.1753%
Hobby/leisure | Ride-ontoycar | 0.02 | 1.9 | 17 | 0.07013%
Hobby/leisure | Spa/hottub | 0.07 | 2.4 | 21 | 0.2454%
HVAC | Aircleaner,portable | 0.06 | 0.2 | 2 | 0.2104%
HVAC | Airconditioner,room/wall | 0.03 | 1.9 | 17 | 0.1052%
HVAC | Ceilingfan | 0.2 | 0.7 | 6 | 0.7013%
HVAC | Fan,portable | 0.03 | 0.4 | 3 | 0.1052%
Imaging | Copier | 0.07 | 4.8 | 42 | 0.2454%
Imaging | Fax,inkjet | 0.13 | 6 | 52 | 0.4558%
Imaging | Fax,laser | 0.02 | 4 | 35 | 0.07013%
Imaging | Fax,thermal | 0.01 | 5 | 43 | 0.03506%
Imaging | Multi-functiondevice,inkjet | 0.35 | 7.9 | 69 | 1.227%
Imaging | Multi-functiondevice,laser | 0.06 | 5.8 | 51 | 0.2104%
Imaging | Printer,inkjet | 0.43 | 5.4 | 47 | 1.508%
Imaging | Printer,laser | 0.07 | 5 | 44 | 0.2454%
Imaging | Printer,photo | 0.18 | 1.4 | 12 | 0.6311%
Imaging | Scanner,flatbed | 0.15 | 3.5 | 31 | 0.5259%
Infrastructure | Garagedooropener | 0.44 | 4.9 | 43 | 1.543%
Lighting | Motionsensor,interior | 0.05 | 0.8 | 7 | 0.1753%
Lighting | Nightlight,interior | 1.2 | 0.2 | 2 | 4.208%
Lighting | Timer,interior | 0.13 | 0.3 | 2 | 0.4558%
Networking | Hub,ethernet | 0.08 | 3.8 | 33 | 0.2805%
Networking | Hub,USB | 0.25 | 1.3 | 11 | 0.8766%
Networking | Modem,cable | 0.25 | 8.3 | 73 | 0.8766%
Networking | Modem,DSL | 0.3 | 6 | 52 | 1.052%
Networking | Modem,POTS | 0.17 | 5.6 | 49 | 0.5961%
Networking | Modem,satellite | 0.02 | 9.5 | 83 | 0.07013%
Networking | Router,ethernet | 0.22 | 5.9 | 52 | 0.7714%
Networking | Wirelessaccesspoint | 0.23 | 4.7 | 41 | 0.8065%
OutdoorAppliances | Charger,hedgetrimmer | 0.04 | 1 | 9 | 0.1403%
OutdoorAppliances | Charger,weedtrimmer | 0.08 | 1.9 | 17 | 0.2805%
OutdoorAppliances | Lawnmower | 0.06 | 1.8 | 16 | 0.2104%
OutdoorAppliances | Timer,irrigation | 0.24 | 2.7 | 24 | 0.8415%
Peripherals | Dock,PDA | 0.13 | 1.4 | 12 | 0.4558%
Peripherals | Externaldrive | 0.06 | 1 | 9 | 0.2104%
Peripherals | Speakers,computer | 0.63 | 2.6 | 23 | 2.209%
PersonalCare | Massager | 0.05 | 1.7 | 15 | 0.1753%
PersonalCare | Shaver,men's | 0.25 | 0.1 | 1 | 0.8766%
PersonalCare | Shaver,women's | 0.15 | 0.1 | 1 | 0.5259%
PersonalCare | Toothbrush | 0.51 | 1.6 | 14 | 1.788%
Power | UninterruptiblePowerSupply(UPS) | 0.03 | 4.5 | 39 | 0.1052%
Security | Securitysystem | 0.2 | 4 | 35 | 0.7013%
Set-top | Set-topbox,analogcable | 0.1 | 8.7 | 76 | 0.3506%
Set-top | Set-topbox,digitalcable | 0.3 | 19.2 | 168 | 1.052%
Set-top | Set-topbox,digitalcablewithPVR | 0.05 | 34.3 | 301 | 0.1753%
Set-top | Set-topbox,gameconsolewithinternetconnectivity | 0.04 | 7.4 | 64 | 0.1403%
Set-top | Set-topbox,internet | 0.06 | 10.8 | 94 | 0.2104%
Set-top | Set-topbox,satellite | 0.48 | 13.7 | 120 | 1.683%
Set-top | Set-topbox,satellitewithPVR | 0.04 | 20.8 | 182 | 0.1403%
Telephony | CallerIDunit | 0.05 | 1.3 | 11 | 0.1753%
Telephony | Charger,cordlessphonehandset | 0.28 | 1.6 | 14 | 0.9818%
Telephony | Charger,mobilephone | 1.68 | 0.4 | 4 | 5.891%
Telephony | Phone,conference | 0.03 | 2 | 18 | 0.1052%
Telephony | Phone,cordless | 1.7 | 2.2 | 19 | 5.961%
Transportation | Golfcart | 0.02 | 11 | 96 | 0.07013%
Transportation | Wheelchair | 0.02 | 9.5 | 83 | 0.07013%
Utility | Charger,battery | 0.26 | 0.2 | 2 | 0.9116%
Utility | Powertool,cordless | 1.72 | 0.6 | 5 | 6.031%
Video | Charger,stillcamera | 0.67 | 0.1 | 1 | 2.349%
Video | Charger,videocamera | 0.35 | 0.1 | 1 | 1.227%
Video | DVDplayer | 1 | 2.2 | 19 | 3.506%
Video | Gameconsole | 0.29 | 3.5 | 31 | 1.017%
Video | Video,PVR(nomultifunctionality) | 0.19 | 22.8 | 200 | 0.6662%
Source: | Lawrence Berkeley National Laboratory: Low-Power Mode Energy Consumption in California Homes, 2008.

## R_PlugProcess_EV Charger
RESIDENTIAL: Level 2 Electric Vehicle Charger
Return to TOC
UPDATE STATUS
Added in Fall 2023 for the Mid-Year PY23 TRM V2.
MEASURE DETAILS
Description
Replacement of a non-ENERGY STAR Level 2 Electric Vehicle Charger with an ENERGY STAR-certified Level 2 Electric Vehicle Charger in an existing home or installation of an ENERGY STAR Level 2 Electric Vehicle Charger in a new or existing home instead of installation of a non-ENERGY STAR charger. The savings are due to a reduction in standby energy losses. The savings are due to a reduction in standby energy losses.
Program Criteria
The High Efficiency Equipment must be an ENERGY STAR certified Level 2 Electric Vehicle Charger.
Unit of Measure
One Level 2 EV charger.
Baseline Equipment
The Baseline Equipment is a non-ENERGY STAR Level 2 Electric Vehicle Charger.
High Efficiency Equipment
The High Efficiency equipment is an ENERGY STAR certified Level 2 Electric Vehicle Charger.
ALGORITHMS
Baseline Annual Energy Use, kWh/yr
(1)
High Efficiency Annual Energy Use, kWh/yr
(2)
Annual Plugged in Hours in Standby Mode, hrs/yr
(3)
Annual Energy Savings, kWh/yr
(4)
Average Power Demand Reduction in Standby Mode, kW
(5)
Peak Demand Reduction, kW
(6)
Lifetime Energy Savings, kWh
(7)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  |  | Value |  | Unit |  | Source/Notes
kWhbase |  | Annual standby energy use of non-ENERGY STAR Level 2 EV charger |  |  | See Equation 1 |  | kWh |  | Only standby energy is considered here since the ENERGY STAR electric vehicle supply equipment specification does not explicitly call for testing of steady state charging efficiency.1
kWhee |  | Annual standby energy use of ENERGY STAR-certified Level 2 EV Charger |  |  | See Equation 2 |  | kWh
HRSsp |  | Annual plugged-in hours of Level 2 EV Charger in standby mode |  |  | 3233 |  | hours |  | Regional Technical Forum.1 Calculated using Equation 3. 3511 hours - 278 hours = 3233 hours
HRSsu |  | Annual unplugged hours of Level 2 EV Charger in standby mode |  |  | 5249 |  | hours |  | Regional Technical Forum.1 Calculated from 8760 hours - 3511 hours = 5249 hours.
HRSp |  | Total annual plugged-in hours of Level 2 EV Charger |  |  | 3511 |  | hours |  | Regional Technical Forum.1 See sheet named "Res Measure UES Analysis" in the RTF workbook for derivation of the hours.
HRSc |  | Annual plugged-in hours of Level 2 EV Charger in charging mode |  |  | 278 |  | hours
Wbase |  | Average standby power of non-ENERGY STAR Level 2 EV Charger |  |  | See Table 1 |  | W |  | Regional Technical Forum and Idaho National Laboratory.2
Weep |  | Plugged-in standby power of ENERGY STAR-certified Level 2 EV Charger |  |  | See Table 1 |  | W |  | ENERGY STAR.3
Weeu |  | Unplugged standby power of ENERGY STAR-certified Level 2 EV Charger |  |  | See Table 1 |  | W
ΔkWh |  | Annual energy savings of Level 2 EV Charger in standby mode |  |  | See Equation 4 |  | kWh |  | Any energy savings during the charging mode are assumed to be relatively small and are therefore ignored.
∆kWs,average |  | Average power demand reduction of Level 2 EV Charger in standby mode |  |  | See Equation 5 |  | kW |  | Any demand reduction during the charging mode are assumed to be relatively small and are therefore ignored.
ΔkW |  | Peak demand reduction |  |  | See Equation 6 |  | kW
CF |  | Peak demand coincidence factor for the average power demand reduction of Level 2 EV Charger in standby mode |  |  | 1 |  | - |  | This CF assumes that EVs are charged during off-peak hours and that the standby energy use and demand savings are fully coincident with the peak demand period. The CF would be lower for charging that occurs during the on-peak hours. Time-of-use rates heavily influence when EVs are charged.4
ΔkWhlife |  | Lifetime energy savings |  |  | See Equation 7 |  | kWh
EULee |  | Effective useful life of measure |  |  | 10 |  | yrs |  | Regional Technical Forum.1 The EUL was established by RTF using professional judgment and from a literature review.
1. Northwest Power and Conservation Council, Regional Technical Forum (RTF), Level 2 Electric Vehicle Charger Workbook Version 3.1, Jul 18, 2023. <https://nwcouncil.app.box.com/v/leve2evcharg-3-1>.
2. Derived by the Regional Technical Forum using Idaho National Laboratory charger testing data.
3. ENERGY STAR Certified Electric Vehicle Supply Equipment - AC-Output, Metadata Updated October 13, 2023. <https://catalog.data.gov/dataset/energy-star-certified-electric-vehicle-supply-equipment-ac-output-v1-1>.
4. To realize the peak demand reductions, customers receiving rebates for EV chargers through the Hawai'i Energy program should be encouraged to charge during off-peak hours, whether or not they are on a TOU rate.
Table 1. Standby Power of Level 2 Electric Vehicle Charger
Level 2 EV Charger Type |  |  | Wbase (W) | Weep (W) |  |  |  | Weeu (W) |  |  | ∆kWs,average (kW)
Networked Level 2 EV Charger |  |  | 9.9 | 5.0595 |  |  |  | 3.4574 |  |  | 0.006
Non-networked Level 2 EV Charger |  |  | 3.7 | 3.746 |  |  |  | 2.0962 |  |  | 0.001
Sources: 1. Baseline wattages were derived by the Regional Technical Forum using Idaho National Laboratory charger testing data. See Northwest Power and Conservation Council, Regional Technical Forum, Level 2 Electric Vehicle Charger Workbook Version 3.1, Jul 18, 2023. <https://nwcouncil.app.box.com/v/leve2evcharg-3-1>. Refer to sheet named "Baseline EPA Charger Efficiency" in the RTF workbook.
2. Energy efficient case wattages were derived by AEG from ENERGY STAR Certified Electric Vehicle Supply Equipment - AC-Output, Metadata Updated October 13, 2023. <https://catalog.data.gov/dataset/energy-star-certified-electric-vehicle-supply-equipment-ac-output-v1-1>. See AEG's analysis file named "Mid-year PY23 TRM - Residential Level 2 Electric Vehicle Charger - Analysis File," sheet named "ESTAR QPL Pivot."
SAVINGS
Measure Name |  |  | Peak Demand Savings |  |  | Annual Energy Savings |  |  |  | Lifetime Energy Savings
Networked Level 2 EV Charger |  |  | 0.006 |  |  | 49.47 |  |  |  | 494.7
Non-networked Level EV Charger |  |  | 0.001 |  |  | 8.27 |  |  |  | 82.7
RESOURCES
• | AEG's 2023 Analysis File named "Mid-year PY23 TRM - Residential Level 2 Electric Vehicle Charger - Analysis File."
• | ENERGY STAR Certified Electric Vehicle Supply Equipment - AC-Output, Metadata Updated October 13, 2023. <https://catalog.data.gov/dataset/energy-star-certified-electric-vehicle-supply-equipment-ac-output-v1-1>.
• | ENERGY STAR Program Requirements for Electric Vehicle Supply Equipment - Eligibility Criteria. Version 1.2. <https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Version%201.2%20EVSE%20Final%20Specification.pdf>.
• | Northwest Council Regional Technical Forum, Level 2 Electric Vehicle Charger v 3.1, Approved July 18, 2023. <https://nwcouncil.box.com/v/leve2evcharg-3-1>.
∆𝑘𝑊= ∆𝑘𝑊𝑠,𝑎𝑣𝑒𝑟𝑎𝑔𝑒∗𝐶𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝑒𝑒
∆𝑘𝑊ℎ=(〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊ℎ〗_𝑒𝑒 )
〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒=((𝐻𝑅𝑆𝑠𝑝+〖𝐻𝑅𝑆〗_𝑠𝑢 )∗𝑊_𝑏𝑎𝑠𝑒)/1000
〖𝑘𝑊ℎ〗_𝑒𝑒=((𝐻𝑅𝑆𝑠𝑝 ∗𝑊_𝑒𝑒𝑝 )+(〖𝐻𝑅𝑆〗_𝑠𝑢 ∗𝑊_𝑒𝑒𝑢))/1000
〖𝐻𝑅𝑆〗_𝑠𝑝=〖𝐻𝑅𝑆〗_𝑝−〖𝐻𝑅𝑆〗_𝑐
〖∆𝑘𝑊〗_(𝑠,𝑎𝑣𝑒𝑟𝑎𝑔𝑒)=((𝑊𝑏𝑎𝑠𝑒−𝑊_𝑒𝑒𝑝)∗〖𝐻𝑅𝑆〗_𝑠𝑝 +(𝑊𝑏𝑎𝑠𝑒−𝑊_𝑒𝑒𝑢 ) ∗ 𝐻𝑅𝑆𝑠𝑢 )/(1000∗(8760−𝐻𝑅𝑆𝑐))

## R_PumpMotor_VFD Pool Pump
RESIDENTIAL: VFD Pool Pump
Return to TOC
UPDATE STATUS
Updated in Winter 2023-2024 for the PY24 TRM. This update applies the federal standard for dedicated-purpose pool pumps, effective June 19, 2021. It also applies the most recent Energy STAR 3.1 specifications for dedicated-purpose pool pumps.
MEASURE DETAILS
Description
This measure involves replacing a single-speed or dual-speed pool filter pump with a variable-speed pump of equivalent horsepower. This measure only applies to self-priming pool filter pumps, typically used with permanent, in-ground pools in single-family homes (there is a separate measure for multi-family and commercial settings). Non-self-priming pool filter pumps, typically used with rigid, above-ground pools, are not applicable.
Program Criteria
Qualifying pumps are variable speed pumps with controllers either built in or purchased and installed as a pair.
The installed variable-speed self-priming pool filter pump's rated Weighted Energy Factor (WEF) must meet or exceed the ENERGY STAR specifications. Any high-speed override capability should be temporary, not to exceed one 24-hour cycle without reverting to default settings.
New construction homes do not qualify.
Unit of Measure
One pump.
Baseline Equipment
The baseline efficiency equipment is a single-speed or dual-speed self-priming pool filter pump.
High Efficiency Equipment
The high efficiency equipment is an ENERGY STAR-certified variable-speed self-priming pool filter pump.
The sunset date for this measure is September 29, 2025, for pool pumps greater or equal to 1.15 but less than 5 total horsepower (THP).
The sunset date for this measure is September 28, 2027, for pool pumps greater or equal to 0.5 but less than 1.15 total horsepower (THP).
ALGORITHMS
Annual Energy Savings, kWh/yr
(1)
Peak Demand Reduction, kW
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  | Value | Unit | Sources/Notes
ΔkWh |  | Annual energy savings |  | Calculated | kWh/yr
ΔkW |  | Peak demand reduction |  | Calculated | kW
kWhDaily,Base |  | Daily energy consumption of baseline pump (depends on pump horsepower) |  |  |  | AEG derived the values from the Regional Technical Forum's (RTF) original analysis in the unit energy savings measure workbook for Efficient Pool Pumps but only included pool pumps meeting the federal code requirements.1
Single-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 4.6603 | kWh/day
|  | > 1 to ≤ 2 hp |  | 4.9693 | kWh/day
|  | > 2 to ≤ 3 hp |  | 6.417 | kWh/day
|  | > 3 to ≤ 4 hp |  | 15.9717 | kWh/day
Dual-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 4.1258 | kWh/day
|  | > 1 to ≤ 2 hp |  | 4.9693 | kWh/day
|  | > 2 to ≤ 3 hp |  | 6.417 | kWh/day
|  | > 3 to ≤ 4 hp |  | 9.0526 | kWh/day
kWhDaily,Eff |  | Daily energy consumption of variable-speed pump (depends on pump horsepower) |  |  |  | AEG derived the values from the RTF's original analysis in the unit energy savings measure workbook for Efficient Pool Pumps but only included pool pumps meeting the Energy Star requirements.2
Variable-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 1.7499 | kWh/day
|  | > 1 to ≤ 2 hp |  | 2.9221 | kWh/day
|  | > 2 to ≤ 3 hp |  | 3.5123 | kWh/day
|  | > 3 to ≤ 4 hp |  | 4.3551 | kWh/day
Days |  | Number of days the pump operates in a year |  | 365 | Days/yr | No change from PY18 TRM.
HoursDaily,Base |  | Daily runtime of baseline pump (depends on pump horsepower) |  |  |  | AEG derived the values from the RTF's original analysis in the unit energy savings measure workbook for Efficient Pool Pumps but only included pool pumps meeting the federal code requirements.1
Single-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 5.6211 | Hrs/day
|  | > 1 to ≤ 2 hp |  | 13.3311 | Hrs/day
|  | > 2 to ≤ 3 hp |  | 12.0653 | Hrs/day
|  | > 3 to ≤ 4 hp |  | 5.8183 | Hrs/day
Dual-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 10.9778 | Hrs/day
|  | > 1 to ≤ 2 hp |  | 13.3311 | Hrs/day
|  | > 2 to ≤ 3 hp |  | 12.0653 | Hrs/day
|  | > 3 to ≤ 4 hp |  | 11.9216 | Hrs/day
HoursDaily,Eff |  | Daily runtime of variable-speed pump (depends on pump horsepower) |  |  |  | AEG derived the values from the RTF's original analysis in the unit energy savings measure workbook for Efficient Pool Pumps but only included pool pumps meeting the Energy Star requirements.2
Variable-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 13.3333 | Hrs/day
|  | > 1 to ≤ 2 hp |  | 16.2811 | Hrs/day
|  | > 2 to ≤ 3 hp |  | 17.0951 | Hrs/day
|  | > 3 to ≤ 4 hp |  | 17.9092 | Hrs/day
CFBase |  | Coincidence factor of baseline pump (depends on pump horsepower) |  |  |  | AEG's estimate, obtained by dividing the number of daily operation hours of pump by 24 hours.
Single-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 0.23421
|  | > 1 to ≤ 2 hp |  | 0.55546
|  | > 2 to ≤ 3 hp |  | 0.50272
|  | > 3 to ≤ 4 hp |  | 0.24243
Dual-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 0.45741
|  | > 1 to ≤ 2 hp |  | 0.55546
|  | > 2 to ≤ 3 hp |  | 0.50272
|  | > 3 to ≤ 4 hp |  | 0.49673
CFEff |  | Coincidence factor of variable-speed pump (depends on pump horsepower) |  |  |  | AEG's estimate, obtained by dividing the number of daily operation hours of pump by 24 hours.
Variable-Speed Pumps
|  | > 0 to ≤ 1 hp |  | 0.55556
|  | > 1 to ≤ 2 hp |  | 0.67838
|  | > 2 to ≤ 3 hp |  | 0.7123
|  | > 3 to ≤ 4 hp |  | 0.74622
EUL |  | Effective useful life of measure |  | 10 | yrs | No change from PY18 TRM; EUL was verified during AEG's 2018 benchmarking.
Sources:
1 Federal Code. Title 10, Subchapter D. Part 431. Subpart Z. § 431.465. Accessible at: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-Y/section-431.465.
2 ENERGY STAR Program Requirements Product Specification for Pool Pumps Version 3.1. Accessible at: https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Version%203.1%20Pool%20Pumps%20Final%20Specification.pdf.
SAVINGS
Measure Name |  |  | Peak Demand Savings | Annual Energy Savings |  |  | Lifetime Energy Savings
Res. VFD Pool Pump
Single-speed to variable speed: > 0 to ≤ 1 hp |  |  | 0.121 | 1062.28 |  |  | 10622.8
Single-speed to variable speed: > 1 to ≤ 2 hp |  |  | 0.085 | 747.25 |  |  | 7472.5
Single-speed to variable speed: > 2 to ≤ 3 hp |  |  | 0.121 | 1060.22 |  |  | 10602.2
Single-speed to variable speed: > 3 to ≤ 4 hp |  |  | 0.484 | 4240.06 |  |  | 42400.6
Dual-speed to variable speed: > 0 to ≤ 1 hp |  |  | 0.099 | 867.21 |  |  | 8672.1
Dual-speed to variable speed: > 1 to ≤ 2 hp |  |  | 0.085 | 747.25 |  |  | 7472.5
Dual-speed to variable speed: > 2 to ≤ 3 hp |  |  | 0.121 | 1060.22 |  |  | 10602.2
Dual-speed to variable speed: > 3 to ≤ 4 hp |  |  | 0.196 | 1714.6 |  |  | 17146
RESOURCES
• | AEG's 2024 Analysis File titled "PY24 TRM - Residential Variable Frequency Drive (VFD) Pool Pump - Analysis File."
• | AEG's 2018 Analysis File titled "AEG HPUC Update of Res Pool Pump VFD - Analysis File."
• | Code of Federal Regulation, Title 10, Subchapter D. Part 431. Subpart Z. § 431.465. Available online at: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-Y/section-431.465
• | Code of Federal Regulation, Title 10, Subchapter D. Part 431. Subpart Z. § 431.485 Available online at: https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-431/subpart-Z/section-431.485
• | DOE National Impact Analysis (NIA) for Dedicated Purpose Pool Pumps ("NIA_PoolPumps_2016-12-19_ForPublication_v2.xlsm"), available online at: https://www.regulations.gov/document?D=EERE-2015-BT-STD-0008-0107.
• | ENERGY STAR Product Specifications for Pool Pumps, Version 3.1, available online at: https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Final%20Version%202.0%20Pool%20Pumps%20Specification.pdf.
• | Regional Technical Forum. Efficient Pool Pumps - Unit Energy Savings Workbook, Version 2.1. Northwest Power and Conservation Council. February 27, 2018. Spreadsheet. Available online at: https://rtf.nwcouncil.org/measure/efficient-pool-pumps.
∆𝑘𝑊ℎ=(〖𝑘𝑊ℎ〗_(𝐷𝑎𝑖𝑙𝑦,𝐵𝑎𝑠𝑒)−〖𝑘𝑊ℎ〗_(𝐷𝑎𝑖𝑙𝑦,𝐸𝑓𝑓) )∗𝐷𝑎𝑦𝑠
∆𝑘𝑊=[(〖𝑘𝑊ℎ〗_(𝐷𝑎𝑖𝑙𝑦,𝐵𝑎𝑠𝑒)/〖𝐻𝑜𝑢𝑟𝑠〗_(𝐷𝑎𝑖𝑙𝑦,𝐵𝑎𝑠𝑒) )∗〖𝐶𝐹〗_𝐵𝑎𝑠𝑒 ]−[(〖𝑘𝑊ℎ〗_(𝐷𝑎𝑖𝑙𝑦,𝐸𝑓𝑓)/〖𝐻𝑜𝑢𝑟𝑠〗_(𝐷𝑎𝑖𝑙𝑦,𝐸𝑓𝑓) )∗〖𝐶𝐹〗_𝐸𝑓𝑓 ]
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗𝐸𝑈𝐿

## R_WH_Heat Pump
RESIDENTIAL: Heat Pump Water Heater
Return to TOC
UPDATE STATUS
Updated in Fall-Winter 2024 for the PY24 TRM. The update added the capability to input the new heat pump water heater's actual Uniform Energy Factor (UEF) rather than use the default UEF value to calculate savings. It also updated the default UEF values with the most recent ENERGY STAR specifications, effective April 18, 2023.
MEASURE DETAILS
Description
Replacement of an Electric Storage Water Heater with an ENERGY STAR-certified Heat Pump Water Heater for residential use.
Program Criteria
The retailers provide rebate applications for water heaters at the time of purchase, or a customer can visit Hawai'i Energy's website and download the form. Rebate applications must include an original purchase receipt showing the brand and model number. The heat pump water heater must be ENERGY STAR certified, 50 up to 82 gallons.
Unit of Measure
One water heater
Baseline Equipment
Baseline equipment is an Electric Storage Water Heater that meets current Federal standards, which were effective April 16, 2015.
High Efficiency Equipment
To qualify for this measure the installed equipment must be an ENERGY STAR certified heat pump water heater. ENERGY STAR qualifying equipment must reach the requirements outlined below in Table 1.
ALGORITHMS
Uniform Energy Factor of Baseline Equipment (Electric Storage Water Heater ≤ 55 gallons)
(1)
Assumes "low" draw pattern
Uniform Energy Factor of Baseline Equipment (Electric Storage Water Heater > 55 gallons)
(2)
Assumes "low" draw pattern
Baseline Annual Energy Use, kWh/yr
(3)
Efficient Case Annual Energy Use, kWh/yr
(4)
Annual Energy Savings, kWh/yr
(5)
Peak Demand Reduction, kW
(6)
Lifetime Energy Savings, kWh
(7)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [10 empty] | Value |  |  |  | Unit |  |  |  | Source/Notes
UEFbase |  |  |  | Uniform Energy Factor1 of the baseline | [10 empty] | See Eq'n 1 or 2 depending on Rated Storage Volume |  |  |  | - |  |  |  | Default UEFbase values assume 50 gallon or 60 gallon Electric Storage Water Heater and Low Draw Pattern.
UEFEff |  |  |  | Uniform Energy Factor of the Heat Pump Water Heaters | [10 empty] | Actual or Table 2 |  |  |  | - |  |  |  | Table 2 values based on ENERGY STAR Product Finder (Jan 2024) and Program requirements of 50-82 gallons <https://www.energystar.gov/productfinder/product/certified-water-heaters/results>.
GPDOcc |  |  |  | Daily hot water use per occupant | [10 empty] | 15 |  |  |  | gal/day-person |  |  |  | AEG's Fall 2018 Benchmarking.
#Occ |  |  |  | Average number of occupants per home | [10 empty] | Actual or Table 3 (default = 3.16) |  |  |  | persons |  |  |  | 2019 Hawaii Statewide Baseline Energy Use Study;2 default is occupancy for non-military single family homes.
ρ |  |  |  | Density of water | [10 empty] | 8.3 |  |  |  | lbm/gal |  |  |  | -
cp |  |  |  | Specific heat capacity of water | [10 empty] | 1 |  |  |  | Btu/lbm°F |  |  |  | -
Tout |  |  |  | Outlet temperature of the water heater | [10 empty] | 125 |  |  |  | °F |  |  |  | Outlet water temperatures typically range from 120 to 140°F. 125 ± 5°F is the temperature prescribed in Uniform Test Method for Measuring the Energy Consumption of Water Heaters.3
Tin |  |  |  | Incoming water temperature from the water main | [10 empty] | See Table 4 (default = 75) | 8760 | 8760 | 8760 | °F |  |  |  | Hawai‘i Energy.4
EFLH | HOURS | HOURS | HOURS | Equivalent full load hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | See Table 4 (default = 3,564) |  |  |  | hrs |  |  |  | AEG's 2018 Hawaii-specific analysis of U.S. DOE OpenEI Load shapes for Residential Electric Water Heating.
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | See Table 4 (default = 0.53) |  |  |  | - |  |  |  | AEG's 2018 Hawaii-specific analysis of U.S. DOE OpenEI Load shapes for Residential Electric Water Heating; peak period defined as non-holiday weekdays from 5-9 pm.
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 10 |  |  |  | yrs |  |  |  | DEER 2020.
1. Assumed draw pattern is "low." Source for UEF equation: Electronic Code of Federal Regulations: <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>.
2. Source for occupancy: 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. (Responses to Question 71 of the Residential Phone / Audit Survey.)
3. Source for Tout: Electronic Code of Federal Regulations, Appendix E to Subpart B of Part 430 <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-B>.
4. Hawai‘i Energy Solar Water Heating Program Handbook, Table 2.
Table 1. Criteria for Certified Electric Water Heaters
Criteria | [17 empty] | ENERGY STAR Version 5.0 Requirements, Effective April 18, 2023
Uniform Energy Factor | [7 empty] | Integrated HPWH | [9 empty] | UEF ≥ 3.30
[8 empty] | Integrated HPWH, 120 Volt / 15 Amp Circuit | [9 empty] | UEF ≥ 2.20
[8 empty] | Split-system HPWH | [9 empty] | UEF ≥ 2.20
First-Hour Rating | [17 empty] | FHR ≥ 45 gallons per hour
Warranty | [17 empty] | Warranty ≥ 6 years on sealed system
Safety | [17 empty] | UL 174 and UL 1995 or UL 60335-2-40
Lower Compressor Cut-Off Temperature (Reporting Requirement Only) | [17 empty] | Report ambient temperature below which the compressor cuts off and electric resistance only operation begins
Upper Compressor Cut-Off Temperature (Optional Reporting Only) | [17 empty] | Partners may report the ambient temperature above which the compressor cuts off and electric resistance only operation begins
Source: ENERGY STAR Program Requirements, Product Specification for Residential Water Heaters, V5.0, <https://www.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20Residential%20Water%20Heaters%20Version%205.0%20Specification%20and%20Partner%20Commitments.pdf>.
Table 2. Average UEF of Heat Pump Water Heaters
Type of Heat Pump Water Heater | [17 empty] | UEF
Heat Pump Water Heater, 50 ≤ x ≤ 55 gal storage tank | [17 empty] | 3.6
Heat Pump Water Heater, 55 < x ≤ 82 gal storage tank | [17 empty] | 3.62
Source: ENERGY STAR Product Finder (Jan 2024): <https://www.energystar.gov/productfinder/product/certified-water-heaters/results>
Table 3. Average Occupancy in Homes | [13 empty] | Table 4. EFLH, CF, and Tin
Type of Home | [6 empty] | No. of Occupants | [6 empty] | Factor |  |  | County
Unspecified | [6 empty] | 3.16 | [9 empty] | Hawaii |  |  | Honolulu |  |  | Maui |  | Unspecified
Hawai‘i Non-Military (SF or MF) | [6 empty] | 2.56 | [6 empty] | EFLH |  |  | 3569 |  |  | 3564 |  |  | 3567 |  | 3564
Honolulu Non-Military (SF or MF) | [6 empty] | 2.96 | [6 empty] | CF |  |  | 0.53 |  |  | 0.53 |  |  | 0.53 |  | 0.53
Maui Non-Military (SF or MF) | [6 empty] | 3.04 | [6 empty] | Tin |  |  | 75 |  |  | 75 |  |  | 71 |  | 75
SF Non-Military (Any County) | [6 empty] | 3.16
MF Non-Military (Any County) | [6 empty] | 2.34
Military (SF or MF) | [6 empty] | 3.82
Custom | [6 empty] | Actual
SF = single family home
MF = multifamily home
SAVINGS
Deemed Savings (based on default values for key parameters)
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Residential Heat Pump Water Heater, ≤ 55 gal | [7 empty] | 0.257 | [7 empty] | 1728.07 | [7 empty] | 17280.7
Residential Heat Pump Water Heater, > 55 gal | [7 empty] | 0.072 | [7 empty] | 482.89 | [7 empty] | 4828.9
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
Enter Type of Home or Custom Occupancy (if known)
[5 empty] | Unspecified | [15 empty] | Average Occupancy = | 3.16
[21 empty] | Custom Occupancy = | 4
Enter Rated Storage Volume in gallons for the New Heat Pump Water Heater (default of 50 gal)
[5 empty] | 60 | [5 empty] | UEFbase = |  |  | 1.978
Enter UEF for Heat Pump Water Heater (default of 3.60 for ≤ 55 gal storage tank and 3.62 for > 55 gal storage tank)
3.62
Enter County (default of Honolulu)
[5 empty] | Unspecified | [5 empty] | EFLH = |  |  | 3564 |  |  |  |  | CF = |  | 0.53 |  |  |  |  | Tin = | 75
Measure Name | [7 empty] | Peak Demand Savings | [7 empty] | Annual Energy Savings | [7 empty] | Lifetime Energy Savings
Residential Heat Pump Water Heater | [7 empty] | 0.072 | [7 empty] | 482.89 | [7 empty] | 4828.9
Note: Savings shown in blue result from sample entries above. They are for illustrative purposes only.
RESOURCES
• | AEG's 2024 Analysis Files titled "PY24 TRM - Residential Heat Pump Water Heater - Analysis File."
• | AEG's 2022 Analysis Files titled "PY22 R_WH_Heat Pump - Analysis File" and Mid-year PY22 TRM - Residential Heat Pump Water Heater - Analysis File."
• | AEG's 2020 Analysis File titled "WHF SAF and HPWH PY20 Updates."
• | AEG's 2018 analysis of U.S. DOE OpenEI Load shapes for Residential Electric Water Heating. Used B10 Benchmark, Base Load prototype for IECC Zone 1A and Hawai‘i weather stations (Keahole-Kona.Intl.AP, Honolulu.Intl.AP, Kahului.AP). Prototype data available here: <https://openei.org/doe-opendata/dataset/commercial-and-residential-hourly-load-profiles-for-all-tmy3-locations-in-the-united-states>.
• | 2019 Hawaii Statewide Baseline Energy Use Study, Appendices, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, DRAFT, in progress. (Responses to Question 71 of the Residential Phone /Audit Survey.)
• | DEER 2020: <http://www.deeresources.com/index.php/deer-versions/deer2020#EUL>.
• | Electronic Code of Federal Regulations: Title 10: Energy, Part 430 - Energy Conservation Program for Consumer Products. Subpart C - Energy and Water Conservation Standards. Section 6d. <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>.
• | Electronic Code of Federal Regulations, Appendix E to Subpart B of Part 430 <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-B>.
• | ENERGY STAR Product Finder: <https://www.energystar.gov/productfinder/product/certified-water-heaters/results>.
• | ENERGY STAR Program Requirements, Product Specification for Residential Water Heaters, V5.0, effective April 18, 2023, <https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Residential%20Water%20Heaters%20Version%205.0%20Specification%20and%20Partner%20Commitments.pdf>.
• | Regional Technical Forum. Residential Heat Pump Water Heater - Unit Energy Savings Workbook, Version 4.1. Northwest Power and Conservation Council. April 19, 2018. Spreadsheet. "ResHPWH_v4_1.xlsm." Uses SEEM Simulation Model Version 0.98 build May 29 2015 13:41:19.
〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒=(1/〖𝑈𝐸𝐹〗_𝑏𝑎𝑠𝑒 )∗(〖𝐺𝑃𝐷〗_𝑂𝑐𝑐∗#𝑂𝑐𝑐∗365 𝑑𝑎𝑦𝑠∗𝜌∗𝑐_𝑝∗(𝑇_𝑜𝑢𝑡−𝑇_𝑖𝑛 ))/(3412 𝐵𝑡𝑢/𝑘𝑊ℎ)
〖𝑈𝐸𝐹〗_𝑏𝑎𝑠𝑒=0.9254−(0.0003∗𝑅𝑎𝑡𝑒𝑑 𝑆𝑡𝑜𝑟𝑎𝑔𝑒 𝑉𝑜𝑙𝑢𝑚𝑒 𝑖𝑛 𝑔𝑎𝑙𝑙𝑜𝑛𝑠)
〖𝑈𝐸𝐹〗_𝑏𝑎𝑠𝑒=2.0440−(0.0011∗𝑅𝑎𝑡𝑒𝑑 𝑆𝑡𝑜𝑟𝑎𝑔𝑒 𝑉𝑜𝑙𝑢𝑚𝑒 𝑖𝑛 𝑔𝑎𝑙𝑙𝑜𝑛𝑠)
〖𝑘𝑊ℎ〗_𝐸𝑓𝑓=(1/〖𝑈𝐸𝐹〗_𝐸𝑓𝑓 )∗(〖𝐺𝑃𝐷〗_𝑂𝑐𝑐∗#𝑂𝑐𝑐∗365 𝑑𝑎𝑦𝑠∗𝜌∗𝑐_𝑝∗(𝑇_𝑜𝑢𝑡−𝑇_𝑖𝑛 ))/(3412 𝐵𝑡𝑢/𝑘𝑊ℎ)
∆𝑘𝑊=∆𝑘𝑊ℎ/𝐸𝐹𝐿𝐻∗𝐶𝐹
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
∆𝑘𝑊ℎ=(〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊ℎ〗_𝐸𝐸 )

## R_WH_SWH
RESIDENTIAL: Solar Water Heater
Return to TOC
UPDATE STATUS
Updated in Winter 2023-2024 for the PY24 TRM. This update clarifies the baseline conditions by tying the baseline tank size to the number of people in the household and also revises the default outlet water heater temperature to be consistent with the heat pump water heater measure.
MEASURE DETAILS
Description
Replacement of an Electric Storage Water Heater with a Solar Water Heater designed for a 90% Solar Fraction. The new Solar Water Heating systems often include upgrading the hot water storage tank capacity to 80 or 120 gallons.
Program Criteria
The retailers provide rebate applications for water heaters at the time of purchase, or a customer can visit the Hawai‘i Energy website and download the form. Rebate applications must include an original purchase receipt showing the brand and model number.
New Construction: New construction single-family homes do not qualify. Per the legislation, new homes in Hawai‘i must have Solar Water Heaters as of 2010, with a few exceptions.
Unit of Measure
One system.
Baseline Equipment
Baseline equipment is an Electric Storage Water Heater that meets current Federal codes and standards effective April 16, 2015. The baseline storage tank is typically sized based on the number of people in the household and their typical daily hot water use. Proposed federal standards will require a heat pump water heater in the baseline, effective 2029.
High Efficiency Equipment
High efficiency equipment is a new Solar Water Heater with electric backup designed for a 90% Solar Fraction. The Solar Water Heating collectors must meet the Solar Rating and Certification Corporation (SRCC™) OG-100 standard. OG-300 certification for the solar water heating system is not required. Solar Water Heating systems use solar thermal energy to meet most of the water heating load and continue to utilize electricity to operate the circulation pump and provide heating through an electric resistance element when needed.
ALGORITHMS
Uniform Energy Factor of Baseline Equipment (Electric Storage Water Heater ≤ 55 gallons)
(1)
Assumes "low" draw pattern
Uniform Energy Factor of Baseline Equipment (Electric Storage Water Heater > 55 gallons)
(2)
Assumes "low" draw pattern
Baseline Annual Energy Use, kWh/hr
(3)
Efficient Case Annual Energy Use, kWh/hr
(4)
Annual Energy Savings, kWh/yr
(5)
Peak Demand Reduction, kW
(6)
Lifetime Energy Savings, kWh
(7)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [10 empty] | Value |  |  |  | Unit |  |  |  | Source/Notes
UEFbase |  |  |  | Uniform energy factor of the baseline equipment1 | [10 empty] | See Equation 1 (default = 0.9104) and Equation 2 (default = 1.978) |  |  |  | - |  |  |  | Default UEF assumes a 50 gallon electric storage water heater tank for 5 or fewer occupants and 60 gallons for more than 5 occupants
Vbase |  |  |  | Rated storage volume of baseline equipment | [10 empty] | See Table 1 |  |  |  | gallons |  |  |  | US DOE2 and Mills3
GPDOcc |  |  |  | Daily hot water use per occupant | [10 empty] | 15 |  |  |  | gal/day-person |  |  |  | AEG's Fall 2018 Benchmarking
#Occ |  |  |  | Average number of occupants per Home | [10 empty] | Actual or Table 2 (default = 3.16 or 6 depending on the new solar water heater tank size) |  |  |  | persons |  |  |  | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Derived from responses to Q71 of the residential phone / audit survey. (Military occupancy is from Evergreen Economics Baseline Study, 2014.) Default is occupancy for non-military single family homes.
ρ |  |  |  | Density of water | [10 empty] | 8.3 |  |  |  | lbm/gal |  |  |  | -
cp |  |  |  | Specific heat capacity of water | [10 empty] | 1 |  |  |  | Btu/lbm°F |  |  |  | -
Tout |  |  |  | Outlet temperature of the water heater | [10 empty] | 125 |  |  |  | °F |  |  |  | Outlet water temperatures typically range from 120 to 140°F. 125 ± 5°F is the temperature prescribed in Uniform Test Method for Measuring the Energy Consumption of Water Heaters.4
Tin |  |  |  | Incoming water temperature from the water main | [10 empty] | See Table 3 (default = 75) | 8760 | 8760 | 8760 | °F |  |  |  | Hawai‘i Energy5
SF |  |  |  | Solar fraction | [10 empty] | User input (default = 0.9) |  |  |  | - |  |  |  | Program requirement is 0.9
UEFSWH |  |  |  | Energy factor of solar water heater when using back-up electric resistance heating | [10 empty] | 0.9 |  |  |  | - |  |  |  | Typical value for electric resistance water heating; equal to efficiency assumption of 0.9 from PY18 TRM
kWpump |  |  |  | Circulation pump demand | [10 empty] | 0.082 |  |  |  | kW |  |  |  | No change from PY18 TRM; Source: KEMA 2005-20076
HOUpump |  |  |  | Pump hours of operation | [10 empty] | 1292 |  |  |  | hr/yr |  |  |  | No change from PY18 TRM; Source: KEMA 2005-20076
PF | PF | PF | PF | Persistence factor | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | persistence factor (% of measures installed and operational) | 0.93 | 0.93 | 0.93 | 0.93 | - |  |  |  | KEMA 2005-2007 report found 7% of solar water heating systems evaluated to be "inoperable"7
EFLH | HOURS | HOURS | HOURS | Equivalent full load hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | annual hours of equipment operation | See Table 3 (default = 3,564) | 8760 | 8760 | 8760 | hrs |  |  |  | AEG's Hawai‘i-specific analysis of U.S. DOE OpenEI Load shapes for Residential Electric Water Heating
CF | CF | CF | CF | Peak demand coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | See Table 3 (default = 0.53) |  |  |  | - |  |  |  | AEG's Hawai‘i-specific analysis of U.S. DOE OpenEI Load shapes for Residential Electric Water Heating; peak period defined as non-holiday weekdays from 5-9 pm
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 18 | 20 years | 20 years | 20 years | yrs |  |  |  | AEG's Fall 2018 Benchmarking
1 Source for UEF equation: Electronic Code of Federal Regulations: <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-C/section-430.32>
2 AEG estimates based on DOE's Sizing a New Water Heater. <https://www.energy.gov/energysaver/sizing-new-water-heater>
3 Hubert Miles, Choose What Size Water Heater You Need Like a Pro. Updated on January 15, 2024. <https://homeinspectioninsider.com/what-size-water-heater-you-need/>
4 Source for Tout: Electronic Code of Federal Regulations, Appendix E to Subpart B of Part 430 <https://www.ecfr.gov/current/title-10/chapter-II/subchapter-D/part-430/subpart-B>.
5 Hawai‘i Energy Solar Water Heating Program Handbook, Table 2. Maui value is average across 19 locations in Maui County (Range: 64-74°F). Primary source of data is the Maui Board of Water Supply.
6 This KEMA report has been referenced in Hawai‘i Energy's TRM algorithms for solar water heating since the PY11 TRM, and may have been in use to estimate savings prior to PY11. The report is cited as "KEMA 2005-2007 Energy and Peak Demand Impact Evaluation Report" and appears to describe a water heating study conducted by KEMA. AEG and the EEM were unable to locate the original KEMA evaluation report, despite inquiring directly with DNV GL (KEMA is now a part of DNV GL). From what AEG can ascertain from the past Hawai‘i Energy TRMs, the circulation pump demand and pump hours of operation were determined from metering a sample of systems. AEG recommends collecting new data to update these values in a future TRM update.
7 From what AEG can ascertain from the past Hawai‘i Energy TRMs, "inoperable" was defined by KEMA as solar water heating systems that use more than an average of 5 kWh per day. The reference for the definition of "inoperable" is cited in past Hawai‘i Energy TRMs as: "Impact Evaluation Report of the 2001-2003 Demand Side Management Programs," KEMA, page 2-36, 2004.
KEMA's solar water heating study involved metering energy and peak demand for a sample of 260 solar water heaters. Of these, 18 (7%) were considered to be in a state of disrepair that made them essentially "inoperable" as solar water heaters. In this "inoperable" state, they used an average of 3,925 kWh/yr, which is more than the current baseline energy use. Additional details about the study, including characteristics of the units tested (age, capacity, maintenance history, etc.) and the metering approach (equipment used, time of year, measurement period, etc.) were not provided in the past TRMs, so these details about the approach could not be verified by AEG. In addition, due to the general lack of published data on solar water heater savings persistence, AEG was unable to find benchmarking information to help validate KEMA's findings. As such, the persistence factor was reviewed, but not updated, for the PY19 TRM. As more data becomes available on savings degradation of solar water heating systems relative to baseline equipment, the persistence factor should be reevaluated for future TRMs.
Table 1. Rated Storage Volume of Electric Storage Water Heater, per Occupancy
No. of Occupants | [6 empty] | Rated Storage Volume (gallons)1,2
#Occ ≤ 2 | [6 empty] | 35
2 < #Occ ≤ 3 | [6 empty] | 40
3 < #Occ ≤ 4 | [6 empty] | 50
4 < #Occ ≤ 5 | [6 empty] | 55
5 < #Occ ≤ 6 | [6 empty] | 60
#Occ. > 6 | [6 empty] | 80
1 AEG estimates based on DOE's Sizing a New Water Heater. <https://www.energy.gov/energysaver/sizing-new-water-heater>
2 Hubert Miles, Choose What Size Water Heater You Need Like a Pro. Updated on January 15, 2024. <https://homeinspectioninsider.com/what-size-water-heater-you-need/>
Table 2. Average Occupancy in Homes | [13 empty] | Table 3. EFLH, CF, and Tin
Type of Home | [6 empty] | No. of Occupants | [6 empty] | Factor |  |  | County
Unspecified ( ≤ 80 gallon solar water heater tank) | [6 empty] | 3.16 | [9 empty] | Hawai‘i |  |  | Honolulu |  |  | Maui |  | Unspecified
Unspecified ( > 80 gallon solar water heater tank) | [6 empty] | 6 | [6 empty] | EFLH 1 |  |  | 3569 |  |  | 3564 |  |  | 3567 |  | 3564
Hawai‘i Non-Military (SF or MF) | [6 empty] | 2.56 | [6 empty] | CF 1 |  |  | 0.53 |  |  | 0.53 |  |  | 0.53 |  | 0.53
Honolulu Non-Military (SF or MF) | [6 empty] | 2.96 | [6 empty] | Tin 2 |  |  | 75 |  |  | 75 |  |  | 71 |  | 75
Maui Non-Military (SF or MF) | [6 empty] | 3.04 | [6 empty] | 1 Source of EFLH and CF: AEG 2018 analysis of U.S. DOE OpenEI Load shape for Residential Electric Water Heating
SF Non-Military (Any County) | [6 empty] | 3.16 | [6 empty] | 2 Source of Tin: Hawai‘i Energy Solar Water Heating Program Handbook, Table 2; Maui value is average across 19 locations in Maui County (Range: 64-74°F)
MF Non-Military (Any County) | [6 empty] | 2.34
Military (SF or MF) | [6 empty] | 3.82
Custom | [6 empty] | Actual
SF = single family home
MF = multifamily home
Source: 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Derived from responses to Q71 of the residential phone / audit survey. (Military occupancy is from Evergreen Economics Baseline Study, 2014.)
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
SAVINGS
Deemed Savings (based on default values for key parameters)
Measure Name | [7 empty] | Peak Demand Savings |  |  |  | 5: Annual Energy Savings | Lifetime Energy Savings
Residential Solar Water Heater, ≤ 5 occupants | [7 empty] | 0.273 |  |  |  | 5: 1833.64 | 33005.52
Residential Solar Water Heater, > 5 occupants | [7 empty] | 0.203 |  |  |  | 5: 1367.19 | 24609.42
Semi-Prescriptive Savings Calculator (based on customer-specific values for key parameters)
Enter Occupancy of Home (default of 3.16 people)
[5 empty] | 5 | [6 empty] | 2: Vbase =; 5: 55; 10: EF =; 12: 0.9089
Enter Solar Fraction for new Solar Water Heater (default of 0.9)
0.9
Enter County (default of Honolulu)
[5 empty] | Honolulu | [5 empty] | EFLH = | 3: 3564; 8: CF =; 10: 0.53 |  |  | Tin = | 75
Measure Name | [7 empty] | Peak Demand Savings |  |  |  | 5: Annual Energy Savings | Lifetime Energy Savings
Residential Solar Water Heater | [7 empty] | 0.441 |  |  |  | 5: 2964.32 | 53357.76
Note: Savings shown in blue result from sample entries above. They are for illustrative purposes only.
RESOURCES
• | AEG's Analysis Files titled "PY24 TRM - Residential Solar Water Heater - Analysis File."
• | AEG's Analysis Files titled "PY24 TRM - Residential Heat Pump Water Heater - Analysis File."
• | AEG's Analysis Files titled 1) "AEG HPUC Update of Residential Measures - Analysis file," 2) "R&C Solar Water Heater - v2 Solar Fraction," and 3) "AEG HPUC Baseline Study Data - Analysis File."
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | AEG's 2018 analysis of U.S. DOE OpenEI Load shapes for Residential Electric Water Heating. Used B10 Benchmark, Base Load prototype for IECC Zone 1A and Hawai‘i weather stations (Keahole-Kona.Intl.AP, Honolulu.Intl.AP, Kahului.AP). Prototype data available here: https://openei.org/doe-opendata/dataset/commercial-and-residential-hourly-load-profiles-for-all-tmy3-locations-in-the-united-states.
• | Baseline Energy Appliance, Equipment and Building Characteristics Study Report, Prepared for the State of Hawaii Public Utilities Commission, November 6, 2013, With errata February 26, 2014, Evergreen Economics.
• | Connecticut's 2018 Program Savings Document, 13th Edition, filed December 15, 2017. https://www.energizect.com/sites/default/files/2018-PSD-FINAL-121217.pdf.
• | Energy and Peak Demand Impact Evaluation Report of the 2005-2007 Demand Management Programs – (KEMA 2005-07)
• | ENERGY STAR Program Requirement for Residential Water Heaters, v3.0, April 2015, https://www.energystar.gov/products/water_heaters/residential_water_heaters_key_product_criteria.
• | ENERGY STAR websites and resources: https://www.energy.gov/energysaver/water-heating/solar-water-heaters, https://www.energy.gov/energysaver/estimating-cost-and-energy-efficiency-solar-water-heater, https://www.energystar.gov/ia/partners/prod_development/new_specs/downloads/water_heaters/WaterHeaterAnalysis_Final.pdf
• | Energy.gov, Solar Water Heating Requirement for New Residential Construction, State of Hawai‘i, https://www.energy.gov/savings/solar-water-heating-requirement-new-residential-construction.
• | Federal Register, Energy Conservation Program for Consumer Products: Definitions for Residential Water Heaters, Table I.2, April 8, 2015, available here: https://www.federalregister.gov/documents/2015/04/08/2015-07956/energy-conservation-program-for-consumer-products-definitions-for-residential-water-heaters.
• | Hawai‘i Energy Solar Water Heating Program Handbook: Design Guidelines, Volume 5, October 2018, available for download here: <https://hawaiienergy.com/files/for-homes/swh_handbook.pdf>.
• | Hubert Miles, Choose What Size Water Heater You Need Like a Pro. Updated on January 15, 2024. <https://homeinspectioninsider.com/what-size-water-heater-you-need/>
• | International Code Council (ICC) and Solar Rating & Certification Corporation (SRCC), 2015 ICC 900/SRCC 300-2015 Solar, Thermal System Standard, https://codes.iccsafe.org/content/ICC9002015/toc.
• | Public Utility Commission of Texas, Texas Technical Reference Manual, Version 5.0, Volume 2: Residential Measures, Program Year (PY) 2018, October 2017.
• | Regional Technical Forum. Residential Heat Pump Water Heater - Unit Energy Savings Workbook, Version 4.1. Northwest Power and Conservation Council. April 19, 2018. Spreadsheet. "ResHPWH_v4_1.xlsm." Uses SEEM Simulation Model Version 0.98 build May 29 2015 13:41:19.
• | Saying Mahalo to Solar Savings: A Billing Analysis of Solar Water Heaters in Hawai‘i, Jenny Yaillen, Evergreen Economics, Chris Ann Dickerson, CAD Consulting, Wendy Takanish and John Cole, Hawaii Public Utilities Commission, ©2012 ACEEE Summer Study on Energy Efficiency in Buildings.
• | STATE OF HAWAI‘I SOLAR WATER HEATING IMPACT ASSESSMENT (1992 - 2011) Prepared For: Department of Business and Economic Development and Tourism (DBEDT) State of Hawai‘i FINAL December 18, 2012 Prepared by: InSynergy Engineering, Inc. Honolulu, HI.
• | System Advisor Model (SAM) is a performance and financial model designed to facilitate decision making for people involved in the renewable energy industry, https://sam.nrel.gov/.
• | Technical Reference Manual, State of Pennsylvania, Act 129 Energy Efficiency and Conservation Program & Act 213 Alternative Energy Portfolio Standards, June 2016.
• | Tennessee Valley Authority Technical Reference Manual, Version 6.0, Oct. 1, 2017.
• | Title 10: Energy, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart B—Test Procedures, Appendix E to Subpart B of Part 430—Uniform Test Method for Measuring the Energy Consumption of Water Heaters, https://www.ecfr.gov/cgi-bin/text-idx?SID=80dfa785ea350ebeee184bb0ae03e7f0&mc=true&node=ap10.3.430_127.e&rgn=div9
• | Title 10: Energy, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates, (d) Water heaters.
• | United Nations Framework Convention of Climate Change, Small-scale Methodology: Solar water heating systems, Version 02.0, Sectoral scope(s): 01, Clean Development Mechanism, AMS-I.J, Aug. 31, 2018, available for download here: <https://cdm.unfccc.int/methodologies/DB/7FWC9VI15EMP2EOCF44OUZH9XHLL5W>.
• | US Department of Energy, Sizing a New Water Heater, <https://www.energy.gov/energysaver/sizing-new-water-heater>.
∆𝑘𝑊=∆𝑘𝑊ℎ/𝐸𝐹𝐿𝐻∗𝐶𝐹
〖𝑈𝐸𝐹〗_𝑏𝑎𝑠𝑒=0.9254−(0.0003∗𝑉_𝑏𝑎𝑠𝑒 )
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒=(1/〖𝑈𝐸𝐹〗_𝑏𝑎𝑠𝑒 )∗(〖𝐺𝑃𝐷〗_𝑂𝑐𝑐∗#𝑂𝑐𝑐∗365 𝑑𝑎𝑦𝑠∗𝜌∗𝑐_𝑝∗(𝑇_𝑜𝑢𝑡−𝑇_𝑖𝑛 ))/(3412 𝐵𝑡𝑢/𝑘𝑊ℎ)
∆𝑘𝑊ℎ=(〖𝑘𝑊ℎ〗_𝑏𝑎𝑠𝑒−〖𝑘𝑊ℎ〗_𝐸𝐸 )∗𝑃𝐹
〖𝑘𝑊ℎ〗_𝐸𝐸=(1−𝑆𝐹)(1/〖𝑈𝐸𝐹〗_𝑆𝑊𝐻 )∗(〖𝐺𝑃𝐷〗_𝑂𝑐𝑐∗#𝑂𝑐𝑐∗365 𝑑𝑎𝑦𝑠∗𝜌∗𝑐_𝑝∗(𝑇_𝑜𝑢𝑡−𝑇_𝑖𝑛 ))/(3412 𝐵𝑡𝑢/𝑘𝑊ℎ)+〖(𝑘𝑊〗_𝑝𝑢𝑚𝑝∗〖𝐻𝑂𝑈〗_𝑝𝑢𝑚𝑝)
〖𝑈𝐸𝐹〗_𝑏𝑎𝑠𝑒=2.0440−(0.0011∗ 𝑉_𝑏𝑎𝑠𝑒 )

## R_WH_SWH Tune Up
RESIDENTIAL: Solar Water Heater Tune Up
Return to TOC
UPDATE STATUS
Updated in Fall 2018 for PY19 TRM.
MEASURE DETAILS
Description
Maintenance and repair of residential solar water heating systems for optimum performance.
Program Criteria
Systems must be more than 3 years old and can only receive a tune-up incentive once every 5 years.
Unit of Measure
One system.
Baseline Equipment
Average per unit energy use (kWh) and on-peak demand (kW) for the baseline solar water heater was estimated by KEMA using field measurements on a sample of 260 solar water heaters. The baseline values represent a blend of 242 "operable" and 18 "inoperable" systems, where "inoperable" refers to systems requiring maintenance and repair. Inoperable systems are defined as systems that use more than an average of 5 kWh per day.
High Efficiency Equipment
Average per unit energy use (kWh) and on-peak demand (kW) for the high efficiency solar water heater was estimated by KEMA using field measurements on the 242 "operable" systems within the sample of 260 solar water heaters tested.
ALGORITHMS
Peak Demand Reduction, kW
(1)
Annual Energy Savings, kWh/yr
(2)
Lifetime Energy Savings, kWh
(3)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description |  | Value | Unit | Source/Notes
Pbase |  |  |  | On Peak Demand, group "All" |  | 0.079 | kW | KEMA 2005-2007 report1
Pop |  |  |  | On Peak Demand, group "Operating" |  | 0.05 | kW | KEMA 2005-2007 report
Ebase |  |  |  | kWh per Unit, group "All" |  | 577 | kWh | KEMA 2005-2007 report
Eop |  |  |  | kWh per Unit, group "Operating" |  | 328 | kWh | KEMA 2005-2007 report
PF |  |  |  | Persistence factor |  | 0.5 | - | Factor accounts for savings degradation between tune-ups; the value of 0.5 assumes linear degradation of savings across measure life.
EULEE | Measure Life | Measure Life | Measure Life | Effective useful life of measure |  | 5 | yrs
1 This KEMA report has been referenced in Hawai‘i Energy's TRM algorithms for solar water heating since the PY11 TRM, and may have been in use to estimate savings prior to PY11. The report is cited as "KEMA 2005-2007 Energy and Peak Demand Impact Evaluation Report" and appears to describe a water heating study conducted by KEMA. AEG and the EEM were unable to locate the original KEMA evaluation report, despite inquiring directly with DNV GL (KEMA is now a part of DNV GL). From what AEG can ascertain from the past Hawai‘i Energy TRMs, "inoperable" was defined by KEMA as solar water heating systems that use more than an average of 5 kWh per day. The reference for the definition of "inoperable" is cited in past Hawai‘i Energy TRMs as: "Impact Evaluation Report of the 2001-2003 Demand Side Management Programs," KEMA, page 2-36, 2004.
KEMA's solar water heating study involved metering energy and peak demand for a sample of 260 solar water heaters. Of these, 18 (7%) were considered to be in a state of disrepair that made them essentially "inoperable" as solar water heaters. Additional details about the study, including characteristics of the units tested (age, capacity, maintenance history, etc.) and the metering approach (equipment used, time of year, measurement period, etc.) were not provided in the past TRMs, so these details about the approach could not be verified by AEG. In addition, due to the general lack of published data on savings from solar water heater maintenance and repair measures, AEG was unable to find benchmarking information to help validate KEMA's findings. As such, the energy and peak demand values for the baseline and high efficiency cases were reviewed, but not updated, for the PY19 TRM. However, AEG did add a persistence factor to the algorithms to account for gradual degradation of savings between tune-ups. As new data becomes available on savings from tune-ups, this measure entry should be reevaluated for future TRMs.
SAVINGS
Measure Name |  |  |  |  | Peak Demand Savings | Annual Energy Savings |  |  | Lifetime Energy Savings
Solar WH Tune Up |  |  |  |  | 0.015 | 124.5 |  |  | 622.5
RESOURCES
• | AEG's 2018 Analysis File titled "AEG HPUC Update of Residential Measures - Analysis file."
• | Hawai‘i Energy Efficiency Program, Program Year 3, July 2011 through June 2012, Technical Reference Manual, No. 2011, Measure Savings Calculations.
• | Solar Hot Water System Specifications and Requirements, Form: SHW102, Environmental Protection Agency, https://www.epa.gov/sites/production/files/2016-01/documents/webinar_20140416_systemspecifications.pdf.
• | Solar Water Heating System Maintenance and Repair, Energy Saver webpage, Department of Energy, accessed 11/21/2018, https://www.energy.gov/energysaver/solar-water-heating-system-maintenance-and-repair.
〖∆𝑘𝑊ℎ〗_𝑙𝑖𝑓𝑒=∆𝑘𝑊ℎ∗〖𝐸𝑈𝐿〗_𝐸𝐸
∆𝑘𝑊ℎ=(𝐸_𝑏𝑎𝑠𝑒−𝐸_𝑜𝑝 )∗𝑃𝐹
∆𝑘𝑊=(𝑃_𝑏𝑎𝑠𝑒−𝑃_𝑜𝑝 )∗𝑃𝐹

## R_WH_Faucet Aerator
RESIDENTIAL: Faucet Aerator
Return to TOC
UPDATE STATUS
Updated in Winter 2019-2020 for PY20 TRM.
MEASURE DETAILS
Description
Efficient Low-Flow Aerators (bathroom and kitchen).
Program Criteria
Qualified low-flow bathroom aerators and kitchen swivel aerators are provided directly by Hawai‘i Energy via online store or direct-install program.
Unit of Measure
One aerator.
Baseline Equipment
For the direct-install program, the savings approach assumes early retirement (ER). A dual baseline approach is used since Hawaii adopted new state standards for faucets and aerators in 2019, which will be effective as of 1/1/2021. The first baseline will be a 2.2 gpm aerator per current Federal regulations in effect since 1994. The second baseline will be 1.2 gpm for bathroom faucet aerators and 1.8 gpm for kitchen faucet aerators per Hawaii's new state standards.
For the online marketplace, the savings approach assumes replace-on-burnout (ROB). A single baseline approach is used. For July 1 - December 31, 2020, the online marketplace baseline will be 2.2 gpm per current Federal regulations in effect since 1994. After January 1, 2021, the baseline will be 1.2 gpm for bathroom faucet aerators and 1.8 gpm for kitchen faucet aerators per Hawaii's new state standards.
High Efficiency Equipment
1.0 gpm bathroom faucet aerator or 1.5 gpm kitchen swivel aerator.
ALGORITHMS
First Baseline Peak Demand Reduction, kW
(1)
Second Baseline Peak Demand Reduction, kW
(2)
First Baseline Annual Energy Savings, kWh/yr
(3)
Second Baseline Annual Energy Savings, kWh/yr
(4)
Lifetime Energy Savings, kWh
Dual baseline (Direct-Install):
(5)
Single baseline (Online Marketplace, July 1 - December 31, 2020):
(6)
Single baseline (Online Marketplace, January 1, 2021 and later):
(7)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [7 empty] | Bathroom |  |  | Kitchen |  | Unit |  | Sources/Notes
Peak kW / Annual kWh |  |  |  | Ratio of Peak kW to Annual kWh | [7 empty] | 0.0002 |  |  |  |  | 1/hr |  | AEG's approach to calculate this parameter for Hawaii is similar to the Texas TRM v6.0 and Arkansas TRM v7.0 approaches, except modified to reflect Hawaii's peak demand period of 5-9 PM non-holiday weekdays. The approach for Hawaii also uses daily water use profiles from the Water Research Foundation's 2016 Residential End Use of Water study.1
gpmbase1 | gpm_base | gpm_base | gpm_base | 1st baseline flow rate | [7 empty] | 2.2 |  |  |  |  | gal/min |  | Federal Regulations.
gpmbase2 | gpm_base | gpm_base | gpm_base | 2nd baseline flow rate | [7 empty] | 1.2 |  |  | 1.8 |  | gal/min |  | Hawaii State Standards, effective January 1, 2021.
gpmEE | gpm_low | gpm_low | gpm_low | Efficient flow rate | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | 1 |  |  | 1.5 |  | gal/min |  | Products offered on Hawai'i Energy's online marketplace.
MPD | MPD | MPD | MPD | Usage time | usage time in minutes per day | usage time in minutes per day | usage time in minutes per day | usage time in minutes per day | usage time in minutes per day | usage time in minutes per day | usage time in minutes per day | 1.6 |  |  | 4.5 |  | min/day /person |  | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013.
PH |  |  |  | People per household, multi-family | people per household, multi family | people per household, multi family | people per household, multi family | people per household, multi family | people per household, multi family | people per household, multi family | people per household, multi family | 2.34 |  |  |  |  | people/ house |  | 2019 Hawaii Statewide Baseline Energy Use Study.2
|  |  |  | People per household, single-family | people per household, single family | people per household, single family | people per household, single family | people per household, single family | people per household, single family | people per household, single family | people per household, single family | 3.16
FH |  |  |  | Fixtures per household, multi-family | fixtures per household, multi family | fixtures per household, multi family | fixtures per household, multi family | fixtures per household, multi family | fixtures per household, multi family | fixtures per household, multi family | fixtures per household, multi family | 2.42 |  |  | 1.05 |  | fixtures/ house |  | 2019 Hawaii Statewide Baseline Energy Use Study.3
|  |  |  | Fixtures per household, single-family | fixtures per household, single family | fixtures per household, single family | fixtures per household, single family | fixtures per household, single family | fixtures per household, single family | fixtures per household, single family | fixtures per household, single family | 3.56 |  |  | 1.24
S | S | S | S | Conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | 8.3 |  |  |  |  | Btu/gal/ ˚F |  | Engineering constant.
Tmix | T_mix | T_mix | T_mix | Temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | 86 |  |  | 93 |  | ˚F |  | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013.
Tinlet | T_inlet | T_inlet | T_inlet | Average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | 75 |  |  |  |  | ˚F |  | Hawai‘i Energy Solar Water Heating Program Handbook, Table 2, for Hawaii and Honolulu counties. (Maui county average temperature is 71 °F).
EF |  |  |  | Energy Factor, storage electric resistance (SERWH) | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | 0.945 |  |  |  |  | - |  | Default Energy Factor for storage electric resistance WH baseline in Solar WH measure (R_WH_SWH).
|  |  |  | Energy Factor, tankless electric resistance (TERWH) | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | recovery efficiency electric resistance | 0.975 |  |  |  |  | - |  | Typical EFs for tankless electric resistance WHs range from 0.96 to 0.99 per DOE.
|  |  |  | Energy Factor, heat pump water heater (HPWH) | recovery efficiency heat pump water heater | recovery efficiency heat pump water heater | recovery efficiency heat pump water heater | recovery efficiency heat pump water heater | recovery efficiency heat pump water heater | recovery efficiency heat pump water heater | recovery efficiency heat pump water heater | 2.6 |  |  |  |  | - |  | Average of Uniform Energy Factor for baseline case and EE case from Heat Pump WH measure (R_WH_Heat Pump). Assumes 56 gal storage tank.
|  |  |  | Equivalent Energy Factor, solar water heater (SWH) | recovery efficiency solar water heater | recovery efficiency solar water heater | recovery efficiency solar water heater | recovery efficiency solar water heater | recovery efficiency solar water heater | recovery efficiency solar water heater | recovery efficiency solar water heater | 6.5 |  |  |  |  | - |  | An equivalent EF derived from Solar WH energy use since EF doesn't directly apply (R_WH_SWH).
Constant | Conversion | Conversion | Conversion | Conversion factor | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | 365 |  |  |  |  | Days/yr
Constant | Conversion | Conversion | Conversion | Conversion factor | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | 3412 |  |  |  |  | Btu/kWh |  | Engineering constant.
ISR |  |  |  | Lifetime in-service rate, direct-install | [7 empty] | 0.93 |  |  | 0.94 |  | - |  | AEG's Winter 2020 Benchmarking.1
|  |  |  | Lifetime in-service rate, online marketplace | [7 empty] | 1 |  |  |  |  | - |  | Assumes customers who purchase products online have a need for the product and will install them and keep them installed.
RUL | Measure Life | Measure Life | Measure Life | Remaining useful life of measure | [7 empty] | 3 |  |  |  |  | yrs |  | Assumed to be 1/3 of the EUL, rounded to nearest year.
EUL | Measure Life | Measure Life | Measure Life | Effective useful life of measure | [7 empty] | 10 |  |  |  |  | yrs |  | AEG 2018 Analysis.4
1 AEG's 2020 Analysis File titled "AEG HPUC Water Saving Measures - Analysis file," see sheet named "Benchmarking Analysis."
2 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. (Responses to Question 71 of the Residential Phone / Audit Survey.)
3 Derived by AEG from raw survey responses to Questions 15, 22, and 29 for bathroom faucets and Question 13b for kitchen faucets, Residential Phone / Audit Survey, AEG's 2019 Hawaii Statewide Baseline Energy Use Study.
4 AEG's 2018 Analysis File titled "AEG HPUC EUL Analysis."
Table 1: Residential Water Heating Type Distribution, Online Marketplace
Water Heater Type | [9 empty] | Total |  |  |  | Single Family |  |  | Multi- Family
Storage Electric Resistance | [9 empty] | 43.7% |  |  |  | 32.11% |  |  | 63.75%
Tankless Electric Resistance | [9 empty] | 4.219% |  |  |  | 3.608% |  |  | 4.296%
Heat Pump | [9 empty] | 6.25% |  |  |  | 7.143% |  |  | 5.155%
Solar | [9 empty] | 27.08% |  |  |  | 36.73% |  |  | 9.278%
Gas/Propane | [9 empty] | 10.42% |  |  |  | 14.29% |  |  | 3.093%
Other | [9 empty] | 8.333% |  |  |  | 6.122% |  |  | 14.43%
Source: 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Data from Figure 3-13 of the report and from responses to Question 47b of the Residential Phone / Audit Survey.
Table 2: Residential Home Type Distribution, Online Marketplace
Multi-Family | [9 empty] | 38%
Single Family | [9 empty] | 62%
Source: Total Housing Units, State of Hawaii, TableID:DP04, 2018: ACS 5-year Estimates Data Profiles, American Community Survey, U.S. Census Bureau, <https://www.census.gov/acs/www/data/data-tables-and-tools/data-profiles/>, accessed 12/31/2019.
SAVINGS
Direct Install Program - Dual Baseline
Table 3: Detailed Savings by Category
Type | [11 empty] | First Baseline | [5 empty] | Second Baseline |  |  | Lifetime
[12 empty] | ΔkW1 |  |  |  | ΔkWh1 |  | ΔkW2 |  | ΔkWh2 | ΔkWhdual
SERWH |  |  | Multi-family |  |  |  |  | Bathroom |  |  |  | 0.004 |  |  |  | 17.84 |  | 0.001 |  | 2.97 | 74.31
[8 empty] | Kitchen |  |  |  | 0.022 |  |  |  | 111.6 |  | 0.01 |  | 47.83 | 669.61
|  |  | Single-family |  |  |  |  | Bathroom |  |  |  | 0.003 |  |  |  | 16.38 |  | 0.001 |  | 2.73 | 68.25
[8 empty] | Kitchen |  |  |  | 0.026 |  |  |  | 127.62 |  | 0.011 |  | 54.69 | 765.69
TERWH |  |  | Multi-family |  |  |  |  | Bathroom |  |  |  | 0.003 |  |  |  | 17.3 |  | 0.001 |  | 2.88 | 72.06
[8 empty] | Kitchen |  |  |  | 0.022 |  |  |  | 108.17 |  | 0.009 |  | 46.36 | 649.03
|  |  | Single-family |  |  |  |  | Bathroom |  |  |  | 0.003 |  |  |  | 15.88 |  | 0.001 |  | 2.65 | 66.19
[8 empty] | Kitchen |  |  |  | 0.025 |  |  |  | 123.69 |  | 0.011 |  | 53.01 | 742.14
HPWH |  |  | Multi-family |  |  |  |  | Bathroom |  |  |  | 0.001 |  |  |  | 6.49 |  | 0 |  | 1.08 | 27.03
[8 empty] | Kitchen |  |  |  | 0.008 |  |  |  | 40.56 |  | 0.003 |  | 17.38 | 243.34
|  |  | Single-family |  |  |  |  | Bathroom |  |  |  | 0.001 |  |  |  | 5.95 |  | 0 |  | 0.99 | 24.78
[8 empty] | Kitchen |  |  |  | 0.009 |  |  |  | 46.38 |  | 0.004 |  | 19.88 | 278.3
SWH |  |  | Multi-family |  |  |  |  | Bathroom |  |  |  | 0.001 |  |  |  | 2.59 |  | 0 |  | 0.43 | 10.78
[8 empty] | Kitchen |  |  |  | 0.003 |  |  |  | 16.23 |  | 0.001 |  | 6.95 | 97.34
|  |  | Single-family |  |  |  |  | Bathroom |  |  |  | 0 |  |  |  | 2.38 |  | 0 |  | 0.4 | 9.94
[8 empty] | Kitchen |  |  |  | 0.004 |  |  |  | 18.55 |  | 0.002 |  | 7.95 | 111.3
Online Marketplace, July 1 - December 31, 2020
Table 4: Online Marketplace Blended Savings, July 1 - December 31, 2020
Type |  |  |  |  | First Year Savings | [7 empty] | Lifetime Savings
[5 empty] | ΔkW1 |  |  |  | ΔkWh1 |  |  |  | ΔkWhsingle1
Bathroom |  |  |  |  | 0.002 |  |  |  | 9.14 |  |  |  | 91.4
Kitchen |  |  |  |  | 0.013 |  |  |  | 65.62 |  |  |  | 656.2
Online Marketplace, January 1, 2021 and later
Table 5: Online Marketplace Blended Savings, January 1, 2021 and later
Type |  |  |  |  | First Year Savings | [7 empty] | Lifetime Savings
[5 empty] | ΔkW2 |  |  |  | ΔkWh2 |  |  |  | ΔkWhsingle2
Bathroom |  |  |  |  | 0 |  |  |  | 1.52 |  |  |  | 15.2
Kitchen |  |  |  |  | 0.006 |  |  |  | 28.12 |  |  |  | 281.2
Assumes that the high efficiency case remains at 1.0 gpm for bathroom faucet aerators and 1.5 gpm for kitchen faucet aerators after January 1, 2021.
RESOURCES
• | 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | AEG's Analysis Files titled "AEG HPUC Water Saving Measures - Analysis file," "AEG HPUC Baseline Study Data - Analysis File," and "AEG HPUC EUL Analysis."
• | Analysis of raw data from responses to select questions from 2019 Baseline Study, Residential Phone / Audit (P/A) Survey, Analysis by Kirk Voegtlin, December 30. 2019.
• | Appliance Standards Awareness Project, accessed Jan. 11, 2020, <https://appliance-standards.org/state-legislation/hawaii-2019-5-products>.
• | Arkansas TRM Version 7.0 Vol. 2, <http://www.apscservices.info/EEInfo/TRMv7.0.pdf>.
• | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013.
• | Electronic Code of Federal Regulations, Title 10: Energy, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates, (o) Faucets and (p) Showerheads.
• | ENERGY STAR Residential Water Heaters: Final Criteria Analysis, Department of Energy, April 1, 2008. Lists typical range of EFs for tankless electric resistance water heaters. <https://www.energystar.gov/ia/partners/prod_development/new_specs/downloads/water_heaters/waterheateranalysis_final.pdf>.
• | Hawaii House Bill 556 (Prior Session Legislation), A Bill for an Act, Relating to Energy Efficiency, Passed 7/1/2019, Act 141 6/26/2019, access text here: <https://legiscan.com/HI/text/HB556/id/2003415/Hawaii-2019-HB556-Amended.html>.
• | Illume: Overview of Energy Savings "Kit" Programs: Background, Challenges, and Opportunities, White Paper, ILLUME Advising LLC, Jan. 15, 2015. <https://illumeadvising.com/files/2016/08/KitsWhitePaper_Final.pdf>.
• | Massachusetts 2019-2021 Plan TRM, Effective from 12/31/2018 to 12/30/2021, electronic TRM, accessed on Jan 3, 2020, <https://etrm.anbetrack.com/#/workarea/trm/MADPU/RES-WH-FA/2019-2021%20Plan%20TRM/version/1?measureName=Hot%20Water%20-%20Faucet%20Aerator>.
• | Navigant, ComEd-Nicor Gas EPY4/GPY1 Multifamily Home Energy Savings Program Evaluation Report FINAL 2013-06-05.
• | Regional Technical Forum, Bathroom and Kitchen Faucet Aerators, workbook, Aerators v1.1, Aug. 22, 2018, worksheet named "In Service Rates," available here <https://nwcouncil.app.box.com/v/Aeratorsv1-1>.
• | Residential End Uses of Water Study, Version 2, Water Research Foundation, April 2016. The study investigated a sample of 23,749 single family homes across the US and Canada, with water use logged in 762 of those homes.
• | Texas TRM, v6.0, Vol 2 Residential Measures, Nov. 7, 2018.
• | Total Housing Units, State of Hawaii, TableID:DP04, 2018: ACS 5-year Estimates Data Profiles, American Community Survey, U.S. Census Bureau, <https://www.census.gov/acs/www/data/data-tables-and-tools/data-profiles/>, accessed 12/31/2019.
〖∆𝑘𝑊ℎ〗_𝑑𝑢𝑎𝑙=〖∆𝑘𝑊ℎ〗_1∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2∗(𝐸𝑈𝐿−𝑅𝑈𝐿)
〖∆𝑘𝑊ℎ〗_𝑠𝑖𝑛𝑔𝑙𝑒1=〖∆𝑘𝑊ℎ〗_1∗𝐸𝑈𝐿
〖∆𝑘𝑊ℎ〗_𝑠𝑖𝑛𝑔𝑙𝑒2=〖∆𝑘𝑊ℎ〗_2∗𝐸𝑈𝐿
〖∆𝑘𝑊ℎ〗_1=((〖𝑔𝑝𝑚〗_𝑏𝑎𝑠𝑒1−〖𝑔𝑝𝑚〗_𝐸𝐸 )∗𝑀𝑃𝐷∗𝑃𝐻/𝐹𝐻∗𝑆∗(𝑇_𝑚𝑖𝑥−𝑇_𝑖𝑛𝑙𝑒𝑡 )∗365∗𝐼𝑆𝑅)/((𝐸𝐹∗3412) )
〖∆𝑘𝑊〗_1=〖∆𝑘𝑊ℎ〗_1∗〖𝑅𝑎𝑡𝑖𝑜〗_(𝐴𝑛𝑛𝑢𝑎𝑙 𝑘𝑊ℎ)^(𝑃𝑒𝑎𝑘 𝑘𝑊)
〖∆𝑘𝑊〗_2=〖∆𝑘𝑊ℎ〗_2∗〖𝑅𝑎𝑡𝑖𝑜〗_(𝐴𝑛𝑛𝑢𝑎𝑙 𝑘𝑊ℎ)^(𝑃𝑒𝑎𝑘 𝑘𝑊)
〖∆𝑘𝑊ℎ〗_2=((〖𝑔𝑝𝑚〗_𝑏𝑎𝑠𝑒2−〖𝑔𝑝𝑚〗_𝐸𝐸 )∗𝑀𝑃𝐷∗𝑃𝐻/𝐹𝐻∗𝑆∗(𝑇_𝑚𝑖𝑥−𝑇_𝑖𝑛𝑙𝑒𝑡 )∗365∗𝐼𝑆𝑅)/((𝐸𝐹∗3412) )

## R_WH_LFShowerhead
RESIDENTIAL: Low-Flow Showerhead
Return to TOC
UPDATE STATUS
Updated in Winter 2019-2020 for PY20 TRM.
MEASURE DETAILS
Description
Efficient Low-Flow Showerheads (fixed or handheld).
Program Criteria
Qualified showerheads are provided directly by Hawai‘i Energy via online store or direct-install program.
Unit of Measure
One showerhead.
Baseline Equipment
For the direct-install program, the savings approach assumes early retirement (ER). A dual baseline approach is used since Hawaii adopted new state standards for showerheads, which will be effective as of 1/1/2021. The first baseline will be 2.5 gpm per current Federal regulations in effect since 1994. The second BL will be 1.8 gpm per Hawaii's new state standards.
For the online marketplace, the savings approach assumes replace-on-burnout (ROB). A single baseline approach is used. For July 1 - December 31, 2020, the online marketplace baseline will be 2.5 gpm per current Federal regulations in effect since 1994. After January 1, 2021, the baseline will be 1.8 gpm per Hawaii's new state standards.
High Efficiency Equipment
1.5 gpm showerhead.
ALGORITHMS
First Baseline Peak Demand Reduction, kW
(1)
Second Baseline Peak Demand Reduction, kW
(2)
First Baseline Annual Energy Savings, kWh/yr
(3)
Second Baseline Annual Energy Savings, kWh/yr
(4)
Lifetime Energy Savings, kWh
Dual baseline (Direct-Install):
(5)
Single baseline (Online Marketplace, July 1 - December 31, 2020):
(6)
Single baseline (Online Marketplace, January 1, 2021 and later):
(7)
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit | Source/Notes
Peak kW / Annual kWh |  |  |  | Ratio of Peak kW to Annual kWh | [11 empty] | 0.0002 | 0.0278 | 0.0278 | 0.0278 | 1/hr | AEG's approach to calculate this parameter for Hawaii is similar to the Texas TRM v6.0 and Arkansas TRM v7.0 approaches, except modified to reflect Hawaii's peak demand period of 5-9 PM non-holiday weekdays. The approach for Hawaii also uses daily water use profiles from the Water Research Foundation's 2016 Residential End Use of Water study.1
gpmbase1 | gpm_base | gpm_base | gpm_base | 1st baseline flow rate | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | 2.5 | 2.5 | 2.5 | 2.5 | gal/min | Federal Regulations.
gpmbase2 | gpm_base | gpm_base | gpm_base | 2nd baseline flow rate | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | flow rate of the baseline unit | 1.8 | 2.5 | 2.5 | 2.5 | gal/min | Hawaii State Standards, effective January 1, 2021.
gpmEE | gpm_low | gpm_low | gpm_low | Efficient flow rate | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | flow rate of the enhanced unit | 1.5 | 1.5 | 1.5 | 1.5 | gal/min | Products offered on Hawai'i Energy's online marketplace.
MPS | MS | MS | MS | Minutes per shower | minutes per shower | minutes per shower | minutes per shower | minutes per shower | minutes per shower | minutes per shower | minutes per shower | minutes per shower | minutes per shower | minutes per shower | minutes per shower | 7.8 | 7.8 | 7.8 | 7.8 | min/ shower | Residential End Uses of Water Study, Version 2, Executive Report, Water Research Foundation, April 2016, page 9. | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013
SPD | SPD | SPD | SPD | Average showers per day, per person | showers per day | showers per day | showers per day | showers per day | showers per day | showers per day | showers per day | showers per day | showers per day | showers per day | showers per day | 0.69 | 0.6 | 0.6 | 0.6 | shower/ day/ person | Gauley, B. and J. Koeller, Shower-Based Water Savings, Flow Rate vs. Duration vs. Volume, an Independent Maximum Performance (MaP) Research Report, January 2017.
PH |  |  |  | People per household, multi-family | people per household | people per household | people per household | people per household | people per household | people per household | people per household | people per household | people per household | people per household | people per household | 2.34 | 2.6 | 2.6 | 2.6 | people/ house | 2019 Hawaii Statewide Baseline Energy Use Study.2
|  |  |  | People per household, single-family | people per household | people per household | people per household | people per household | people per household | people per household | people per household | people per household | people per household | people per household | people per household | 3.16 | 3.24 | 3.24 | 3.24
FH |  |  |  | Shower fixtures per household, multi-family | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | 1.6 | 1.66 | 1.66 | 1.66 | fixtures/ house | 2019 Hawaii Statewide Baseline Energy Use Study.3
|  |  |  | Shower fixtures per household, single-family | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | shower fixtures per household | 2.2 | 2.13 | 2.13 | 2.13
S | S | S | S | Conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | conversion factor | 8.3 | 8.3 | 8.3 | 8.3 | Btu/gal/ ˚F | Engineering constant. | Engineering constant in units of Btu/(gal˚F) | Engineering constant in units of Btu/(gal˚F) | Engineering constant in units of Btu/(gal˚F) | Engineering constant in units of Btu/(gal˚F) | Engineering constant in units of Btu/(gal˚F) | Engineering constant in units of Btu/(gal˚F) | Engineering constant in units of Btu/(gal˚F) | Engineering constant in units of Btu/(gal˚F)
T_mix | T_mix | T_mix | T_mix | Temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | temperature at end use | 101 | 101 | 101 | 101 | ˚F | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013. | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013 | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013
T_inlet | T_inlet | T_inlet | T_inlet | Average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | average ground water temperature | 75 | 75 | 75 | 75 | ˚F | Hawai‘i Energy Solar Water Heating Program Handbook, Table 2, for Hawaii and Honolulu counties. (Maui county average temperature is 71 °F). | Honolulu Board of Water Supply. | Honolulu Board of Water Supply. | Honolulu Board of Water Supply. | Honolulu Board of Water Supply. | Honolulu Board of Water Supply. | Honolulu Board of Water Supply. | Honolulu Board of Water Supply. | Honolulu Board of Water Supply.
EF |  |  |  | Energy Factor, storage electric resistance (SERWH) | recovery efficiency | recovery efficiency | recovery efficiency | recovery efficiency | recovery efficiency | recovery efficiency | recovery efficiency | recovery efficiency | recovery efficiency | recovery efficiency | recovery efficiency | 0.945 | 0.98 | 0.98 | 0.98 | - | Default Energy Factor for storage electric resistance WH baseline in Solar WH measure (R_WH_SWH). | Electric Resistance ER from AHRI1 | Electric Resistance ER from AHRI1 | Electric Resistance ER from AHRI1 | Electric Resistance ER from AHRI1 | Electric Resistance ER from AHRI1 | Electric Resistance ER from AHRI1 | Electric Resistance ER from AHRI1 | Electric Resistance ER from AHRI1
|  |  |  | Energy Factor, tankless electric resistance (TERWH) | [11 empty] | 0.975 |  |  |  | - | Typical EFs for tankless electric resistance WHs range from 0.96 to 0.99 per DOE.
|  |  |  | Energy Factor, heat pump water heater (HPWH) | [11 empty] | 2.6 |  |  |  | - | Average of Uniform Energy Factor for baseline case and EE case from Heat Pump WH measure (R_WH_Heat Pump). Assumes 56 gal storage tank.
|  |  |  | Equivalent Energy Factor, solar water heater (SWH) | [11 empty] | 6.5 | 1.8 | 1.8 | 1.8 | - | An equivalent EF derived from Solar WH energy use since EF doesn't directly apply (R_WH_SWH).
Constant | Conversion | Conversion | Conversion | Conversion factor | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | 365 | 3412 | 3412 | 3412 | Days/yr
Constant | Conversion | Conversion | Conversion | Conversion factor | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | engineering units | 3412 | 3412 | 3412 | 3412 | Btu/kWh | Engineering constant.
ISR |  |  |  | Lifetime in-service rate, direct-install | [11 empty] | 0.93 |  |  |  | - | AEG's Winter 2020 Benchmarking.1
|  |  |  | Lifetime in-service rate, online marketplace | [11 empty] | 1 |  |  |  | - | Assumes customers who purchase products online have a need for the product and will install them and keep them installed.
RUL |  |  |  | Remaining useful life of measure | [11 empty] | 3 |  |  |  | yrs | Assumed to be 1/3 of the EUL, rounded to nearest year.
EUL | Measure Life | Measure Life | Measure Life | Effective useful life of measure | [11 empty] | 10 | 5 | 5 | 5 | yrs | DEER 2020.
1 AEG's 2020 Analysis File titled "AEG HPUC Water Saving Measures - Analysis file," see sheet named "Benchmarking Analysis."
2 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. (Responses to Question 71 of the Residential Phone / Audit Survey.)
3 2019 Hawaii Statewide Baseline Energy Use Study, Report, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020, Table 3-1.
Table 1: Residential Water Heating Type Distribution, Online Marketplace
Water Heater Type | [9 empty] | Total |  |  |  | Single Family |  |  |  | Multi- Family
Storage Electric Resistance | [9 empty] | 43.7% |  |  |  | 32.11% |  |  |  | 63.75%
Tankless Electric Resistance | [9 empty] | 4.219% |  |  |  | 3.608% |  |  |  | 4.296%
Heat Pump | [9 empty] | 6.25% |  |  |  | 7.143% |  |  |  | 5.155%
Solar | [9 empty] | 27.08% |  |  |  | 36.73% |  |  |  | 9.278%
Gas/Propane | [9 empty] | 10.42% |  |  |  | 14.29% |  |  |  | 3.093%
Other | [9 empty] | 8.333% |  |  |  | 6.122% |  |  |  | 14.43%
Source: 2019 Hawaii Statewide Baseline Energy Use Study, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020. Data from Figure 3-13 of the report and from responses to Question 47b of the Residential Phone / Audit Survey.
Table 2: Residential Home Type Distribution, Online Marketplace
Multi-Family | [9 empty] | 38%
Single Family | [9 empty] | 62%
Source: Total Housing Units, State of Hawaii, TableID:DP04, 2018: ACS 5-year Estimates Data Profiles, American Community Survey, U.S. Census Bureau, <https://www.census.gov/acs/www/data/data-tables-and-tools/data-profiles/>, accessed 12/31/2019.
SAVINGS
Direct Install Program
Table 3: Detailed Savings by Category
Type | [11 empty] | First Baseline | [7 empty] | Second Baseline | [5 empty] | Lifetime
[12 empty] | ΔkW1 |  |  |  | ΔkWh1 |  |  |  | ΔkW2 |  | ΔkWh2 |  |  |  | ΔkWhdual
SERWH | [5 empty] | Multi-family | [5 empty] | 0.036 |  |  |  | 178.82 |  |  |  | 0.011 |  | 53.65 |  |  |  | 912.01
[6 empty] | Single-family | [5 empty] | 0.035 |  |  |  | 175.63 |  |  |  | 0.011 |  | 52.69 |  |  |  | 895.72
TERWH | [5 empty] | Multi-family | [5 empty] | 0.035 |  |  |  | 173.32 |  |  |  | 0.01 |  | 52 |  |  |  | 883.96
[6 empty] | Single-family | [5 empty] | 0.034 |  |  |  | 170.22 |  |  |  | 0.01 |  | 51.07 |  |  |  | 868.15
HPWH | [5 empty] | Multi-family | [5 empty] | 0.013 |  |  |  | 65 |  |  |  | 0.004 |  | 19.5 |  |  |  | 331.5
[6 empty] | Single-family | [5 empty] | 0.013 |  |  |  | 63.83 |  |  |  | 0.004 |  | 19.15 |  |  |  | 325.54
SWH | [5 empty] | Multi-family | [5 empty] | 0.005 |  |  |  | 26 |  |  |  | 0.002 |  | 7.8 |  |  |  | 132.6
[6 empty] | Single-family | [5 empty] | 0.005 |  |  |  | 25.53 |  |  |  | 0.002 |  | 7.66 |  |  |  | 130.21
Online Marketplace, July 1 - December 31, 2020
Table 4: Online Marketplace Blended Savings, July 1 - December 31, 2020
Type | [5 empty] | First Year Savings | [7 empty] | Lifetime Savings
[6 empty] | ΔkW1 |  |  |  | ΔkWh1 |  |  |  | ΔkWhsingle1
LF Showerhead | [5 empty] | 0.019 |  |  |  | 95.487 |  |  |  | 954.87
Online Marketplace, January 1, 2021 and Later
Table 5: Online Marketplace Blended Savings, January 1, 2021 and Later
Type | [5 empty] | First Year Savings | [7 empty] | Lifetime Savings
[6 empty] | ΔkW2 |  |  |  | ΔkWh2 |  |  |  | ΔkWhsingle2
LF Showerhead | [5 empty] | 0.006 |  |  |  | 28.647 |  |  |  | 286.47
Assumes that the high efficiency case remains at 1.5 gpm per showerhead.
RESOURCES
• | 2019 Hawaii Statewide Baseline Energy Use Study, Report, Prepared for Hawaii Public Utilities Commission, Prepared by Applied Energy Group, 2020.
• | AEG's Analysis Files titled "AEG HPUC Water Saving Measures - Analysis file," "AEG HPUC Baseline Study Data - Analysis File," and "AEG HPUC EUL Analysis."
• | Analysis of raw data from responses to select questions from 2019 Baseline Study, Residential Phone / Audit (P/A) Survey, Analysis by Kirk Voegtlin, December 30. 2019.
• | Appliance Standards Awareness Project, accessed Jan. 11, 2020, <https://appliance-standards.org/state-legislation/hawaii-2019-5-products>.
• | Arkansas TRM Version 7.0 Vol. 2, <http://www.apscservices.info/EEInfo/TRMv7.0.pdf>.
• | Cadmus and Opinion Dynamics. Showerhead and Faucet Aerator Meter Study. Memorandum prepared for Michigan Evaluation Working Group. 2013.
• | Electronic Code of Federal Regulations, Title 10: Energy, PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER PRODUCTS, Subpart C—Energy and Water Conservation Standards, §430.32 Energy and water conservation standards and their compliance dates, (o) Faucets and (p) Showerheads.
• | ENERGY STAR Residential Water Heaters: Final Criteria Analysis, Department of Energy, April 1, 2008. Lists typical range of EFs for tankless electric resistance water heaters. <https://www.energystar.gov/ia/partners/prod_development/new_specs/downloads/water_heaters/waterheateranalysis_final.pdf>.
• | Gauley, B. and J. Koeller, Shower-Based Water Savings, Flow Rate vs. Duration vs. Volume, an Independent Maximum Performance (MaP) Research Report, January 2017, <https://www.map-testing.com/assets/reports/Shower-Based%20Water%20Savings%20Report%20Final%20revised%20March%2010,%202017.pdf>.
• | Hawaii House Bill 556 (Prior Session Legislation), A Bill for an Act, Relating to Energy Efficiency, Passed 7/1/2019, Act 141 6/26/2019, access text here: <https://legiscan.com/HI/text/HB556/id/2003415/Hawaii-2019-HB556-Amended.html>.
• | Illume: Overview of Energy Savings "Kit" Programs: Background, Challenges, and Opportunities, White Paper, ILLUME Advising LLC, Jan. 15, 2015. <https://illumeadvising.com/files/2016/08/KitsWhitePaper_Final.pdf>.
• | Massachusetts 2019-2021 Plan TRM, Effective from 12/31/2018 to 12/30/2021, electronic TRM, accessed on Jan 3, 2020, <https://etrm.anbetrack.com/#/workarea/trm/MADPU/RES-WH-FA/2019-2021%20Plan%20TRM/version/1?measureName=Hot%20Water%20-%20Faucet%20Aerator>.
• | Navigant, ComEd-Nicor Gas EPY4/GPY1 Multifamily Home Energy Savings Program Evaluation Report FINAL 2013-06-05.
• | Regional Technical Forum, Commercial and Residential Showerheads, workbook, Showerheads v4.3, Oct. 23, 2019, worksheet named "Adjustments_Installation Rates," available here <https://rtf.nwcouncil.org/measure/showerheads>.
• | Residential End Uses of Water Study, Version 2, Water Research Foundation, April 2016. The study investigated a sample of 23,749 single family homes across the US and Canada, with water use logged in 762 of those homes.
• | Texas TRM, v6.0, Vol 2 Residential Measures, Nov. 7, 2018.
• | Total Housing Units, State of Hawaii, TableID:DP04, 2018: ACS 5-year Estimates Data Profiles, American Community Survey, U.S. Census Bureau, <https://www.census.gov/acs/www/data/data-tables-and-tools/data-profiles/>, accessed 12/31/2019.
〖∆𝑘𝑊ℎ〗_𝑑𝑢𝑎𝑙=〖∆𝑘𝑊ℎ〗_1∗𝑅𝑈𝐿+〖∆𝑘𝑊ℎ〗_2∗(𝐸𝑈𝐿−𝑅𝑈𝐿)
〖∆𝑘𝑊ℎ〗_𝑠𝑖𝑛𝑔𝑙𝑒1=〖∆𝑘𝑊ℎ〗_1∗𝐸𝑈𝐿
〖∆𝑘𝑊ℎ〗_𝑠𝑖𝑛𝑔𝑙𝑒2=〖∆𝑘𝑊ℎ〗_2∗𝐸𝑈𝐿
〖∆𝑘𝑊ℎ〗_1=((〖𝑔𝑝𝑚〗_𝑏𝑎𝑠𝑒1−〖𝑔𝑝𝑚〗_𝐸𝐸 )∗𝑀𝑃𝑆∗𝑆𝑃𝐷∗𝑃𝐻/𝐹𝐻∗𝑆∗(𝑇_𝑚𝑖𝑥−𝑇_𝑖𝑛𝑙𝑒𝑡 )∗365∗𝐼𝑆𝑅)/((𝐸𝐹∗3412) )
〖∆𝑘𝑊〗_1=〖∆𝑘𝑊ℎ〗_1∗〖𝑅𝑎𝑡𝑖𝑜〗_(𝐴𝑛𝑛𝑢𝑎𝑙 𝑘𝑊ℎ)^(𝑃𝑒𝑎𝑘 𝑘𝑊)
〖∆𝑘𝑊〗_2=〖∆𝑘𝑊ℎ〗_2∗〖𝑅𝑎𝑡𝑖𝑜〗_(𝐴𝑛𝑛𝑢𝑎𝑙 𝑘𝑊ℎ)^(𝑃𝑒𝑎𝑘 𝑘𝑊)
〖∆𝑘𝑊ℎ〗_2=((〖𝑔𝑝𝑚〗_𝑏𝑎𝑠𝑒2−〖𝑔𝑝𝑚〗_𝐸𝐸 )∗𝑀𝑃𝑆∗𝑆𝑃𝐷∗𝑃𝐻/𝐹𝐻∗𝑆∗(𝑇_𝑚𝑖𝑥−𝑇_𝑖𝑛𝑙𝑒𝑡 )∗365∗𝐼𝑆𝑅)/((𝐸𝐹∗3412) )

## MASTER (hidden)
COMMERCIAL/RESIDENTIAL: Measure Name
MEASURE DETAILS
Description
Program Criteria
Unit of Measure
Baseline Equipment
High Efficiency Equipment
ALGORITHMS
DEFINITIONS & ASSUMPTIONS
Variable |  | Description |  | Value | Unit | Notes
SAVINGS
Measure Name |  |  | Peak Demand Savings | Annual Energy Savings

## Revision Log (internal) (hidden)
Date | Location | Action | Detail
2017-09-08 | R_Light_LED | ADD | Added EISA baseline analysis and citations
2017-09-14 | C_Appliance_Refrigerator R_Appliance_Refrigerator | CORRECT | Demand using 70% duty cycle rather than 100%
2017-09-14 | General | CHECK ADD | For all the following, double-checked calculations and added calculations where none were present: ◦ C_Kitchen_Freezer ◦ C_Kitchen_Refrigerator ◦ C_Spray_Nozzle -- calculations added to show how final numbers were derived ◦ C_IceMaker (calcs added) ◦ C_ElectricSteamCooker ◦ C_Electric Griddle (calcs added) ◦ C_Fryer (calcs added) ◦ C_Holding Cabinet ◦ C_Convection Oven ◦ C_Combination Oven
2017-09-14 | C_Kitchen_Combination Oven C_Kitchen_Convection Oven | CHECK | CF… should be 1.0 like other commercial kitchen?
2017-09-14 | C_Kitchen_DCV | CORRECT | C_Kitchen_DCV final savings value changed from kWh/year to kWh/hp/year
2017-09-21 | Definitions | ADD | Added definitions page
2017-09-21 | Reference | ADD | Added Reference tables page
2017-09-21 | R_WH_LFShowerhead | ADD | Added Showerheads from v1.3. changed MFDI pf from 0.51 to 0.96
2017-09-21 | R_WH_Faucet Aerator | ADD | Added FaucetAerators from v1.3. changed MFDI pf from 0.59 to 0.96
2017-09-21 | General | REMOVE | Remove all incentive dollar values because these do not belong in TRM, they are subject to change at Program discretion.
2017-09-21 | C_Light_Refrigerated Case | ADD | Added interactive factors to calculation
2017-09-21 | General | ADD | Augmented definitions
2017-10-13 | R_HVAC_Window¦VRF | MODIFY | Split R_HVAC_Window¦VRF into 2 distinct tabs
2017-11-15 | R_PlugProcess_Adv Power Strip | REMOVE | Remove R_smart strip "average/unknown". If not explicitely Tier 2, then it is Tier 1.
2018-03-15 |  | CORRECT | General rounding corrections (2 decimal places for kWh, 3 for kW)
2018-03-15 | R_Appliance_Clothes Washer | ADD | Filled in formulas for Clothes Washers, Tier 1,2,3
2018-03-18 | R_HVAC_Smart Thermostat | ADD | Added tab for R_Smart Thermostat
2018-05-10 | Introduction | ADD | Added Introduction tab
2018-05-10 | Key Metrics | ADD | Added Key Metrics tab
2018-05-10 | Savings Factors | ADD | Added Savings Factors tab
2018-05-10 | Definitions | CORRECT | Renamed 'Definitions' tab to 'Glossary' tab
2018-05-10 | Reference | MODIFY REMOVE | Redistributed reference tables to Savings Factors and EFLH tabs, then removed Reference tab.
2018-05-18 | Custom | ADD | Added Custom section tab
2018-05-21 | R_FaucetAerator | REMOVE | Remove old R_faucetaerator tab with proposed methodology
2018-05-21 | R_FaucetAerator | ADD | Add new R_faucetaerator tab with new OD approved methodology
2018-05-21 | R_Showerhead | REMOVE | Remove old R_showerhead tab with proposed methodology
2018-05-21 | R_Showerhead | ADD | Add new R_showerhead tab with new OD approved methodology
2018-05-23 | Master EUL | ADD | Added Master EUL tab. Cut EUL table from Key Metrics tab.
2018-05-23 | Master EUL | MODIFY | Made individual entry tab measures lives link to the Master EUL tab
2018-05-23 | C_Transformers | REMOVE | C_Transformers tab as this measure is now custom
2018-05-23 | R_CFL | REMOVE | Removed R_CFL tab
2018-05-23 | Master EUL | MODIFY | Master EUL table. There was some inconsistency between individual entries and Table entries.
2018-06-01 | C_Light_All | ADD | Added new measures: 3' Linear LED, 8' Linear LED, 4' T5/T5HO Linear LED
2018-06-01 | C_Light_All | CORRECT | Updated Linear LED wattages
2018-06-01 | C_Light_All | CORRECT | Updated Corn Cob wattage ranges and values
2018-06-01 | C_Light_All | MODIFY | Calculations link to EFLH and Savings Factor tab, instead of in-tab table
2018-06-01 | Key Metrics | CORRECT | Updated TRB table
2018-06-03 | C_HVAC_Chiller_WKST | ADD | Added Chiller worksheet
2018-06-03 | C_HVAC_AC_WKST | ADD | Added AC worksheet
2018-06-03 | C_Light_Dimmable(Nonlinear LED) | MODIFY REMOVE | Linked to EFLH tab and Savings Factors tab (interactive factors), then removed excess EFLH tables that are not in use.
2018-06-04 | Key Metrics | CORRECT | Updated Net-to-gross table values and reference for residential LED value change from 0.79 to 0.5
2018-06-04 | General | MODIFY | General format standardizations.
2018-06-19 | C_PumpMotor_PE Motor | ADD | Added Premium Efficiency Motor entry from PY15 TRM.
2018-06-21 | C_PumpMotor_PE Motor | CORRECT | Changed efficiency values to reflect updated standards.
2018-06-22 | R_HVAC_VRF Split | CORRECT | Changed enhanced SEER from 16 to 18.

## OLD_Delete_Transformer (hidden)
COMMERCIAL: Transformer
HAWAII ENERGY NOMENCLATURE
| Group | [7 empty] | Type
| Not found in MSL | [7 empty] | Transformer
| Subtype | [7 empty] | Size | [7 empty] | Incentive
MEASURE DETAILS
Description
Program Criteria
Transformers must be listed in CEE Qualified Products List (QPL) to be considered for incentive. QPL Source: http://library.cee1.org/content/transformersqplfebruary2015/
Unit of Measure
One transformer
Baseline Equipment
NEMA TP-1 (current federal minimum standard level)
High Efficiency Equipment
CEE Tier I (single phase) CEE Tier II (single or three phase)
ALGORITHMS
peak kW savings per W | = (E_base,loss - E_he,loss) / (HRS * kVA)
annual kWh savings per W | = (E_base,loss - E_he,loss) / kVA
peak kW savings | = CF * (P_base,loss - P_he,loss)
annual kWh savings | = HRS * (P_base,loss - P_he,loss)
Measure description
DEFINITIONS & ASSUMPTIONS |  |  | INPUT VALUES | Notes
P_base,loss | Power loss of baseline transformer |  | Table 1
P_he,loss | Power loss of energy efficient transformer |  | Table 1
E_base,loss | Annual energy loss of baseline transformer |  | Table 1
E_he,loss | Annual energy loss of high efficiency transformer |  | Table 1
CF | coincidence factor |  | 1
HRS | annual operating hours |  | 8760
Measure Life | expected duration of energy savings |  | 15 | years
Qualified Products List (QPL) | Transformers must be listed in CEE QPL list to be considered for incentive
QPL Source: | http://library.cee1.org/content/transformersqplfebruary2015/
Source: | http://library.cee1.org/sites/default/files/library/7905/Specification_Low_Voltage_Dry_Type_2012.pdf
Total losses and energy savings associated with CEE Tier 1 level for single-phase transformers
| KVA | Total Losses (kWh/yr) |  | Energy Savings vs. Baseline (kWh/yr) | Demand Savings vs. Baseline (kW)
|  | Baseline | Tier 1 | Tier 1 | Tier 1
| 15 | 1058 | 740 | 318 | 0.036187
| 25 | 1533 | 1073 | 460 | 0.052511
| 37.5 | 2070 | 1449 | 621 | 0.07089
| 50 | 2606 | 1824 | 782 | 0.089269
| 75 | 3449 | 2414 | 1035 | 0.11815
| 100 | 4292 | 3005 | 1287 | 0.14703
| 150 | 6056.1791 | 4239.3284 | 1816.8507 | 0.20743 | (interpolated)
| 167 | 6656 | 4659 | 1997 | 0.22797
| 250 | 9198 | 6439 | 2759 | 0.31495
| 333 | 11231 | 7862 | 3369 | 0.38459
Total losses and energy savings associated with CEE Tiers for three-phase equipment
| KVA |  | Total Losses (kWh/yr) |  | Energy Savings vs. Baseline (kWh/yr) |  | Demand Savings vs. Baseline (kW) |  | Marginal Equipment Cost: Tier 1 vs. Baseline
|  | Baseline | Tier 1 | Tier 2 | Tier 1 | Tier 2 | Tier 1 | Tier 2
| 15 | 1380 | 966 | 736 | 414 | 644 | 0.04726 | 0.073516 | 448
| 25 | 1993.3333 | 1395.3333 | 1073.3333 | 598 | 920 | 0.068265 | 0.10502 | 687.3333
| 30 | 2300 | 1610 | 1242 | 690 | 1058 | 0.078767 | 0.12078 | 807
| 45 | 3173 | 2221 | 1683 | 952 | 1490 | 0.10868 | 0.17009 | 851
| 75 | 4599 | 3219 | 2460 | 1380 | 2139 | 0.15753 | 0.24418 | 1115
| 112.5 | 6209 | 4346 | 3346 | 1863 | 2863 | 0.21267 | 0.32683 | 2144
| 150 | 7818 | 5473 | 4139 | 2345 | 3679 | 0.26769 | 0.41998 | 2740
| 225 | 10348 | 7243 | 4139 | 3105 | 6209 | 0.35434 | 0.70879 | 3617
| 300 | 12877 | 9014 | 5151 | 3863 | 7726 | 0.44098 | 0.88196 | 5078
| 450 | 18166 | 12716 | 6921.75 | 5450 | 11244.25 | 0.62215 | 1.2836 | 4880.75
| 500 | 19929 | 13950 | 7512 | 5979 | 12417 | 0.68253 | 1.4175 | 4815
| 750 | 27594 | 19316 | 10118 | 8278 | 17476 | 0.94498 | 1.995
| 1000 | 33726 | 23608 | 12571 | 10118 | 21155 | 1.155 | 2.415
OUTPUTS
CEE High Performance Tiers
| KVA | Energy Savings vs. Baseline (kWh/yr) |  | Inventives (total) $
|  | Tier 1 | Tier 2 | Tier 1 | Tier 2
Single-phase
| 15 | 318 |  | 79.5
| 25 | 460 |  | 115
| 37.5 | 621 |  | 155.25
| 50 | 782 |  | 195
| 75 | 1035 |  | 260
| 100 | 1287 |  | 320
| 150 | 1816.8507 |  | 455
| 167 | 1997 |  | 500
| 250 | 2759 |  | 689.75
| 333 | 3369 |  | 840
Three-phase
| 15 | 414 | 644 | 105 | 160
| 25 | 598 | 920 | 150 | 230
| 30 | 690 | 1058 | 175 | 265
| 45 | 952 | 1490 | 240 | 375
| 75 | 1380 | 2139 | 345 | 535
| 112.5 | 1863 | 2863 | 465 | 715
| 150 | 2345 | 3679 | 585 | 920
| 225 | 3105 | 6209 | 775 | 1550
| 300 | 3863 | 7726 | 965 | 1930
| 450 | 5450 | 11244.25 | 1365 | 2810
| 500 | 5979 | 12417 | 1495 | 3100
| 750 | 8278 | 17476 | 2070 | 4370
| 1000 | 10118 | 21155 | 2530 | 5290
WORKSHEET
High Efficiency Transformer Worksheet Effective July 1, 2016; subject to availability of funds. Hawaii Energy is a ratepayer-funded conservation and efficiency program administered by Leidos Engineering under contract with the Hawaii Public Utilities Commission serving the islands of Hawaii, Lanai, Maui, Molokai, and Oahu.
Measure Costs and Incentive Levels
· If a transformer size is not listed in table, we will apply the lower one
· > 1000 KVA (3-Phase) will be based on Custom Incentive Program
· > 333 KVA (Single Phase) will be based on Custom Incentive Program
· Marginal (incremental) cost – see TRM Tables for 3-Phase.
· Incentive level is based on the following table.
| Utility Account Holder Name: | [5 empty] | Project / Building Name:
Transformer Calculator
| Please Enter |  |  | Equipment Requirement Tier Check (1=Tier 1, 2 = Tier 2 , 0=Not Qualify) | KVA | Tiers Efficiency (%) |  | Energy Savings vs. Baseline (kWh/yr) |  | Demand Savings vs. Baseline (kW) |  | Inventives (total) $ |  | Results
| KVA | Quantity | Efficiency (%) |  |  | Tier 1 | Tier 2 | Tier 1 | Tier 2 | Tier 1 | Tier 2 | Tier 1 | Tier 2 | KVA | Energy Savings (kWh) | Demand Savings (kW) | Incentives
Example
| 15 | 5 | 99.07 | 1 | 15 | 98.39 |  | 318 |  | 0.036187 |  | 80 |  | 75 | 1590 | 0.18094 | 400
Single-Phase
| 15 | 0 |  | 0 | 15 | 98.39 |  | 318 |  | 0.036187 |  | 80 |  | 0 | 0 | 0 | 0
| 25 | 0 |  | 0 | 25 | 98.6 |  | 460 |  | 0.052511 |  | 115 |  | 0 | 0 | 0 | 0
| 37.5 | 0 |  | 0 | 37.5 | 98.74 |  | 621 |  | 0.07089 |  | 155 |  | 0 | 0 | 0 | 0
| 50 | 0 |  | 0 | 50 | 98.81 |  | 782 |  | 0.089269 |  | 195 |  | 0 | 0 | 0 | 0
| 75 | 0 |  | 0 | 75 | 98.95 | N/A | 1035 | N/A | 0.11815 | N/A | 260 | N/A | 0 | 0 | 0 | 0
| 100 | 0 |  | 0 | 100 | 99.02 |  | 1287 |  | 0.14703 |  | 320 |  | 0 | 0 | 0 | 0
| 150 | 0 |  | 0 | 150 | 99.0722 |  | 1816.8507 |  | 0.20743 |  | 455 |  | 0 | 0 | 0 | 0
| 167 | 0 |  | 0 | 167 | 99.09 |  | 1997 |  | 0.22797 |  | 500 |  | 0 | 0 | 0 | 0
| 250 | 0 |  | 0 | 250 | 99.16 |  | 2759 |  | 0.31495 |  | 690 |  | 0 | 0 | 0 | 0
| 333 | 0 |  | 0 | 333 | 99.23 |  | 3369 |  | 0.38459 |  | 840 |  | 0 | 0 | 0 | 0
Three-Phase
| 15 | 0 |  | 0 | 15 | 97.9 | 98.4 | 414 | 644 | 0.04726 | 0.073516 | 105 | 160 | 0 | 0 | 0 | 0
| 25 | 0 |  | 0 | 25 | 98.1333 | 98.5667 | 598 | 920 | 0.068265 | 0.10502 | 150 | 230 | 0 | 0 | 0 | 0
| 30 | 0 |  | 0 | 30 | 98.25 | 98.65 | 690 | 1058 | 0.078767 | 0.12078 | 175 | 265 | 0 | 0 | 0 | 0
| 45 | 0 |  | 0 | 45 | 98.39 | 98.78 | 952 | 1490 | 0.10868 | 0.17009 | 240 | 375 | 0 | 0 | 0 | 0
| 75 | 0 |  | 0 | 75 | 98.6 | 98.93 | 1380 | 2139 | 0.15753 | 0.24418 | 345 | 535 | 0 | 0 | 0 | 0
| 112.5 | 0 |  | 0 | 112.5 | 98.74 | 99.03 | 1863 | 2863 | 0.21267 | 0.32683 | 465 | 715 | 0 | 0 | 0 | 0
| 150 | 0 |  | 0 | 150 | 98.81 | 99.1 | 2345 | 3679 | 0.26769 | 0.41998 | 585 | 920 | 0 | 0 | 0 | 0
| 225 | 0 |  | 0 | 225 | 98.95 | 99.4 | 3105 | 6209 | 0.35434 | 0.70879 | 775 | 1550 | 0 | 0 | 0 | 0
| 300 | 0 |  | 0 | 300 | 99.02 | 99.44 | 3863 | 7726 | 0.44098 | 0.88196 | 965 | 1930 | 0 | 0 | 0 | 0
| 450 | 0 |  | 0 | 450 | 99.0725 | 99.4925 | 5450 | 11244.25 | 0.62215 | 1.2836 | 1365 | 2810 | 0 | 0 | 0 | 0
| 500 | 0 |  | 0 | 500 | 99.09 | 99.51 | 5979 | 12417 | 0.68253 | 1.4175 | 1495 | 3100 | 0 | 0 | 0 | 0
| 750 | 0 |  | 0 | 750 | 99.16 | 99.56 | 8278 | 17476 | 0.94498 | 1.995 | 2070 | 4370 | 0 | 0 | 0 | 0
| 1000 | 0 |  | 0 | 1000 | 99.23 | 99.59 | 10118 | 21155 | 1.155 | 2.415 | 2530 | 5290 | 0 | 0 | 0 | 0
[14 empty] | KVA | kWh | kW | Total Incentives
[13 empty] | Total | 0 | 0 | 0 | 0
PY2016HT

## OLD_CFL (hidden)
RESIDENTIAL: CFL
HAWAII ENERGY NOMENCLATURE
| Equipment Group | [7 empty] | Lighting | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC
| Equipment Type | [7 empty] | Compact Fluorescent Light | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan | Fan
Equipment Subtype
Nomenclature
MEASURE DETAILS
Description
Replacing incandescent lamp with standard screw-in, ENERGY STAR CFL.
Program Criteria
Unit of Measure
One lamp
Baseline Equipment
High Efficiency Equipment
ALGORITHMS
peak kW savings/lamp | [7 empty] | = (kW.base - kW.CFL) * CF * PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF | =kW_b*CF*PF-kW_cfl*CF*PF
annual kWh savings/lamp | [7 empty] | = (kW.base - kW.CFL) * HRS * PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF | =kW_b*HOURS*PF-kW_cfl*HOURS*PF
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  |  | Unit |  |  | Notes
kW.base | kW_b | kW_b | kW_b | Baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | baseline wattage of average residential bulb | See Table 1 | see Table 1 | see Table 1 | see Table 1 | kW
kW.CFL | kW_cfl | kW_cfl | kW_cfl | Wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | wattage of average CFL bulb | See Table 2 | see Table 2 | see Table 2 | see Table 2 | kW
CF | CF | CF | CF | Coincidence factor | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | coincidence factor, percent of time savings correspond with utility peak 5pm -9 pm | 0.12 | 0.12 | 0.12 | 0.12 | -
PF | PF | PF | PF | Persistence factor | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | persistence factor, % of measures installed and operating | 0.96 | 0.96 | 0.96 | 0.96 | - |  |  | Informed by 2012 EM&V report | informed by 2012 EM&V report? | informed by 2012 EM&V report? | informed by 2012 EM&V report? | informed by 2012 EM&V report? | informed by 2012 EM&V report? | informed by 2012 EM&V report? | informed by 2012 EM&V report? | informed by 2012 EM&V report?
HOURS | HOURS | HOURS | HOURS | Hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | hours of lamp operation per year | See Table 1 | See Table 1 | See Table 1 | See Table 1 | hrs
Measure Life | Measure Life | Measure Life | Measure Life | Expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 6 | 20 years | 20 years | 20 years | yrs
Table 1. Baseline Lamp Characteristics1
Lamp Types |  |  |  |  | Retired Base (W) |  |  | Demand Base '07 EISA (kW.bs) |  |  | Demand Base post-2020 (kW.b20) |  |  | Hours per Day, non-military |  |  | Hours per Day, military |  |  | HE Pentration % |  |  |  | Total kWh2, non-military |  |  |  | Total kWh, military
Incandescent |  |  |  |  | 100-150 |  |  | 0.072 |  |  | 0.023 |  |  | 2.3 |  |  | 3.45 |  |  | 2.4% |  |  |  | 1.4507 |  |  |  | 2.176
Incandescent |  |  |  |  | 75 |  |  | 0.053 |  |  | 0.018 |  |  | 2.3 |  |  | 3.45 |  |  | 26.5% |  |  |  | 11.7908 |  |  |  | 17.6862
Incandescent |  |  |  |  | 60 |  |  | 0.043 |  |  | 0.015 |  |  | 2.3 |  |  | 3.45 |  |  | 24.7% |  |  |  | 8.9163 |  |  |  | 13.3745
Incandescent |  |  |  |  | 40 |  |  | 0.029 |  |  | 0.009 |  |  | 2.3 |  |  | 3.45 |  |  | 28.2% |  |  |  | 6.8654 |  |  |  | 10.2981
CFL | [7 empty] | 0.026 | [5 empty] | 2.3 |  |  | 3.45 |  |  | 0.5% |  |  |  | 0.10913 |  |  |  | 0.1637
CFL | [7 empty] | 0.023 | [5 empty] | 2.3 |  |  | 3.45 |  |  | 5.9% |  |  |  | 1.1392 |  |  |  | 1.7088
CFL | [7 empty] | 0.014 | [5 empty] | 2.3 |  |  | 3.45 |  |  | 5.5% |  |  |  | 0.64641 |  |  |  | 0.96962
CFL | [7 empty] | 0.013 | [5 empty] | 2.3 |  |  | 3.45 |  |  | 6.3% |  |  |  | 0.68755 |  |  |  | 1.0313
Total Average Baseline Energy (kWh) | [23 empty] | 31.6055 |  |  |  | 47.4082
Total Average Demand (kW) | [23 empty] | 0.037648
Source: |  | Hawaii Energy Efficiency Program Technical Reference Manual, PY 2015. Measure Savings Calculations, p.28
Note: |  | 1. CFL and incandescent penetration rates assume 81.8% incandescent replacement rate, and 18.2% CFL replacement rate, annually, which reflects 1 CFL burnout per every 4.5 incandescent burnout in 9000 hours of operation. 2. Baseline kW assumptions reflect federal minimum standards for general use and specialty bulbs imposed by the Energy Independence and Security Act (EISA) for 2007 and 2020, as summarized in the 2016 Pennsylvania Technical Reference Manual (puc.pa.gov).
Table 2. Efficient Lamp Characteristics
Demand Baseline (kW.CFL) |  |  | Hours per Day, non-military |  |  | Hours per Day, military |  |  | HE Penetration % |  |  |  | Total kWh2, non-military |  |  |  | Total kWh, military
0.026 |  |  | 2.3 |  |  | 3.45 |  |  | 2% |  |  |  | 0.43654 |  |  |  | 0.65481
0.023 |  |  | 2.3 |  |  | 3.45 |  |  | 33% |  |  |  | 6.3718 |  |  |  | 9.5577
0.014 |  |  | 2.3 |  |  | 3.45 |  |  | 24% |  |  |  | 2.8207 |  |  |  | 4.2311
0.013 |  |  | 2.3 |  |  | 3.45 |  |  | 42% |  |  |  | 4.5837 |  |  |  | 6.8755
Total Average Energy (kWh) | [12 empty] | 14.2127 |  |  |  | 21.3191
Total Average Demand (kW) | [12 empty] | 0.016762
SAVINGS
Peak kW savings/lamp | [12 empty] | 0.002
Annual kWh savings/lamp, military | [12 empty] | 16.7
Annual kWh savings/lamp, non-military | [12 empty] | 25.05
RECOMMENDATIONS

## OLD_Other_Direct Install Kit (hidden)
RESIDENTIAL: Direct Install Kit
HAWAII ENERGY NOMENCLATURE
Equipment Group
Equipment Type
Equipment Subtype
Nomenclature
MEASURE DETAILS
Description
The Hawaii Energy/Honeywell team went in to multifamily residential buildings and offered free installation of energy efficiency devices, including light bulbs, low flow showerheads and faucet aeartors, and an advanced power strip. The savings claim for each household depends on the type of water heating for each home, as well as the occupancy for each home (this data was collected by the team).
Program Criteria
Unit of Measure
Baseline Equipment
100 W incandescent (replaced with 23 W CFL) 75 W incandescent (replaced with 20 W CFL) 60 W incandescent (replaced with 13 W CFL) Showerhead = 2.5 gpm Faucet = 2.2 gpm
High Efficiency Equipment
23 W CFL to replace the 100 W incandescent 20 W CFL to replace the 75 W incandescent 13 W CFL to replace the 60 W incandescent Advanced power strip (7 plugs) for home entertainment system or home office Low-flow showerheads = 1.5 gpm (40% reduction) Low-flow faucet aerators = 1.5 gpm (32% reduction)
ALGORITHMS
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description |  |  | CFL |  | P Strip | Aerator | Unit | Notes
PF |  |  | Persistance factor |  |  | 96% |  | 96% | 100% | -
CF |  |  | Coincidence factor |  |  | 12% |  | 100% | 20% | -
Measure Life |  |  | Expected duration of savings |  |  | 6 |  | 5 | 5 | yrs
SAVINGS
Measure Name |  |  |  |  | Peak Demand Savings |  | Annual Energy Savings
100 |  | --> | 23 | CFL1 | 0.009 |  | 62.06
75 |  | --> | 20 | CFL1 | 0.006 |  | 44.33
60 |  | --> | 13 | CFL1 | 0.005 |  | 37.88
1 For each bulb replaced, the reduced wattage was calculated. Run time was assumed to be 2.3 hours per day per bulb, 365 days per year.
Measure Name |  |  |  |  | Peak Demand Savings |  | Annual Energy Savings
Advanced Power Strip2 |  |  |  |  | 0.011 |  | 98.69
2 Given that this device was a 7-plug strip, the 7-plug strip value was used, rather than the TRM assumption of an average 6-plug unit.
For low-flow showerheads:
• Given standard electric resistance water heating: PY14 TRM value of 306 kWh for an average family size of 3.77 people. This value was normalized on a per person basis of 81.2 kWh. Then the value was multiplied by the actually occupancy of the household. These values were assumed to be the same regardless of individual electric resistance water heating in the residential unit or system level electric resistance water heating in the building. Also, these values were assumed to be the same regardless of individually metered electrical billing at the apartment or master-metered electrical billing at the building.
• Given heat pump water heating: Starting with the PY14 TRM value of 2460 kWh per year required for heating all water for an average family size of 3.77 people, this value was divided by an average COP of 2.26 for heat pump water heaters, for 1088 kWh per year. Then the value was added up given 6% tank and pipe losses, for 1157 kWh per year. Given the assumption that showers account for 28% of all hot water use, heat pump water heating consumption for an average family is 324 kWh per year. By reducing shower water consumption by 40% with the low-flow showerhead, heat pump water heading consumption is reduced to 195 kWh per year per family, for a savings of 130 kWh per year per family. Per person energy savings is 34.5 kWh per person per year. Finally, the value was multiplied by the actually occupancy of the household. Savings is assumed to be the same regardless of individual heat pump, central heat pump, individually metered billing, or master-metered billing.
• Given on-demand electric water heating: Starting with the PY14 TRM value of 2460 kWh per year required for heating all water for an average family size of 3.77 people, this value was divided by an average efficiency of 0.98 for on-demand/instantaneous water heaters, for 2510 kWh per year. Then the value was added up given 2% tank and pipe losses, for 2561 kWh per year. Given the assumption that showers account for 28% of all hot water use, heat pump water heating consumption for an average family is 717 kWh per year. By reducing shower water consumption by 40% with the low-flow showerhead, on-demand water heading consumption is reduced to 430 kWh per year per family, for a savings of 287 kWh per year per family. Per person energy savings is 76.1 kWh per person per year. Finally, the value was multiplied by the actually occupancy of the household. Savings is assumed to be the same regardless of individually metered billing or master-metered billing. There are no central on-demand water heating systems, only individual systems.
• Given boiler water heating: Savings were assumed to be the same for boiler water heating as for standard electric resistance water heating because gas-fired boilers were not in the scope of this measure. An electric-fired boiler is essentially the same as a standard electric resistance water heater. Savings are assumed to be the same regardless of individually metered billing or master-metered billing. There are no individual boiler water heaters in apartments, only central boilers.
Measure Name |  |  |  |  | Peak Demand Savings
LFSH w/ Electric Resistance3 |  |  |  |  | 0.1144
LFSH w/ Heat Pump |  |  |  |  | 0.1008
LFSH w/ On-demand4 |  |  |  |  | 0.1144
3 Taken from Hawai'i Energy PY14 TRM
4 Assumed the same as electric-resistance (conservative value)
For faucet aerators:
• Given standard electric-resistance water heating: PY14 TRM value for savings per year for an average family size of 3.77 people for faucet aerators is 65 kWh (assuming 90% efficiency). This value was normalized on a per person basis of 17.2 kWh. Then the value was multiplied by the actually occupancy of the household. These values were assumed to be the same regardless of individual electric resistance water heating in the residential unit or system level electric resistance water heating in the building. Also, these values were assumed to be the same regardless of individually metered electrical billing at the apartment or master-metered electrical billing at the building.
• Given heat pump water heating: Starting with the PY14 TRM value of 58.44 kWh savings per year for a family of 3.77 for faucet aerators (assuming 100% efficiency), this value was divided by an average COP of 2.26 for heat pump water heaters, for 25.9 kWh per year. Then the value was added up given 6% tank and pipe losses, for 27.6 kWh per year per family, or 7.3 kWh per year per person. Finally, the value was multiplied by the actually occupancy of the household. Savings is assumed to be the same regardless of individual heat pump, central heat pump, individually metered billing, or master-metered billing.
• Given on-demand electric water heating: Starting with the PY14 TRM value of 58.44 kWh savings per year for a family of 3.77 for faucet aerators (assuming 100% efficiency), this value was divided by an average efficiency of 98% for on-demand/instantaneous water heaters, for 59.6 kWh per year. Then the value was added up given 2% tank and pipe losses, for 60.8 kWh per year per family, or 16.1 kWh per year per person. Finally, the value was multiplied by the actually occupancy of the household. Savings is assumed to be the same regardless of individually metered billing, or master-metered billing. There is only individual on-demand water heating, no central systems.
• Given boiler water heating: Savings were assumed to be the same for boiler water heating as for standard electric resistance water heating because gas-fired boilers were not in the scope of this measure. An electric-fired boiler is essentially the same as a standard electric resistance water heater. Savings are assumed to be the same regardless of individually metered billing or master-metered billing. There are no individual boiler water heaters in apartments, only central boilers.
Measure Name |  |  |  |  | Peak Demand Savings
LFSH w/ Electric Resistance5 |  |  |  |  | 0.1144
LFSH w/ Heat Pump |  |  |  |  | 0.1008
LFSH w/ On-demand6 |  |  |  |  | 0.1144
5 Taken from Hawai'i Energy PY14 TRM
6 Assumed the same as electric-resistance (conservative value)

## OLD_HVAC_Chiller (2) (hidden)
COMMERCIAL: Chiller
HAWAII ENERGY NOMENCLATURE
| Group | [7 empty] | Type
| Not found in MSL | [7 empty] | Chiller
| Subtype | [7 empty] | Size
VERSION HISTORY
Draft Date
| Revision Date |  |  |  |  | 2017-09-21
| Review Date |  |  |  |  | 2011-10-05
MEASURE DETAILS
Description
The replacement of chillers with Energy Efficiency above the code efficiency values in place at the time of permitting the project. In multiple unit chiller plants, a review of operational chillers will be conducted to determine what fraction of installed chillers will be incentivized. This is to avoid paying for standby units.
Program Criteria
Unit of Measure
One ton of cooling capacity
Baseline Equipment
Hawaii Energy assumes Honolulu code IECC 2006
High Efficiency Equipment
Equipment whose efficiency is 15% higher than IECC 2006
ALGORITHMS
peak kW savings per ton | [5 empty] | =1 ton capacity*[η_bs-η_ee]*CF
annual kWh savings per ton | [5 empty] | =1 ton capacity*[IPLV_bs-IPLV_ee]*HOURS
DEFINITIONS & ASSUMPTIONS
Variable |  |  | Description | [5 empty] | Value |  | Unit | Notes
η_bs |  |  | Baseline rated full load efficiency, which depends on cooling capacity of proposed equipment. | [5 empty] | Table |  | kW/ton | Hawaii Energy assumes Honolulu code IECC 2006
η_ee |  |  | Proposed measure rated full load efficiency | [5 empty] | Table |  | kW/ton | Hawaii Energy applies a default 15% better than code qualifying efficiency (on kW/ton basis).
IPLV_bs |  |  | Baseline integrated part load value efficiency | [5 empty] | Table |  | kW/ton
IPLV_ee |  |  | Proposed measure integrated part load value efficiency | [5 empty] | Table |  | kW/ton | Hawaii Energy applies a default 15% better than code qualifying efficiency.
ton |  |  | Unit of equipment cooling capacity | [5 empty] | 12000 |  | Btu/hr
HRS |  |  | Annual operating hours | [5 empty] | Table |  | hrs
CF |  |  | Coincidence factor | [5 empty] | Table |  | -
Measure Life |  |  | Expected duration of energy savings | [5 empty] | 22 |  | yrs
Table 1: Chiller Program Efficiencies
Cooling Method |  | Type |  |  | Size |  |  | Published Full Load COP | Published IPLV |  | Full HE η_bs | Full HE η_ee |  | IPLV_bs 1 |  | IPLV_ee
Air |  | None |  |  | <150 tons |  |  | 2.8 | 2.8 |  | 1.2561 | 1.0677 |  | 1.2561 |  | 1.0677
|  | None |  |  | >=150 tons |  |  | 2.5 | 2.5 |  | 1.4068 | 1.1958 |  | 1.4068 |  | 1.1958
|  | No Condenser |  |  | Any |  |  | 3.1 | 3.1 |  | 1.1345 | 0.96434 |  | 1.1345 |  | 0.96434
Water |  | Reciprocating |  |  | Any |  |  | 4.2 | 4.65 |  | 0.83738 | 0.71177 |  | 0.75634 |  | 0.64289
|  | Rotary |  |  | <150 tons |  |  | 4.45 | 4.5 |  | 0.79034 | 0.67179 |  | 0.78156 |  | 0.66432
[5 empty] | 150-300 tons |  |  | 4.9 | 4.95 |  | 0.71775 | 0.61009 |  | 0.7105 |  | 0.60393
[5 empty] | >=300 tons |  |  | 5.5 | 5.6 |  | 0.63945 | 0.54354 |  | 0.62804 |  | 0.53383
|  | Centrifugal |  |  | <150 tons |  |  | 5 | 5 |  | 0.7034 | 0.59789 |  | 0.7034 |  | 0.59789
[5 empty] | 150-300 tons |  |  | 5.55 | 5.55 |  | 0.63369 | 0.53864 |  | 0.63369 |  | 0.53864
[5 empty] | >=300 tons |  |  | 6.1 | 6.1 |  | 0.57656 | 0.49007 |  | 0.57656 |  | 0.49007
Table 1 Source: 2006 International Energy Conservation Code, Table 503.2.3(7). kW/ton are derived from COP (unitless) using kW/ton=12/(COP*3.412)
Table 1 Footnotes: 1. water cooled kW/ton IPLV values are converted from unitless IPLV for 2017.
Table 1.V2. Chiller Baseline Minimum Efficiencies
Cooling Method |  | Technology |  | Type |  |  | Size (tons) |  |  | Published Units | Published Full Load Eff Path A | Published IPLV Path A |  | Published Full Load Eff Path B |  | Published IPLV Path B
Air | [6 empty] | <150 |  |  | BTU/W | 10.1 | 13.7 |  | 9.7 |  | 15.8
[7 empty] | >=150 |  |  | BTU/W | 10.1 | 13.7 |  | 9.7 |  | 16.1
|  | Absorbtion |  | Single Effect |  |  | All |  |  | COP | 0.6 | N/A |  | N/A |  | N/A
Water |  | Electric |  | Positive Displacement |  |  | <75 |  |  | kW/ton | 0.75 | 0.6 |  | 0.78 |  | 0.5
[7 empty] | >=75 to <150 |  |  | kW/ton | 0.72 | 0.56 |  | 0.75 |  | 0.49
[7 empty] | >=150 to <300 |  |  | kW/ton | 0.66 | 0.54 |  | 0.68 |  | 0.44
[7 empty] | >=300 to <600 |  |  | kW/ton | 0.61 | 0.52 |  | 0.625 |  | 0.41
[7 empty] | >=600 |  |  | kW/ton | 0.56 | 0.5 |  | 0.585 |  | 0.38
|  |  |  | Centrifugal |  |  | <150 |  |  | kW/ton | 0.61 | 0.55 |  | 0.695 |  | 0.44
[7 empty] | >=150 to <300 |  |  | kW/ton | 0.61 | 0.55 |  | 0.635 |  | 0.4
[7 empty] | >=300 to <400 |  |  | kW/ton | 0.56 | 0.52 |  | 0.595 |  | 0.39
[7 empty] | >=400 |  |  | kW/ton | 0.56 | 0.5 |  | 0.585 |  | 0.38
|  | Absorbtion |  | Single Effect |  |  | All |  |  | COP | 0.7 | N/A |  | N/A |  | N/A
|  | Absorbtion |  | Double Effect |  |  | Indirect/Direct-fired |  |  | COP | 1 | 1.05 |  | N/A |  | N/A
Table 1 Source: 2015 International Energy Conservation Code, Table C403.2.3(7). kW/ton are derived from COP (unitless) using kW/ton=12/(COP*3.412).Path A is intended for constant speed chillers operating at or near full load most of the time. Path B is intended for variable speed chillers operating at part load most of the time.
Table 2a: Derived1 Coincidence Factor by Building Type and Equipment Capacity, Water Cooled
Building Type |  |  | Reciprocating |  | Rotary Screw or Scroll | [5 empty] | Centrifugal
|  |  | All |  | <150 |  |  | 150-300 | >300 |  | <150 |  | 150-300 |  | >300
Misc. Commercial |  |  | 0.50953 |  | 0.52298 |  |  | 0.53872 | 0.54213 |  | 0.57814 |  | 0.57862 |  | 0.57814
Cold Storage |  |  | 0.57322 |  | 0.59047 |  |  | 0.60373 | 0.61511 |  | 0.65397 |  | 0.65226 |  | 0.65908
Education |  |  | 0.66875 |  | 0.69169 |  |  | 0.7059 | 0.70894 |  | 0.75822 |  | 0.75746 |  | 0.76315
Grocery |  |  | 0.44583 |  | 0.4555 |  |  | 0.46441 | 0.46915 |  | 0.50232 |  | 0.50498 |  | 0.50877
Health |  |  | 0.56525 |  | 0.58203 |  |  | 0.59445 | 0.60468 |  | 0.64449 |  | 0.64174 |  | 0.64752
Hotel/Motel |  |  | 0.43787 |  | 0.44707 |  |  | 0.45512 | 0.45872 |  | 0.49284 |  | 0.49446 |  | 0.4972
Industrial |  |  | 0.50953 |  | 0.52298 |  |  | 0.53872 | 0.54213 |  | 0.57814 |  | 0.57862 |  | 0.57814
Office |  |  | 0.38214 |  | 0.39646 |  |  | 0.39939 | 0.4066 |  | 0.43598 |  | 0.43133 |  | 0.43939
Restaurant |  |  | 0.44583 |  | 0.4555 |  |  | 0.46441 | 0.46915 |  | 0.50232 |  | 0.50498 |  | 0.50877
Retail |  |  | 0.54933 |  | 0.56516 |  |  | 0.57587 | 0.58383 |  | 0.62553 |  | 0.6207 |  | 0.6244
Warehouse |  |  | 0.50156 |  | 0.51455 |  |  | 0.52943 | 0.5317 |  | 0.56867 |  | 0.5681 |  | 0.57814
Table 2b: Derived1 Coincidence Factor by Building Type and Equipment Capacity, Air Cooled
Building Type |  |  | Chiller
|  |  | <150 tons |  | >= 150 tons
Misc. Commercial |  |  | 0.49891 |  | 0.50232
Cold Storage |  |  | 0.49891 |  | 0.50232
Education |  |  | 0.20169 |  | 0.19903
Grocery |  |  | 0.84921 |  | 0.84826
Health |  |  | 0.64752 |  | 0.64923
Hotel/Motel |  |  | 0.59975 |  | 0.60184
Industrial |  |  | 0.49891 |  | 0.50232
Office |  |  | 0.49891 |  | 0.50232
Restaurant |  |  | 0.74837 |  | 0.74874
Retail |  |  | 0.59975 |  | 0.60184
Warehouse |  |  | 0.45114 |  | 0.45019
Table 2 Source: Hawaii Energy Efficiency Program Technical Reference Manual, PY 2015, July 1 2015-June 30, 2016. Measure Savings Calculations, p.106-108. See Support tab.
Table 2 footnotes: 1. Hawaii Energy TRM has published unit savings tables by building type and cooling capacity range since 2011. These tables are likely derived from California DEER database simulated savings. For the purposes of documenting applicable savings calculations, the published tables and algorithm inputs above were used here to 'back calculate' apparent coincidence factors for each combination of building type and capacity range. E.g., CF=kW savings/ton/(COP_b-COP_ee)/1 ton
Table 3a: Derived Cooling Hours by Building Type and Equipment Capacity, Water Cooled
Building Type |  |  | Reciprocating |  | Rotary Screw or Scroll | [5 empty] | Centrifugal
|  |  | All |  | <150 |  |  | 150-300 | >300 |  | <150 |  | 150-300 |  | >300
Misc. Commercial |  |  | 2487.9167 |  | 2560.9335 |  |  | 2611.8481 | 2652.2613 |  | 2834.8033 |  | 2817.3453 |  | 2838.6892
Cold Storage |  |  | 4272.8476 |  | 4397.2813 |  |  | 4486.2113 | 4555.9678 |  | 4868.7344 |  | 4839.3533 |  | 4876.0702
Education |  |  | 2451.2945 |  | 2522.975 |  |  | 2573.7664 | 2613.6868 |  | 2793.1011 |  | 2776.316 |  | 2797.0628
Grocery |  |  | 4272.8476 |  | 4397.2813 |  |  | 4486.2113 | 4555.9678 |  | 4868.7344 |  | 4839.3533 |  | 4876.0702
Health |  |  | 3468.7529 |  | 3570.6296 |  |  | 3641.9119 | 3698.9871 |  | 3952.2333 |  | 3929.3445 |  | 3957.9769
Hotel/Motel |  |  | 2487.1205 |  | 2560.0899 |  |  | 2611.8481 | 2652.2613 |  | 2833.8556 |  | 2817.3453 |  | 2838.6892
Industrial |  |  | 3468.7529 |  | 3570.6296 |  |  | 3641.9119 | 3698.9871 |  | 3952.2333 |  | 3929.3445 |  | 3957.9769
Office |  |  | 4140.6895 |  | 4262.3178 |  |  | 4347.8168 | 4415.2228 |  | 4718.0378 |  | 4689.9646 |  | 4725.7527
Restaurant |  |  | 2778.5053 |  | 2859.5403 |  |  | 2917.4306 | 2962.9429 |  | 3166.5256 |  | 3147.6837 |  | 3170.5441
Retail |  |  | 2180.6092 |  | 2244.6126 |  |  | 2289.5468 | 2325.9414 |  | 2485.0733 |  | 2470.1743 |  | 2488.3337
Warehouse |  |  | 4272.8476 |  | 4397.2813 |  |  | 4486.2113 | 4555.9678 |  | 4868.7344 |  | 4839.3533 |  | 4876.0702
Table 3b: Derived Cooling Hours by Building Type and Equipment Capacity, Air Cooled
Building Type |  |  | Chiller
|  |  | <150 tons |  | >= 150 tons
Misc. Commercial |  |  | 2969.5773 |  | 2975.5483
Cold Storage |  |  | 5100.0301 |  | 5110.8917
Education |  |  | 2925.5246 |  | 2931.9506
Grocery |  |  | 5100.0301 |  | 5110.8917
Health |  |  | 4140.4241 |  | 4149.3711
Hotel/Motel |  |  | 2968.5158 |  | 2975.0744
Industrial |  |  | 4140.4241 |  | 4149.3711
Office |  |  | 4942.9265 |  | 4953.0867
Restaurant |  |  | 3316.6915 |  | 3323.8567
Retail |  |  | 2603.356 |  | 2608.7583
Warehouse |  |  | 5100.0301 |  | 5110.8917
Table 3 Source: 2016 Pennsylvania Technical Reference Manual cooling hours for Philadelphia, PA, adjusted for Hawaii climate using deemed cooling hours from https://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/Calc_CAC.xls. See Cooling Hr Proxy 2 tab
SAVINGS
Table 4.a. Air cooled chiller: Calculated Peak kW Savings/Ton by Building Type and Equipment Size (BTU/hr)
Building Type |  |  | Chiller
|  |  | <150 tons |  | >= 150 tons
Misc. Commercial |  |  | 0.094 |  | 0.106
Cold Storage |  |  | 0.094 |  | 0.106
Education |  |  | 0.038 |  | 0.042
Grocery |  |  | 0.16 |  | 0.179
Health |  |  | 0.122 |  | 0.137
Hotel/Motel |  |  | 0.113 |  | 0.127
Industrial |  |  | 0.094 |  | 0.106
Office |  |  | 0.094 |  | 0.106
Restaurant |  |  | 0.141 |  | 0.158
Retail |  |  | 0.113 |  | 0.127
Warehouse |  |  | 0.085 |  | 0.095
Table 4.b. Air cooled chiller: Calculated Annual kWh Savings/Ton by Building Type and Equipment Size (BTU/hr)
Building Type |  |  | Chiller |  | Chiller
|  |  | <150 tons |  | >= 150 tons
Misc. Commercial |  |  | 559.5 |  | 627.9
Cold Storage |  |  | 960.9 |  | 1078.5
Education |  |  | 551.2 |  | 618.7
Grocery |  |  | 960.9 |  | 1078.5
Health |  |  | 780.1 |  | 875.6
Hotel/Motel |  |  | 559.3 |  | 627.8
Industrial |  |  | 780.1 |  | 875.6
Office |  |  | 931.3 |  | 1045.2
Restaurant |  |  | 624.9 |  | 701.4
Retail |  |  | 490.5 |  | 550.5
Warehouse |  |  | 960.9 |  | 1078.5
Table 5.a. Water cooled chiller: Calculated Peak kW Savings/Ton by Building Type and Equipment Size (ton)
Building Type |  |  | Reciprocating |  | Rotary Screw or Scroll | [5 empty] | Centrifugal
|  |  | All |  | <150 |  |  | 150-300 | >300 |  | <150 |  | 150-300 |  | >300
Misc. Commercial |  |  | 0.064 |  | 0.062 |  |  | 0.058 | 0.052 |  | 0.061 |  | 0.055 |  | 0.05
Cold Storage |  |  | 0.072 |  | 0.07 |  |  | 0.065 | 0.059 |  | 0.069 |  | 0.062 |  | 0.057
Education |  |  | 0.084 |  | 0.082 |  |  | 0.076 | 0.068 |  | 0.08 |  | 0.072 |  | 0.066
Grocery |  |  | 0.056 |  | 0.054 |  |  | 0.05 | 0.045 |  | 0.053 |  | 0.048 |  | 0.044
Health |  |  | 0.071 |  | 0.069 |  |  | 0.064 | 0.058 |  | 0.068 |  | 0.061 |  | 0.056
Hotel/Motel |  |  | 0.055 |  | 0.053 |  |  | 0.049 | 0.044 |  | 0.052 |  | 0.047 |  | 0.043
Industrial |  |  | 0.064 |  | 0.062 |  |  | 0.058 | 0.052 |  | 0.061 |  | 0.055 |  | 0.05
Office |  |  | 0.048 |  | 0.047 |  |  | 0.043 | 0.039 |  | 0.046 |  | 0.041 |  | 0.038
Restaurant |  |  | 0.056 |  | 0.054 |  |  | 0.05 | 0.045 |  | 0.053 |  | 0.048 |  | 0.044
Retail |  |  | 0.069 |  | 0.067 |  |  | 0.062 | 0.056 |  | 0.066 |  | 0.059 |  | 0.054
Warehouse |  |  | 0.063 |  | 0.061 |  |  | 0.057 | 0.051 |  | 0.06 |  | 0.054 |  | 0.05
Table 5.b. Water cooled chiller: Calculated Annual kWh Savings/Ton by Building Type and Equipment Size (ton)
Building Type |  |  | Reciprocating |  | Rotary Screw or Scroll | [5 empty] | Centrifugal
|  |  | All |  | <150 |  |  | 150-300 | >300 |  | <150 |  | 150-300 |  | >300
Misc. Commercial |  |  | 282.26 |  | 300.23 |  |  | 278.36 | 249.86 |  | 299.1 |  | 267.8 |  | 245.5
Cold Storage |  |  | 484.76 |  | 500.92 |  |  | 455.38 | 402.53 |  | 450.83 |  | 406.15 |  | 369.53
Education |  |  | 278.1 |  | 287.37 |  |  | 261.25 | 230.93 |  | 258.64 |  | 233.01 |  | 212
Grocery |  |  | 484.76 |  | 500.92 |  |  | 455.38 | 402.53 |  | 450.83 |  | 406.15 |  | 369.53
Health |  |  | 393.54 |  | 406.65 |  |  | 369.68 | 326.78 |  | 365.99 |  | 329.72 |  | 299.99
Hotel/Motel |  |  | 282.17 |  | 291.57 |  |  | 265.07 | 234.3 |  | 262.42 |  | 236.41 |  | 215.1
Industrial |  |  | 393.54 |  | 406.65 |  |  | 369.68 | 326.78 |  | 365.99 |  | 329.72 |  | 299.99
Office |  |  | 469.77 |  | 485.43 |  |  | 441.3 | 390.08 |  | 436.88 |  | 393.59 |  | 358.1
Restaurant |  |  | 315.23 |  | 325.73 |  |  | 296.12 | 261.75 |  | 293.16 |  | 264.11 |  | 240.3
Retail |  |  | 247.39 |  | 255.64 |  |  | 232.4 | 205.43 |  | 230.08 |  | 207.28 |  | 188.59
Warehouse |  |  | 484.76 |  | 500.92 |  |  | 455.38 | 402.53 |  | 450.83 |  | 406.15 |  | 369.53
RECOMMENDATIONS
1. Eliminate CF variation by equipment size if the derived values can't be substantiated in literature or measured data. See Cooling Hr Proxy and consider adjusting an existing set of cooling hours deemed by building type, e.g. Pennsylvania Technical Reference Manual.
2. Check federal standards for commercial chilers at https://www.regulations.gov/#!documentDetail;D=EERE-2013-BT-STD-0007-0030.
3. Revisit conversions from IECC to kW/ton values for IPLV_b efficiency metrics.
4. Consider using full load efficiency to calculate kW savings and part load efficiency to calculate kWh savings as per Pennsylvania PUC Technical Reference Manual.
Note on D66: Aurilio, Kate C.: not currently part of our program

## OLD_C_WH_Heat Pump (hidden)
COMMERCIAL: Heat Pump Water Heater
HAWAII ENERGY NOMENCLATURE
| Group | [7 empty] | Type
| Not found in MSL | [7 empty] | Heat Pump Water Heater
| Subtype | [7 empty] | Size | [7 empty] | Incentive
MEASURE DETAILS
Description
The installation of a heat pump water heater in place of a standard electric water heater or existing less efficient heat pump water heater.
Program Criteria
Unit of Measure
One heat pump
Baseline Equipment
Standard electric water heater or heat pump water heater
High Efficiency Equipment
High efficiency heat pump water heater
ALGORITHMS
peak kW savings/ton | [7 empty] | = Base Power*CF_base - HPWH Power*CF_HP
annual kWh savings/ton | [7 empty] | = Base WH Energy Usage - HPWH Energy Usage
Base WH Energy Usage | [7 empty] | = Energy per Day per ton*Days/Yr/COP_base
HPWH Energy Usage | [7 empty] | = Energy per Day per ton*Days/Yr/COP_HP
DEFINITIONS & ASSUMPTIONS
Variable |  |  |  | Description | [11 empty] | Value |  |  | Unit |  | Notes
Energy per Day |  |  |  | 13.3 gallons/day/person*3.77 persons*8.34 lbs/gallon*(130 deg.F-75 deg.F)*1.0[BTU/deg. F/lb] | [11 empty] | 22981 |  |  | BTU |  | Assumed in Hawaii Energy PY7 TRM, p.123
Energy per Day per ton | Energy per Day per ton | Energy per Day per ton | Energy per Day per ton | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 12,000 BTU/ton/3412kWh/BTU | 3.517 | 3.517 | 3.517 | kW |  | Assumed in Hawaii Energy PY7 TRM, p.123
Days/Yr | Days/Yr | Days/Yr | Days/Yr | [12 empty] | 365 | 365 | 365 | days
COP_base | COP_base | COP_base | COP_base | [12 empty] | See table 1 | see table 1 | see table 1 | -
COP_HP | COP_HP | COP_HP | COP_HP | [12 empty] | See table 1 | see table 1 | see table 1 | -
CF_base | CF_base | CF_base | CF_base | [12 empty] | See table 1 | see table 1 | see table 1 | -
CF_HP | CF_HP | CF_HP | CF_HP | [12 empty] | See table 1 | see table 1 | see table 1 | -
Base Power (kW/ton) | Base Power (kW/ton) | Base Power (kW/ton) | Base Power (kW/ton) | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =Base WH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | See table 1 | see table 1 | see table 1 | kW |  | depends on baseline water heater
HPWH Power (kW/ton) | HPWH Power (kW/ton) | HPWH Power (kW/ton) | HPWH Power (kW/ton) | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | =HPWH Energy Usage/(10 hrs/day*365 days/yr)/3650 hours/yr | See table 1 | see table 1 | see table 1 | kW |  | PY7 TRM calculates assuming 30.4 days/mth*12 months/yr
Measure Life | Measure Life | Measure Life | Measure Life | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | expected duration of energy savings | 10 | 10 years | 10 years | yrs
Table 1. Water Heater Parameters
[8 empty] | COP_base |  |  |  | COP_HP |  |  |  | CF_base |  |  |  | CF_HP |  | Base Power | HPWH Power1
electric resistance W.H. | [7 empty] | 0.98 |  |  |  | N/A |  |  |  | 0.143 |  |  |  | N/A |  | 0.4 | N/A
heat pump W.H. | [7 empty] | ? |  |  |  | 3.5 |  |  |  | 0.08 |  |  |  | 0.08 |  | ? | 0.3
Source: |  | Hawaii Energy Efficiency Program Technical Reference Manual, PY 2015, July 1 2015-June 30, 2016. Measure Savings Calculations, p.123
Note: |  | 1. Heat pump power consumption value of 0.3 kW reported in the PY7 TRM appears to be derived based on 943 kWh/ton savings, rather than heat pump energy usage of 367 kWh/ton.
SAVINGS
[13 empty] | Peak kW/ton | [5 empty] | Annual kWh/ton
Heat Pump WH replacing Resistance WH | [12 empty] | 0.0332 | [5 empty] | 942.6131
RECOMMENDATIONS
1. consider different basis of savings--heat pump water heaters rarely rated in tons?
2. Define baseline heat pump water heater COP