## Program Rules & Worksheet Tips
Program Rules
1) | In order to ensure the best chances of qualifying for an incentive, Hawai‘i Energy requires that you contact our program for preliminary approval prior to the start of any work. Otherwise, the project is at significant risk of being disqualified. Projects are handled on a case-by-case basis and may require documentation before and after implementation (e.g. pre- and post-data, pre-inspection, etc.)
2) | Incentives may not exceed 50% of incremental project costs
3) | The Simple Payback calculated in our Overview tab must be greater than one year for custom non-lighting projects
4) | The Utility Benefit Test calculated in our Overview tab must be equal to or greater than one
5) | Incentives are based on projected energy and demand savings for both new construction and retrofit projects:
| 5.1) | On-Peak Demand savings: The amount of kW saved during 5pm to 9pm on weekdays
|  | - | Peak Demand Savings Incentive Rate | $ 125/kW
| 5.2) | First-Year Energy savings: The amount of kWh saved in the first year based on average annual operating hours
|  | - | Energy Savings Incentive Rate | $ 0.08/kWh (Project Measure Life ≤ 5 years)
$ 0.12/kWh (Project Measure Life > 5 years)
Program Rules for Power Move Demand Savings Bonus
1) | Project must be pre-approved by Hawai‘i Energy through a Rebate Commitment Letter to be eligible for the incentive rates below.
2) | Incentives may not exceed 50% of incremental project costs
3) | Project must be a retrofit. New construction is not eligible for this offer.
4) | The Simple Payback calculated in our Overview tab must be greater than one year for custom non-lighting projects
5) | The Utility Benefit Test calculated in our Overview tab must be equal to or greater than one
6) | Incentives are based on projected energy and demand savings for retrofit projects:
| 6.1) | On-Peak Demand savings: The amount of kW saved during 5pm to 9pm on weekdays
|  | - | Power Move Demand Savings Incentive Rate | $ 400/kW
| 6.2) | First-Year Energy savings: The amount of kWh saved in the first year based on average annual operating hours
|  | - | Energy Savings Incentive Rate | $ 0.08/kWh (Project Measure Life ≤ 5 years)
$ 0.12/kWh (Project Measure Life > 5 years)
See the Power Move webpage for complete Rules & Requirements and instructions on how to apply.
Worksheet Instructions
1) | Go to the "Input" tab and enter in all the customer, project, and facility information.
Enter in all the information for your project in the blue fields and the white cells will populate automatically.
2) | Once you have completed the above steps, go to the Program Requirements section (in Overview & Inputs tab) towards the bottom and make sure the Utility Benefit Test and the Simple Payback (without Hawai‘i Energy rebate) have a green Pass indicator.
3) | If the project passes the two metrics above, submit the worksheet to Hawai‘i Energy along with any other necessary documentation including the energy savings calculations, the Commercial Incentive Application, and IRS Form W-9 for the Applicant (Utility Account Holder).
If you have any questions, please call our Business Program (808) 839-8880 (O‘ahu) or toll free at (877) 231-8222
www.hawaiienergy.com
Transformer Incentive Worksheet
Effective July 1, 2023 to June 30, 2024. (WKS_C_Transformer_PY23_1ELS)
Hawai‘i Energy's mission is to empower island families and businesses to make smart energy choices that reduce energy consumption, save money and pursue a 100% clean energy future.

## Input
Account Name: | [8 empty] | Project Name:
|  | Facility Type: | [6 empty] | Facility Annual Hours:
|  | Special Offerings: | None
Notes:
· If age of transformer is not available nor attainable, another proxy may be acceptable; for example, the age of the building which it services, if reasonable.
· "Cooling Load Impact" columns account for the interactive effect of cooling indoor transformers. Please attach any relevant calculations if using this column.
· > 1000 KVA (3-Phase) will be based on Custom Incentive Program.
[6 empty] | Reference | Select whether to use user input baseline values or reference values (reference by default)
Size (kVA) | Qty | Location | Baseline Equipment Manufacture Year | Average Loading Percentage | Replacement Event | Baseline Transformer |  |  | Replacement Transformer |  | Cooling Load Impact |  |  |  | Demand Savings (kW) | Annual Energy Savings (kWh) | Incentives
[6 empty] | No Load Losses (Watts) User Input* | No Load Losses (Watts) Reference | Annual Losses (kWh) | No Load Losses (Watts) | Annual Losses (kWh) | Actively-cooled Transformer Room | Cooling System Performance (kW/ton) | Cooling Load Reduction (kW) | Annual Cooling Reduction (kWh)
[5 empty] | End of Life | [6 empty] | 0 | [5 empty] | Yes
[5 empty] | End of Life | [6 empty] | 0 | [5 empty] | No
[5 empty] | End of Life | [6 empty] | 0 | [5 empty] | User Input
[5 empty] | End of Life | [6 empty] | 0 | [5 empty] | Reference
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
[5 empty] | End of Life | [6 empty] | 0
Total: | [13 empty] | 0 | 0 | 0
*This is optional in the case more accurate baseline values are known
Formulas:
Replacement Event = IF(OR([Average Loading Percentage]>0.35, [Average Loading Percentage]=0), IF(YEAR(TODAY())-[Baseline Equipment Manufacture Year]<INDEX(EUL,1), INDEX(EventType,1), INDEX(EventType,2)), IF(YEAR(TODAY())-[Baseline Equipment Manufacture Year]<INDEX(EUL,2), INDEX(EventType,1), INDEX(EventType,2)))
Replacement Event = IF(OR([Average Loading Percentage]>0.35, [Average Loading Percentage]=0), IF(YEAR(TODAY())-[Baseline Equipment Manufacture Year]<=INDEX(EUL,1), INDEX(EventType,1), INDEX(EventType,2)), IF(YEAR(TODAY())-[Baseline Equipment Manufacture Year]<=INDEX(EUL,2), INDEX(EventType,1), INDEX(EventType,2)))

## Lookup (hidden)
Three-Phase |  | Pre-TP1 |  | TP-1 |  | DOE2016 |  | HVAC EFLH |  | Event Type | EUL
kVA | DOE 2016 | kVA | No-Load Losses (W) | kVA | No-Load Losses (W) | kVA | No-Load Losses (W) | Building Type | Hours | Retrofit | 30
15 | 97.89% | 10 | 233.6667 | 10 | - | 10 | 57.0733 | Misc. Commercial | 3050 | End of Life | 50
25 | 98.12% | 15 | 286 | 15 | 162 | 15 | 77.0442 | Cold Storage | 3050
30 | 98.23% | 20 | 461 | 20 | - | 20 | 95.3224 | Education | 2342 | Incentive / kWh | Incentive / kW
45 | 98.4% | 25 | 282 | 25 | - | 25 | 112.4367 | Grocery | 3050 | 0.12 | 125
75 | 98.6% | 30 | 443 | 30 | 233 | 30 | 128.6774 | Health | 4709
112.5 | 98.74% | 37.5 | 533 | 37.5 | - | 37.5 | 151.7804 | Hotel/Motel | 1952 | Special Offerings
150 | 98.83% | 45 | 623 | 45 | - | 45 | 173.704 | Industrial | 3520 | None
225 | 98.94% | 50 | 585 | 50 | - | 50 | 187.7891 | Office | 2603 | Power Move Demand Savings Bonus
300 | 99.02% | 63 | 765.8 | 63 | - | 63 | 222.8151 | Restaurant | 3050
450 | 99.11% | 75 | 861 | 75 | 406 | 75 | 253.5 | Retail | 3379
500 | 99.14% | 100 | 1089.6667 | 100 | - | 100 | 313.6409 | Warehouse | 3050
750 | 99.23% | 112.5 | 1204 | 112.5 | 400 | 112.5 | 342.2043
1000 | 99.28% | 125 | 1300.6667 | 125 | - | 125 | 369.9526
|  | 150 | 1494 | 150 | 425 | 150 | 423.3896
Single-Phase |  | 167 | 1570.3867 | 167 | - | 167 | 458.3981
kVA | DOE 2016 | 200 | 1718.6667 | 200 | - | 200 | 523.8354
15 | 97.7% | 225 | 1831 | 225 | 630 | 225 | 571.5414
25 | 98% | 250 | 2030.3333 | 250 | - | 250 | 617.8858
37.5 | 98.2% | 300 | 2429 | 300 | 660 | 300 | 707.135
50 | 98.3% | 400 | 2740.3333 | 400 | - | 400 | 874.8972
75 | 98.5% | 500 | 3269 | 500 | 1231.25 | 500 | 1031.978
100 | 98.6% | 750 | 3830 | 750 | 1395 | 750 | 1393.0861
150 | 98.67% | 1000 |  | 1000 | - | 1000 | 1723.5847
167 | 98.7%
250 | 98.8%
333 | 98.9%
Note on A1: Source: Electronic Code of Federal Regulations: Title 10, Chapter II, Subchapter D, §431.196
Note on D1: Source: Validated data from Powersmiths International Corp. database of field measurements as of May 18, 2017. Non-bold capacities are interpolated.
Note on G1: Source: Hawai`i Energy Losses Database (WIP).
Note on J1: Source: Energy Efficiency & Renewable Energy Office (EERE): Technical Support Document: Energy Efficiency Program for Consumer Products & Commercial & Industrial Equipment, Distribution Transformers, 2013. No-load losses calculated using formula presented in Chapter 5.2.2: Scaling Relationships in Transformer Manufacturing.
Note on M1: Source: Hawai`i Energy Technical Reference Manual (TRM).
Note on K12: Source: Energy Efficiency & Renewable Energy Office (EERE): Final Rule LCC Spreadsheet: Design Line #7: 75kVA, Dry Type, 3-Phase, 10kV BIL. Average of transformers filtered for 98.60% (DOE2016) efficiency.
Note on A17: Source: Electronic Code of Federal Regulations: Title 10, Chapter II, Subchapter D, §431.196

## TP-1 Data (hidden)
kVA | Phase | NL | FL
30 | 3 | 233 | 1321.9
15 | 3 | 162 | 990.7
75 | 3 | 412 | 2687.8
225 | 3 | 1120 | 6485.7
225 | 3 | 400 | 10000
225 | 3 | 500 | 5950
300 | 3 | 740 | 5300
112.5 | 3 | 400 | 2020
500 | 3 | 740 | 14940
750 | 3 | 1395 | 14005
75 | 3 | 400 | 730
300 | 3 | 740 | 5300
225 | 3 | 500 | 5450
150 | 3 | 400 | 3587
150 | 3 | 400 | 3590
500 | 3 | 1395 | 7000
500 | 3 | 1395 | 6785
500 | 3 | 1395 | 6785
112.5 | 3 | 400 | 2020
150 | 3 | 400 | 3587
300 | 3 | 500 | 11930
150 | 3 | 500 | 2130